APPENDIX “B”

GENERAL PROGRAM LAYOUT

lines 1-1000		All code that reads values from other control panels (here ONLY, assign values

to virtual points)

Outside air temperature code

Other “boiler plate” code

lines 2000-2999		Code to control a specific piece of equipment such as an air handler

lines 2000-2099		Code to control one component such as fan speed control for duct static

pressure

lines 2100-2199		Code to control another component

.

.

lines 3000-3999		Code for another piece of equipment

.

.

last line 10000	GOTO 1

Example Program

1  C

2  C          FID C 963, location of control panel in that building

3  C          what systems this FID controls

4  C          who wrote this code and when it was written

5  C

6  C     GET OA TEMP FROM 960 IF NETWORK IS CONNECTED

7  Program lines are executed by the FID microprocessor  Comment lines are ignored by the microprocessor.

Comment lines provide an opportunity for copious description of a functional block’s operation and the points used.

Comment lines start from a multiple of one hundred and are numbered by ones (e.g., 100, 101, 102,…)

Program lines will start from the next higher multiple of ten and be numbered by tens (e.g., 110, 120, 130,…)

Comment blocks should begin and end with a C line as in below examples. This structure provides eight lines of comment text and nine lines of program code for each functional block. If a function cannot be described in eight comment lines and performed in nine program lines it can probably be broken down further into smaller functional blocks.

Lines 1-9		Introductory comments and outside air point identifiers

Lines 10-90		Outside air temperature code

Lines 100-109		Comments for next functional block

Lines 110-990		Code passing values to/from other panel virtual points & other “boiler plate” code

Lines 1000-1009		Comments for next functional block

Lines 1010-1990		Code to control a specific major system such as an air handler

Lines 1100-1109		Comments for next functional block

Lines 1110-1190		Code to control one component of that system such as fan speed for duct static pressure

Lines 1200-1209		Comments for next functional block

Lines 1210-1290		Code to control the next system component

Lines 2000-2009		Comments for next functional block

Lines 2010-2990		Code to control the next major system

Lines 3000-3009		Comments for next functional block

Lines 3010-3990		Code to control the next major system

Et cetera

Last line 10010		GOTO 10

Program must flow from top to bottom. Top line and bottom line must be evaluated on each pass-through. Do not condense program size at the expense of clarity or ease of troubleshooting. If possible perform control of all parts of a system in the same general area of the program. Use virtual points instead of local variables where it is necessary to check the progress/accuracy of program operation.

Example Program

1	C

2	C	[Building and FID location] [systems controlled] [author and date]

3	C

4	C	GET OA TEMP FROM 960 IF NETWORK IS CONNECTED

5	C	A9605S = PRIMARY OUTSIDE AIR TEMPERATURE SENSOR

6	C	A96333 = SECONDARY OUTSIDE AIR TEMPERATURE SENSOR

7	C	C963O1 = OUTSIDE AIR TEMPERATURE VIRTUAL POINT FOR THIS FID

8	C	NODE12 = THE NODE RESIDENT POINT FOR FID A AT 960

9	C

10      	IF (A9605S .NE. FAILED) THEN GOTO 40

20      C963O1 = A96333

30      GOTO 10	C963O1 = A96333

30	GOTO 110

40      	IF (NODE12 .NE. FAILED) THEN GOTO 70

50      C963O1 = A96333

60      GOTO 100

70      C963O1 = A9605S

A9605S = primary outside air temperature sensor

A96333 = secondary outside air temperature sensor

C963O1 = outside air temperature for this control panel (virtual point)

NODE12 = the node of FID A at 960	C963O1 = A96333

60	GOTO 110

70	C963O1 = A9605S

Note: The outside air temperature code has been developed to work under several different failure scenarios. The lines must appear in exactly the order show above and with no consolidation of the lines. The secondary temperature sensor should be one that is located in the same building and on the same trunk segment as the new control panel. If no such sensor exists, then the secondary outside air temperature sensor for the trunk is used.

80  C

90  C          FIND THE COLDEST ROOM TEMP

95  C

100    MIN(C963T1, [room temp sensors])

C963T1 = is a priority 3 alarm below 50 degrees F

170  C

180  C     LOW TEMP PROTECTION

190  C     100	C

101	C	STORE VALUE OF COLDEST ROOM TEMPERATURE IN VIRTUAL POINT C963T1

102	C

110	MIN(C963T1, [room temp sensors])

200	C

201	C	SET VALUE OF LOW TEMPERATURE ALARM C963A1

202	C

200   10	IF (C963O1 .GT. 30.0 .AND. C963T1 .GT. 60.0) THEN OFF (C963A1)

210   20	IF (C963O1 .LE. 25.0 .OR. C963T1 .LE. 55.0) THEN ON (C963A1)

270  C

280  C     RESET WEEKEND

290  C     300	C

301	C	RESET WEEKEND

302	C

300   10	IF (DAY .LE. 2) THEN C963W1 = 2.0

370  C

380  C     DECIDE WHETHER TODAY IS A WORK DAY

390  C     400	C

401	C	SET VALUE OF WORK DAY C963B1

402	C	C963H1 IS COMMANDED ON DURING HOLIDAYS

403	C	C963W1 VALUE OF: 5 OR LESS = M-F; 6 = M-F & SATURDAY;

404	C	C963W1 VALUE OF: 7 = M-F & SUNDAY, 13 = M-F & SAT & SUN

405	C

400   10	IF (C963H1 .EQ. ON ) THEN GOTO 4450

410   20	IF (DAY .LE. 5 .OR. C963W1 .GT. 12.5 .AND. C963W1 .LE. 13.5) THEN GOTO 4670

420   30	IF (DAY .EQ. 6 .AND. C963W1 .GT. 5.5 .AND. C963W1 .LE. 6.5) THEN GOTO 4670

430   40	IF (DAY .EQ. 7 .AND. C963W1 .GT. 6.5 .AND. C963W1 .LE. 7.5) THEN GOTO 4670

440   OFF (C963B1)

450   GOTO 500

460   ON (C963B1)

C963H1 = is commanded on during holidays

C963W1 = 6 to run Saturday, 7 to run Sunday, and 13 to run Saturday and Sunday

C963B1 = work day point

470  C

480  C     SET AH07 OCCUPY POINT, ON FOR 24HR RUN OR OVERRIDE (C963D5)

490  C     50	OFF (C963B1)

460	GOTO 510

470	ON (C963B1)

500	C

501	C	TEST 24 HOUR RUN C963B2, 4 HOUR OCCUPY DEMAND C963D5, & NORMAL

502	C	START/STOP TIME POINTS TO SET VALUE OF AH07 SYSTEM RUN POINT C963B5

503	C	C963B3 = START TIME FOR AH07

504	C	C963B4 = STOP TIME FOR AH07

505	C

500   10	IF (C963B2 .OR. C963D5 .OR. C963A1) THEN GOTO 5450

510   20	IF (C963B1.EQ.ON.AND.CRTIME.GT.C963B3.AND.CRTIME.LT.C963B4)THEN GOTO 5450

520   OFF (C963B5)

530   GOTO 600

540   ON (C963B5)

C963B2 = 24 hour run point for AH07

C963B3 = start time for AH07

C963B4 = stop time for AH07

C963B5 = occupy point for AH07

670  C

680  C     TOGGLE LEAD PUMP SELECTORS MONTHLY

690  C

700   IF (DAYOFM .NE. 1) THEN ON30	OFF (C963B5)

540	GOTO 610

550	ON (C963B5)

600	C

601	C	TOGGLE/INCREMENT LEAD PUMP SELECTORS ON FIRST OF EACH MONTH AT 6 AM

602	C	C963L1 = DIGITAL LEAD/LAG SELECTOR FOR 1 OF 2 HW COIL PUMPS

603	C	C963L2 = ANALOG LEAD/LAG/STANDBY SELECTOR FOR 1 OF 3 CW COIL PUMPS

604	C

610	IF (DAYOFM .NE. 1) THEN OFF($LOC1)

710   620	IF (DAYOFM .NE. 1 .OR. $LOC1 .EQ. OFF .OR. C963B5 .NE. ON) THEN GOTO 80OR. CRTIME .NE. 6.0) THEN GOTO 710

720   630	IF (C963L1) THEN OFF(C963L1) ELSE ON(C963L1)

730   IF (C963L2) THEN OFF(C963L2) ELSE ON(C963L2)

740   OFF ($LOC1)

C963L1 = lead/lag selector point for HW coil pumps

C963L2 = lead/lag selector point for CW coil pumps

770 C

780 C     SET OCCUPY FOR 4 HOURS IF OCCUPY OVERRIDE BUTTON IS PUSHED

790 640	IF (C963L2 .GT. 2.0) THEN (C963L2 = 1.0 ) ELSE (C963L2 = C963L2 + 1.0 )

650	OFF ($LOC1)

700	C

701	C	TEST UNOCCUPY OVERRIDE BUTTON TO SET OCCUPY FOR 4 HOURS

702	C	C96332 = BUTTON

703	C	C963D5 = OVERRIDE DEMAND

704	C

800    710	IF (C96332 .AND. C963D5 .EQ. 0) THEN C963D5 = 2

810    720	IF (C963D5 .EQ. 0) THEN SECND4 = 0

820    730	IF (SECND4 .LT. 7200) THEN GOTO 10010

830    740	SECND4 = 0

840    750	IF (C963D5 .EQ. 2) THEN C963D5 = 1 ELSE C963D5 = 0

C96332 = button

C963D5 = override demand

2970  C

2980  C     RUN FAN AND CONTROL SPEED FOR DUCT STATIC PRESSURE

2990  C

3000    IF (C963B5) ON (C96301) ELSE OFF (C96301)

3010    IF (C96301 .NE. PRFON) THEN GOTO 3040

1000	C

1001	C	TEST SYSTEM RUN (C963B5) TO RUN SUPPLY FAN C96300

1002	C	TEST FAN RUN STATUS TO DETERMINE CONTROL STRATEGY

1003	C

1010	IF (C963B5) ON (C96300) ELSE OFF (C96300)

1020	IF (C96300 .EQ. PRFON) THEN GOTO 1210

1100	C

1101	C	FAN IS OFF. CLOSE RELIEF DAMPER, MINIMUM OA DAMPER, & COIL VALVES

1102	C	SET FAN SPEED CONTROL TO IDLE

1103	C

1110	SET (0.0,C96322,C96323, C96326)

1120	SET (15.0, C96325)

1130	SET (8.0,C96321)

1140	GOTO 2010

1200	C

1201	C	FAN RUNS. CONTROL FAN SPEED TO MAKE DUCT STATIC PRESSURE MEET SETPT

1202	C	C96355 = DUCT STATIC PRESSURE

1203	C	C96321 = FAN SPEED CONTROL

1204	C	C963S1 = DUCT STATIC SETPOINT

1205	C

3020    1210	LOOP (0,C96355,C96321,C963S1,2000,40,0,2,8.0,4.0,20.0,0)

3030    GOTO 3100

3040    C96321 = 8.0

C96301 = supply fan

C96355 = duct static pressure

C96321 = fan speed control

C963S1 = duct static setpoint

3070  C

3080  C   OPEN MIN OUTSIDE AIR DAMPER DURING OCCUPY

3090  C

3100    IF (C963B5) THEN C96323 = 15.0 ELSE C96323 = 1.0

C96323 = minimum outside air damper

3170  C

3180  C   CONTROL RELIEF DAMPER FOR BLDG STATIC PRESSURE

3190  C

3200   SAMPLE (2) GOTO 3220

3210   GOTO 3500

3220   C963C9 = C963C8

3230   C963C8 = C963C7

3240   C963C7 = C963C6

3250   C963C6 = C963C5

3260   C963C5 = C963C4

3270   C963C4 = C963C3

3280   C963C3 = C963C2

3290   C963C2 = C963C1

3300   C963C1 = C963C0

3310   C963C0 = C96353

3320   $LOC3 = C963C9 + C963C8 + C963C7 + C963C6 + C963C5

3330   $LOC3 = $LOC3 + C963C4 + C963C3 + C963C2 + C963C1 + C963C0

3340   $LOC3 = $LOC3 * 10.0

3350   1300	C

1301	C	OPEN MIN OUTSIDE AIR DAMPER C96323 WHEN FAN RUNS

1302	C

1310	SET(15.0,C96323)

1400	C

1401	C	TAKE 10 SAMPLES OF BLDG STATIC PRESSURE OVER 20 SECONDS & GET AVERAGE

1402	C	CONTROL RELIEF DAMPER TO MAKE AVERAGED PRESSURE MEET SETPT

1403	C	C96353 = BUILDING STATIC PRESSURE

1404	C	C963S2 = BUILDING STATIC PRESSURE SETPOINT

1405	C	C96322 = RELIEF DAMPER

1406	C

1410	TIMAVG ($LOC2,2,10,C96353)

1420	$LOC3 = $LOC2 * 100.0

1430	$LOC4 = C963S2 * 100.0

3360   1440	LOOP (128,$LOC3,C96322,$LOC4,375,8,1,1,7.0,7.0,14.0,0)

C963C0-C9 = LAO’s with a slope of 0.01 (for resolution), an intercept of 0.0, and a

COV limit of 100 (won’t cause network traffic)

C96353 = building static pressure

C963S2 = building static pressure setpoint

C96322 = relief damper

Note: 3340 $LOC3 = $LOC3 * 10.0 is the same as

3340 $LOC3 = ($LOC3/10.0) * 100.0, where the quotient completes the average.

The building static pressure is averaged to prevent erratic control on windy days. The $LOC

points are used to prevent excessive COV traffic and to scale the duct static variables.

If building static pressure is controlled using return fans then at most one LOOP statement is used

for each static pressure sensor. Systems that do not have isolated air flow may require the use of

only one LOOP statement to control all return fans based on an average of all the building static

pressures.

3570  C

3580  C   SET HW PUMP DEMAND ON OA TEMP AND DISCH TEMP

3590  C1500	C

1501	C	CONTROL HW & CW COIL VALVES TO MAKE SA TEMP MEET SETPT

1502	C

1510	LOOP (0,C96352,$LOC7,C963S0,800,16,0,2,7.5,1.0,14.0,0)

1520	TABLE ($LOC7,C96325,7.0,7.0,14.0,14.0)

1530	TABLE ($LOC7,C96326,1.0,1.0,7.0,7.0)

2000	C

2001	C	TEST OA TEMP & COMPARE SA TEMP TO SETPT TO SET HW PUMP DEMAND

2003	C

2010	IF ((C963S0 - C96352) .GT. 5.0) THEN GOTO 2030

2020	SECNDS = 0

3640    2030	IF (SECNDS .GT. 600) THEN ON ($LOC5) ELSE OFF ($LOC5)

3840     IF (SECND1 .GT. 600) THEN ON ($LOC6) ELSE OFF($LOC6)

3600    2040	IF (C963O1 .LE. 60.0 .OR. $LOC5) THEN ON (C963D2)

3610    2050	IF (C963O1 .GT. 65.0 .AND. $LOC5 .NE. ON) THEN OFF (C963D2)

3620    IF ((C963S0 - C96352) .GT. 5.0) THEN GOTO 3640

3630    SECNDS = 0

2100	C

2101	C	TEST DEMAND FOR HW COIL PUMP TO DETERMINE PUMP OPERATION

2102	C

2110	IF (C963D2) THEN GOTO 2310

2200	C

2201	C	DEMAND FOR PUMP IS OFF. TURN OFF BOTH PUMPS

2202	C

2210	OFF (C96303, C96304)

2220	GOTO 3010

2300	C

2301	C	DEMAND IS ON. TEST LEAD SELECTOR TO DETERMINE PUMP ASSIGMENT

2302	C

2310	IF (C963L1) THEN GOTO 2510

2400	C

2401	C	RUN NORTH PUMP AS LEAD, SOUTH AS LAG

2402	C

2410	ON (C96303)

3640    IF (SECNDS .GT. 600) THEN ON ($LOC5) ELSE OFF ($LOC5)

The inclusion of discharge temperature in setting pump demand is a new strategy and may require

some modification.

3670  C

3680  C   RUN LEAD HW PUMP

3690  C

3700    IF (C963D2 .NE. ON) THEN GOTO 3780

3710    IF (C963L1) THEN GOTO 3750

3720    ON (C96303)

3730    2420	IF (C96303 .NE. PRFON) THEN ON(C96304) ELSE OFF (C96304)

3740    GOTO 3800

3750    2430	GOTO 3800

2500	C

2501	C	RUN SOUTH PUMP AS LEAD, NORTH AS LAG

2502	C

2510	ON (C96304)

3760    2520	IF (C96304 .NE. PRFON) THEN ON(C96303) ELSE OFF (C96303)

3770    GOTO 3800

3780    OFF (C96303, C96304)

3790   C

3793   C   SET CW PUMP DEMAND ON OA TEMP, DISCH TEMP

3795   C

3000	C

3001	C	TEST OA TEMP & COMPARE SA TEMP TO SETPT TO SET CW COIL PUMP DEMAND

3002	C

3010	IF ((C96352 - C963S0) .GT. 5.0) THEN GOTO 3030

3020	SECND1 = 0

3030	IF (SECND1 .GT. 600) THEN ON ($LOC6) ELSE OFF($LOC6)

3800     040	IF (C963O1 .GT. 70.0 .OR. $LOC6) THEN ON(C963D3)

3810     050	IF (C963O1 .LE. 65.0 .AND. $LOC6 .NE. ON) THEN OFF(C963D3)

3820     IF ((C96352 - C963S0) .GT. 5.0) THEN GOTO 3840

3830     SECND1 = 0

100	C

3101	C	TEST DEMAND FOR CW PUMP TO DETERMINE PUMP OPERATION

3102	C

3110	IF(C963D3)THEN GOTO 3310

3200	C

3201	C	NO DEMAND FOR CW. TURN OFF PUMPS

3202	C

3210	OFF(C96301,C96302,C96303)

3220	GOTO 10010

3300	C

3301	C	TEST VALUE OF LEAD SELECTOR & SET PUMP ASSIGNMENTS

3302	C	RUN EAST AS LEAD, CENTER AS LAG, WEST AS STANDBY

3303	C

3310	IF(C963L2.GT.1.0)THEN GOTO 3410

3320	ON(C96301)

3330	IF(C96301.EQ.PRFON)THEN GOTO 3370

3340	ON(C96302)

3350	IF(C96302.EQ.PRFON)THEN OFF(C96303)ELSE ON(C96303)

3360	GOTO 10010

3370	OFF(C96302,C96303)

3380	GOTO 10010

3400	C

3401	C	TEST VALUE OF LEAD SELECTOR & SET PUMP ASSIGNMENTS

3402	C	RUN CENTER AS LEAD, WEST AS LAG, EAST AS STANDBY

3403	C

3410	IF(C963L2.GT.2.0)THEN GOTO 3510

3420	ON(C96302)

3430	IF(C96302.EQ.PRFON)THEN GOTO 3470

3440	ON(C96303)

3450	IF(C96303.EQ.PRFON)THEN OFF(C96301)ELSE ON(C96301)

3460	GOTO 10010

3470	OFF(C96303, C96301)

3480	GOTO 10010

3500	C

3501	C	TEST VALUE OF LEAD SELECTOR & SET PUMP ASSIGNMENTS

3502	C	RUN WEST AS LEAD, EAST AS LAG, CENTER AS STANDBY

3503	C

3520	ON(C96303)

3530	IF(C96303.EQ.PRFON)THEN GOTO 3570

3540	ON(C96301)

3550	IF(C96301.EQ.PRFON)THEN OFF(C96302)ELSE ON(C96302)

3560	GOTO 10010

3570	OFF(C96301, C96302)

10000	C

3870   C

3880   C   RUN LEAD CW PUMP

3890   C

3900     IF (C963D3 .NE. ON) THEN GOTO 3980

3910     IF (C963L2) THEN GOTO 3950

3920     ON (C96300)

3930     IF (C96300 .NE. PRFON) THEN ON (C96302) ELSE OFF (C96302)

3940     GOTO 4000

3950     ON (C96302)

3960     IF (C96302 .NE. PRFON) THEN ON (C96300) ELSE OFF (C96300)

3970     GOTO 4000

3980     OFF (C96300, C96302)

3990  C

3993  C    CONTROL COIL VALVES

3995  C

4000     IF (C96301 .NE. PRFON) THEN GOTO 4200

4010     LOOP (0,C96352,$LOC7,C963S0,800,16,0,2,7.5,1.0,14.0,0)

4020     TABLE ($LOC7,C96326,1.0,1.0,7.0,7.0)

4030     TABLE ($LOC7,C96325,7.0,7.0,14.0,14.0)

4040     SECND2 = 0

4050     GOTO 4200

9970  C

9980  C     10001	C	THE END. GO BACK TO THE TOP AND DO IT AGAIN

9990  C

10000 GOTO 1010002	C

10010	GOTO 10

Control strategies shown are basic. Application may call for more detailed control with time delay, anti-toggle protection, emergency on or lockout, etc.

Boiler control is similar to the hot and cold water pump control shown above. There is a demand point, usually based on outside air temperature, and there is a minimum run time for the boiler.

Chiller/Tower control strategies vary because the systems vary. Demand points are used, but are not always based on outside air temperature. Pumps and chillers require lead/lag points as show in the example code.