## Project Summary
Project-Level Commercial & Industrial Lighting Calculator
This worksheet calculates the annual energy savings and Conservation Rate Credit or Conservation Acquisition Agreement reimbursement resulting from the installation of energy efficient lighting. The project-level economics including savings after HVAC interaction, busbar savings, O&M costs or savings, and periodic lamp replacement costs or savings, PV Life Cycle Cost and TRC B/C ratio are also calculated. No data on this sheet may be edited. Enter all data on the Site Audit tab. Inputs here reflect data entered on that tab.
Calculator Last Revised> |  | 2006-10-01 | Version 1.5 | Todays Date>>> | 2007-01-03
Project & Facility Name> |  | Lighting Measure Examples |  | C&I Machinery
Facility Street Address> |  | 123 West C&I Avenue |  | Building> | Main Warehouse
Facility City, State, Zip> |  | Longview |  | Washington | 97567
Utility Invoice # & Name |  | Pick a unique # that you will remember | NW Public Power | Account # | A-12345
Line No. | INPUTS FROM SITE AUDIT TAB
1 | Total Floor Area Affected by Project (# of fixtures x 64 sqft/fixture) |  |  |  | 20864
2 | Project/Measure Change in Cleaning/Other O&M Cost (Savings -$ or Increases +$) |  |  |  | 0
3 | Dominant Building Type |  |  |  | Other Commercial
4 | Primary Space Heat Fuel Source |  |  |  | Gas
5 | Total Existing Watts of Area Affected by Retrofit |  |  |  | 57678
6 | Total Proposed Watts of Area Affected by Retrofit |  |  |  | 29789
7 | Total Estimated Annual kWh Site Savings (unadjusted) |  |  |  | 307282
8 | Project Cost |  |  |  | 32000
9 | Project-Level Net PV of Periodic Lamp Replacement Cost (Savings -$ or Increases +$) |  |  |  | 0
10 | Default Hours of Lighting Operation for Building Type |  |  |  | 4000
11 | RESULTS FOR ADDING PROJECT TO CART
12 | Measure Life |  |  |  | 12
13 | Inferred Weighted Average Hours of Operation (kWh saved/ kW saved) |  |  |  | 11018.0358
14 | Lighting Savings Yield (HVAC Interaction Adjustment for Building & Space Heat Type) |  |  |  | 103%
15 | Annual Site Energy Savings Adjusted for HVAC Interaction (kWh) |  |  |  | 316501.9635
16 | Annual Busbar Energy Savings Adjusted for HVAC Interaction (kWh) |  |  |  | 340635.2383
17 |  |  |  | Wattage Reduction (%) | 48.35%
18 | Customer Retail Rate |  |  |  | 0.0625
19 | Annual Energy Cost Savings |  |  |  | 19781.3727
20 | Simple Payback |  |  |  | 1.6177
21 | Site Unit Energy Savings (kWh/sf) |  |  |  | 14.7279
22 | Site Lighting Power Density (lpd) Reduction (W/sf) |  |  |  | 1.3367
23 | Unit Value of Electric Savings (NPV/kWh) |  |  |  | 0.46224
24 | Present Value Energy Savings |  |  |  | 157455.2325
25 | Present Value of Energy Costs |  |  |  | 52393.3324
26 | Unit Value of Gas Heat Interaction (NPV/kWh saved) |  |  |  | 0.0038037
27 | Present Value of Change in Cleaning/Other O&M Cost (Savings -$ or Increases +$) |  |  |  | 0
28 | Present Value of Change in Gas Heating Cost (Savings -$ or Increases +$) |  |  |  | 1295.6734
29 | Present Value Life Cycle Lamp Replacement Cost (Savings -$ or Increases +$) |  |  |  | 0
30 | Present Value Project/Measure Change in O&M Cost (Savings -$ or Increases +$) |  |  |  | 1295.6734
31 | Project Life Cycle Cost |  |  |  | 85689.0058
32 | Project Benefit/Cost Ratio |  |  |  | 4.729
33 | Total BPA Credit/ Reimbursement |  |  |  | 12686
Note on C11: Charlie Grist: Include change in maintenance costs (if any) OTHER THAN periodic lamp change costs or fuel costs. Example: Change in fixture cleaning costs if new fixtures cleaned more or less frequently than existing fixtures. Periodic lamp replacement costs and any change in fuel costs due to HVAC interaction are calculated automatically below.
Note on C18: Charlie Grist: Automatically calculated based on lamp-life and lighting schedule data taken from Site Audit. Used for TRC calculations.
Note on C39: Charlie Grist: For lighting measures this includes 1) Regular O&M such as change in cleaning costs, 2) Change in gas costs due to HVAC interaction if any and 3) Change in periodic lamp replacement costs over the life cycle of the measure.

## Site Audit
IMPORTANT NOTE: Input/select information into cells that have a blue color font. Leave cells with black or red color fonts alone.
Standard Offer Lighting Spreadsheet Tool - Updated October 01, 2006
| Project Name: | Lighting Measure Examples | [7 empty] | Utility Invoice Number: | Pick a unique # that you will remember
| Dominant Building Type: | [8 empty] | Serving Utility: | NW Public Power
| Space Heat Fuel Source: | [8 empty] | Utility Contact Name: | Manie Hats
| Customer Name | C&I Machinery | [7 empty] | Utility Phone Number: | 530-456-9876
| Contact Name: | John Q. Public | [7 empty] | Energy Rate ($/kWh) & estimated $ savings/yr: | 0.0625 |  |  |  |  | 19781.3727
| Facility Street Address: | 123 West C&I Avenue | [7 empty] | Demand Rate ($/kW) & estimated $ savings/yr: | 2.22 |  |  |  |  | 742.963 | [7 empty] | This Section for Calculating PV of Periodic Lamp Replacement Cost
| Facility City: | Longview | [7 empty] | Audit Prepared By: | Craig Ciranny | [12 empty] | Uses a user-defined function called dfuncPV
| Facility State & Zip: | Washington | 97567 | [6 empty] | Auditor Phone Number(s): | 503-230-5865 Office | [12 empty] | Program Parameters
| Building/Account | Main Warehouse | A-12345 | [6 empty] | Date & Time (fills in automatically): | 2007-01-03 11:55
[24 empty] | Discount Rate | 4% |  | =dfuncPV(Number,OperatingHours,AverageLife,Cost,Labor,Labor_Rate,Discount_Rate,Measure_Life)
Summary Table >> |  | Total Existing Watts | Total Proposed Watts | [6 empty] | Total Estimated Annual kWh Site Savings (unadjusted) | Annual Hours (weighted) |  |  |  |  | Lighting Wattage Reduction Only |  |  |  |  | Total kWh Site Savings (adjusted for HVAC) |  |  | Measure Life | 12
|  | 57678 | 29789 | [6 empty] | 307282 | 7292.7043 |  |  |  |  | 48.35% |  |  |  |  | 316501.9635 |  |  | Labor Rate | 20
|  | Input the Project Cost>> | 32000 | [6 empty] | Lesser of Credit/Reimbursement -or- 70% Project Cost>> | [5 empty] | 12686
Location | Existing Lamp/Ballast Combination | [7 empty] | Proposed Lamp/Ballast Combination | [6 empty] | Summary/Design Info |  |  |  |  | Measure Info |  |  | Existing |  |  |  | Proposed
For instance; building and room name | Annual Operat Hours | Existing Lamp/Ballast | Q'ty | Watts Each | Mean Lumens Each | Total Watts | Total kWh | Select Proposed Lamp/Ballast | Annual Operat Hours | Proposed Lamp/Ballast | Q'ty | Watts Each | Mean Lumens Each | Total Watts | Total kWh | Annual kWh Savings | Watt Reduc tion | Light Level Change | Proposed kWh |  | Code | $ per unit | Total $ | Rated Average Lamp Life (hours/lamp for ballast type and start frequency) | Lamp Cost ($/lamp) | Lamp Change Labor (hours/lamp) | PV Lamp Periodic Replacement | Rated Average Lamp Life (hours/lamp for ballast type and start frequency) | Lamp Cost ($/lamp) | Lamp Change Labor (hours/lamp) | PV Lamp Periodic Replacement | Net PV Lamp Periodic Replacement (Costs(+) or Savings(-))
[8 empty] | #N/A |  |  | 0 | [8 empty] | LINE, LINE, LINE | [6 empty] | #NAME? |  |  |  | #NAME?
Category A1 Example | 8760 | T12 4' Fluorescent, 2-F40T12ES 34W, 1-Mag | 10 | 82 | 3867.94 | 820 | 7183.2 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | 8760 | T8HP 4', 1-F32T8, 3100+lumen, 1-HLO Universal B232I120HE | 10 | 33 | 3033.35 | 330 | 2890.8 | 4292.4 | 59.76% | -21.58% |  |  | A1 | 15 | 150 | 20000 | 1.12 | 0.09 | #NAME? | 30000 | 3.25 | 0.09 | #NAME?
Category A2 Example | 3500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 50 | 96 | 4867.8 | 4800 | 16800 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | 3500 | T8HP 4', 2-F32T8, 3100+lumen, 1-RLO GE-232-Ultramax-L | 50 | 48 | 4535.3 | 2400 | 8400 | 8400 | 50% | -6.831% |  |  | A2 | 30 | 1500 | 20000 | 1.12 | 0.09 | #NAME? | 30000 | 3.25 | 0.09 | #NAME?
Category B1 Example | 2000 | T12 4' Fluorescent, 1-F40T12 40W, 1-Mag | 1 | 52 | 2433.9 | 52 | 104 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP | 2000 | T8 Standard Electronic, 1-F32T8, 2950+lumen, 1-Elec | 1 | 31 | 2400 | 31 | 62 | 42 | 40.38% | -1.393% | 124 | LINE, LINE, LINE | B1 | 8 | 8 | 20000 | 1.12 | 0.09 | #NAME? | 24000 | 2.5 | 0.09 | #NAME?
Category B2 Example | 2000 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 1 | 96 | 4867.8 | 96 | 192 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | 2000 | T8 Standard Electronic, 2-F32T8, 2950+lumen, 1-ISElec | 1 | 59 | 4932.4 | 59 | 118 | 74 | 38.54% | 1.327% | 236 | LINE, LINE, LINE | B2 | 15 | 15 | 20000 | 1.12 | 0.09 | #NAME? | 24000 | 2.5 | 0.09 | #NAME?
Category C1 Example | 4380 | Incandescent, 1-A 100W, no ballast | 4 | 100 | 1548 | 400 | 1752 | Hard-Wired CFL, 1-PL 26W, 1-Mag | 4380 | New Hard-Wired CFL fixture, 2-bi-ax 13, 1-Elec | 4 | 29 | 1530 | 116 | 508.08 | 1243.92 | 71% | -1.163% | 2225.3904 | LINE, LINE, LINE | C1 | 30 | 120 | 1000 | 0.52 | 0.05 | #NAME? | 10000 | 1.91 | 0.09 | #NAME?
Category C2 Example | 4380 | Incandescent, 1-A 150W, no ballast | 2 | 150 | 2536.5 | 300 | 1314 | Hard-Wired CFL, 2-PL 23W, 2-Mag | 4380 | New Hard-Wired CFL fixture, 2-bi-ax 26W, 1-Elec | 2 | 52 | 3060 | 104 | 455.52 | 858.48 | 65.33% | 20.64% | 1995.1776 | LINE, LINE, LINE | C2 | 50 | 100 | 1000 | 0.52 | 0.05 | #NAME? | 10000 | 3.3 | 0.09 | #NAME?
Category D1 Example | 3500 | Incandescent, 1-PAR 75W, no ballast | 4 | 75 | 688.5 | 300 | 1050 | Hard-Wired CFL, 1-PL 20W, 1-Mag | 3500 | Ceramic Metal Halide, 1-Single End or Double End 39W, 1-Elec | 1 | 45 | 2600 | 45 | 157.5 | 892.5 | 85% | -5.592% | 551.25 | LINE, LINE, LINE | D1 | 50 | 50 | 2000 | 4 | 0.09 | #NAME? | 9000 | 43.25 | 0.15 | #NAME?
Category D2 Example | 3500 | Mercury Vapor, 250W, 1-Std Mag | 2 | 285 | 10700 | 570 | 1995 | T5HO Fluorescent, 2-F54T5HO 54W, 1-Elec | 3500 | Ceramic Metal Halide, 1-Bulb 150W, 1-Elec | 2 | 168 | 9920 | 336 | 1176 | 819 | 41.05% | -7.29% | 4116 | LINE, LINE, LINE | D2 | 80 | 160 | 24000 | 13.85 | 0.4 | #NAME? | 20000 | 43.25 | 0.15 | #NAME?
Category E1 Example | 3500 | Incandescent, 1-A 75W, no ballast | 10 | 75 | 1085.6 | 750 | 2625 | Hard-Wired CFL, 1-PL 20W, 1-Mag | 3500 | Screw-In CFL, 1-23W, 1-Elec | 10 | 23 | 1190 | 230 | 805 | 1820 | 69.33% | 9.617% | 2817.5 | LINE, LINE, LINE | E1 | 3 | 30 | 1200 | 0.52 | 0.05 | #NAME? | 10000 | 4 | 0.09 | #NAME?
Category E2 Example | 3500 | Incandescent, 1-A 150W, no ballast | 5 | 150 | 2536.5 | 750 | 2625 | Hard-Wired CFL, 2-PL 23W, 2-Mag | 3500 | Screw-In CFL, 1-42W, 1-Elec | 5 | 42 | 2380 | 210 | 735 | 1890 | 72% | -6.17% | 2572.5 | LINE, LINE, LINE | E2 | 6 | 30 | 1000 | 0.52 | 0.05 | #NAME? | 10000 | 13 | 0.09 | #NAME?
Category E3 Example | 3500 | Incandescent, 1-PS30 200W, no ballast | 1 | 200 | 3153.5 | 200 | 700 | Hard-Wired CFL, 2-2D 28W, 1-Elec | 3500 | Screw-In CFL, 1-65W, 1-Elec | 1 | 65 | 3570 | 65 | 227.5 | 472.5 | 67.5% | 13.21% | 796.25 | LINE, LINE, LINE | E3 | 12 | 12 | 750 | 4.29 | 0.09 | #NAME? | 10000 | 18 | 0.09 | #NAME?
Category F1 Example | 8760 | Exit Sign, 2-Inc 20W, no ballast | 30 | 40 | 2 | 1200 | 10512 | New Exit Sign, 1-LED <5W, 1-None | 8760 | New Exit Sign, 1 face LED, 1.5W, no ballast | 30 | 1.5 | 2 | 45 | 394.2 | 10117.8 | 96.25% | 0% | 3453.192 | LINE, LINE, LINE | F1 | 30 | 900 | 10000 | 2.31 | 0.1 | #NAME? | 100000 | 25 | 0.2 | #NAME?
Category G1 Example | 4380 | Mercury Vapor, 175W, 1-Std Mag | 4 | 205 | 7600 | 820 | 3591.6 | T8 Fluorescent, 2-F32T8 32W, 1-Elec HLO | 4380 | Induction, 1-QL 85W, 1-RF Generator | 4 | 85 | 4800 | 340 | 1489.2 | 2102.4 | 58.54% | -36.84% | 6522.696 | LINE, LINE, LINE | G1 | 60 | 240 | 24000 | 12.35 | 0.4 | #NAME? | 100000 | 400 | 0.3 | #NAME?
Category G2 Example | 4380 | Mercury Vapor, 250W, 1-Std Mag | 4 | 285 | 10700 | 1140 | 4993.2 | T5HO Fluorescent, 2-F54T5HO 54W, 1-Elec | 4380 | Induction, 1-QL 165W, 1-RF Generator | 4 | 165 | 9600 | 660 | 2890.8 | 2102.4 | 42.11% | -10.28% | 12661.704 | LINE, LINE, LINE | G2 | 120 | 480 | 24000 | 13.85 | 0.4 | #NAME? | 100000 | 400 | 0.3 | #NAME?
Category H1 Example | 8760 | Metal Halide, 175W, 1-Std Mag | 10 | 210 | 9400 | 2100 | 18396 | T5HO Fluorescent, 2-F54T5HO 54W, 1-Elec | 2100 | T8HP 4', 3-F32T8, 3100+lumen, 1-HLO Sylvania Quicktronic QT3X32/120/277/IS Plus | 10 | 112 | 10425.3 | 1120 | 2352 | 16044 | 46.67% | 10.91% | 20603.52 | LINE, LINE, LINE | A2 | 30 | 300 | 10000 | 18.4 | 0.4 | #NAME? | 30000 | 3.25 | 0.09 | #NAME?
Category J1 Occupancy Sensor Example | [9 empty] | Occupancy Sensor or Timer controlling 100 to 200 watts (see above) | 10 |  |  | 0 | 0 |  |  |  |  | LINE, LINE, LINE | J1 | 35 | 350 |  |  |  | #NAME? | No Default | No Default | No Default | #NAME?
Category H2 Example | 8760 | Metal Halide, 250W, 1-Std Mag | 10 | 295 | 11300 | 2950 | 25842 | T5HO Fluorescent, 3-F54T5HO 54W, 1-Elec | 2100 | T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QTP4x32/UNV-ISN-SC | 10 | 114 | 10366.4 | 1140 | 2394 | 23448 | 61.36% | -8.262% | 20971.44 | LINE, LINE, LINE | A2 | 30 | 300 | 10000 | 18.4 | 0.4 | #NAME? | 30000 | 3.25 | 0.09 | #NAME?
Category J1 Occupancy Sensor Example | [9 empty] | Occupancy Sensor or Timer controlling 100 to 200 watts (see above) | 10 |  |  | 0 | 0 |  |  |  |  | LINE, LINE, LINE | J1 | 35 | 350 |  |  |  | #NAME? | No Default | No Default | No Default | #NAME?
Category H3 Example | 8760 | Metal Halide, 400W, 1-Std Mag | 20 | 458 | 26000 | 9160 | 80241.6 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec | 2100 | T8HP 4', 6-F32T8, 3100+lumen, 3-HLO Advance Elec REL/VEL-3P32-HL-SC | 20 | 255 | 23324.4 | 5100 | 10710 | 69531.6 | 44.32% | -10.29% | 93819.6 | LINE, LINE, LINE | K2 | 40 | 800 | 10000 | 18.4 | 0.4 | #NAME? | 30000 | 3.25 | 0.09 | #NAME?
Category J2 Occupancy Sensor Example | [9 empty] | Occupancy Sensor or Timer controlling over 200 watts (see above) | 20 |  |  | 0 | 0 |  |  |  |  | LINE, LINE, LINE | J2 | 45 | 900 |  |  |  | #NAME? | No Default | No Default | No Default | #NAME?
Category H4 Example | 8760 | Mercury Vapor, 1000W, 1-Std Mag | 5 | 1080 | 45000 | 5400 | 47304 | MH Pulse Start, 1-PS 400W, 1-Elec | 2100 | T5HO Fluorescent, 6-F54T5HO 54W, 3-Program Start | 5 | 352 | 28500 | 1760 | 3696 | 43608 | 67.41% | -36.67% | 32376.96 | LINE, LINE, LINE | H4 | 140 | 700 | 24000 | 64.08 | 0.4 | #NAME? | 20000 | 8.22 | 0.09 | #NAME?
Category J2 Occupancy Sensor Example | [9 empty] | Occupancy Sensor or Timer controlling over 200 watts (see above) | 5 |  |  | 0 | 0 |  |  |  |  | LINE, LINE, LINE | J2 | 45 | 225 |  |  |  | #NAME? | No Default | No Default | No Default | #NAME?
Category I1 Example | 4380 | Mercury Vapor, 400W, 1-Std Mag | 10 | 454 | 19100 | 4540 | 19885.2 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec | 4380 | MH Pulse Start, 1-PS 300W, 1-SCWA typical ballast | 10 | 342 | 24400 | 3420 | 14979.6 | 4905.6 | 24.67% | 27.75% | 65610.648 | LINE, LINE, LINE | I1 | 100 | 1000 | 24000 | 18.34 | 0.4 | #NAME? | 20000 | 27.6064 | 0.4 | #NAME?
Category I2 Example | 8760 | Metal Halide, 1000W, 1-Std Mag | 5 | 1080 | 78000 | 5400 | 47304 | MH Pulse Start, 750W, 1-PS Mag | 8760 | MH Pulse Start, 1-PS 750W, 1-SCWA is the only option | 5 | 818 | 60000 | 4090 | 35828.4 | 11475.6 | 24.26% | -23.08% | 313856.784 | LINE, LINE, LINE | I2 | 150 | 750 | 10000 | 41.41 | 0.4 | #NAME? | 20000 | 62.5745 | 0.4 | #NAME?
Category K1 Example | 4000 | T12 8' Fluorescent, 1-F96T12HO 110W, 1-Mag | 2 | 140 | 6715.94 | 280 | 1120 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP HLO | 4000 | T8 Standard Electronic, 1-F96T8HO 86W, 1-Elec | 2 | 99 | 7380 | 198 | 792 | 328 | 29.29% | 9.888% | 3168 | LINE, LINE, LINE | B1 | 8 | 16 | 12000 | 7.02 | 0.09 | #NAME? | 24000 | 2.5 | 0.09 | #NAME?
Category K2 Example | 4000 | T12 8' Fluorescent, 2-F96T12HO 110W, 1-Mag | 10 | 252 | 13431.88 | 2520 | 10080 | T8 Fluorescent, 4-F32T8 32W, 2-Elec HLO | 4000 | T8HP 4', 4-F32T8, 3100+lumen, 2-HLO Advance Elec REL/VEL-2P32-HL-SC | 10 | 154 | 14136 | 1540 | 6160 | 3920 | 38.89% | 5.242% | 24640 | LINE, LINE, LINE | K2 | 40 | 400 | 12000 | 7.02 | 0.09 | #NAME? | 30000 | 3.25 | 0.09 | #NAME?
Category L1 Example | 8760 | T12 8' Fluorescent, 1-F96T12VHO 215W, 1-Mag | 15 | 230 | 9525.6 | 3450 | 30222 | T8 Fluorescent, 1-F96T8 59W, 1-Elec | 2500 | Retrofit to T5HO Fluorescent, 2-F54T5HO 54W, 1-Program Start | 15 | 118 | 9500 | 1770 | 4425 | 25797 | 48.7% | -0.2687% | 38763 | LINE, LINE, LINE | L1 | 25 | 375 | 12000 | 11.58 | 0.09 | #NAME? | 20000 | 8.22 | 0.09 | #NAME?
Category J1 Occupancy Sensor Example | [9 empty] | Occupancy Sensor or Timer controlling 100 to 200 watts (see above) | 15 |  |  | 0 | 0 |  |  |  |  | LINE, LINE, LINE | J1 | 35 | 525 |  |  |  | #NAME? | No Default | No Default | No Default | #NAME?
Category L2 Example | 8760 | T12 8' Fluorescent, 2-F96T12VHO 215W, 1-Mag | 20 | 440 | 19051.2 | 8800 | 77088 | T8 Fluorescent, 2-F96T8HO 86W, 1-Elec | 2500 | Retrofit to T5HO Fluorescent, 4-F54T5HO 54W, 2-Program Start | 20 | 234 | 19000 | 4680 | 11700 | 65388 | 46.82% | -0.2687% | 102492 | LINE, LINE, LINE | L2 | 50 | 1000 | 12000 | 11.58 | 0.09 |  | 20000 | 8.22 | 0.09 | #NAME?
Category J2 Occupancy Sensor Example | [9 empty] | Occupancy Sensor or Timer controlling over 200 watts (see above) | 20 |  |  | 0 | 0 |  |  |  |  | LINE, LINE, LINE | J2 | 45 | 900 |  |  |  |  | No Default | No Default | No Default | #NAME?
Decommission Fixture Example | 8760 | T12 8' Fluorescent, 2-F96T12VHO 215W, 1-Mag | 2 | 440 | 19051.2 | 880 | 7708.8 | T8 Fluorescent, 2-F96T8HO 86W, 1-Elec | 0 | Decommission (Permanently Remove) Lighting Fixture | 2 | 0 | 0 | 0 | 0 | 7708.8 | 100% | -100% | 0 | LINE, LINE, LINE | N/A | 0 | 0 | 12000 | 11.58 | 0.09 |  | 0 | 0 | 0 | #NAME?
No Recommendation Example | 4380 | High Pressure Sodium, 100W, 1-Std Mag | 12 |  |  |  |  | None | 4380 | No recommendation (leave fixture as-is) | 12 | [12 empty] | 24000 | 15.72 | 0.4 |  | 0 | 0 | 0 | #NAME?
TOTALS>>> |  |  | 249 |  |  | 57678 | 420628.6 |  |  |  | 326 |  |  | 29789 | 113346.6 | 307282 |  |  |  | #VALUE! |  |  | 12686 | [8 empty] | 0 | goes to ProjectSave
Note: To unprotect this worksheet; click on tools, protection, and unprotect sheet. There is no password. The best way to add rows is; 1) move the curser to the number box on the left hand side of the row(s) you want to add and "left-click-and-drag" down the total number of rows you want to add, 2) "right-click" in the highlighted area and a dialog box will appear, pick insert from the dialog box, 3) pick a filled in row and move the curser to that row's number box on the left side of the spreadsheet and "left-click"; the row will be highlighted, 4) "right-click" in the highlighted area and a dialog box will appear, 5) choose copy from the dialog box and the whole row will "sparkle", 6) "left-click" on the number box (left side of spreadsheet) of the first row you want to copy to and drag across all rows you want to copy to, 7) "right-click" and pick paste from the dialog box. Make sure you pick a row that has all the equations, etc., and copy the whole row into the new row(s). This will retain all the formatting and equations.
P.S. The print area on this worksheet is set so the note box does not print. The print area is set on the other worksheets as well. | [18 empty] | 754373.612
Note on M19: Automatically copies the Existing Lamp/Ballast Combination Quantity unless user types in a changed value. For instance, type in a different value if one or more fixtures are removed or added.
Note on G19: Mean lamp(s) light output per existing luminaire. Does not include luminaire efficiency. Automatically draws from the Data Existing tab column D of this workbook.
Note on E19: Quantity of existing luminaires. User input value.
Note on F19: Existing watts per luminaire. Automatically draws from the Data Existing tab column C of this workbook.
Note on D19: These are drop-down boxes. Make a selection and it will automatically draw from the Data Existing tab column B of this workbook and populate column F, G, H, I, and J of this spreadsheet.
Note on C19: Estimated annual operating hours of each lighting measure (not the building). This value is user calculated and input.
Note on B19: Area of building, room number, location, office name, etc.. Be specific enough that someone unfamiliar with the building can easily find the room or area. You can group exact same rooms together if they have the same hours of operation and are closely located.
Note on R15: Must be 30% or greater in order to receive a reimbursement or credit. Font turns red if less than 30%.
Note on N19: Proposed watts per luminaire. Automatically drawn from the Data Proposed tab column C of this workbook.
Note on O19: Mean lamp(s) light output per proposed luminaire. Does not include luminaire efficiency. Automatically drawn from the Data Proposed tab column D of this workbook.
Note on R19: Spreadsheet automatically calculates this value. It is a per room per measure calculation.
Note on L19: These are drop-down boxes. Make a selection and it will automatically draw from the Data Proposed tab column B of this workbook and populate column N, O, P, and Q of this spreadsheet.
Note on M15: Weighted average of existing lighting system hours of operation per year.
Note on E15: Calculated from column N of this worksheet. Column N is a hidden column.
Note on D15: Calculated from column H of this worksheet. Column H is a hidden column.
Note on K19: Automatically copies the Existing Annual Operating Hours of the measure unless user types in a changed value. For instance, type in a different value if an occupancy sensor is installed.
Note on L15: Total Project Estimated Annual kWh savings at the site. This value is unadjusted for interactions and busbar savings. This cell sums up values in column R.
Note on M9: OPTIONAL: This value should be the most representative utility demand rate in dollars per kilowatt per month. You may have to average seasonal demand rates.
Note on R9: This cell automatically calculates the estimated dollar savings per year (12 months) associated with kW or Demand savings. This number is added to the energy savings value and put into the estimated dollar savings cell in the letter tab of this workbook.
Note on M8: REQUIRED: This value should be the most representative energy rate in dollars per kilowatt-hour. Usually the highest block rate in the utilities rate structure. May have to average seasonal energy rates.
Note on R16: This is the Reimbursement or Credit amount. Based on the total rebate amounts or 70% of project cost whichever is less.
Note on E16: Input the total project cost from the installation contractor invoices. In-house installation labor can be counted, Use direct labor costs only (no overhead).
Note on X19: This value is taken from the Data Proposed tab column F.
Note on Y19: This value is the multiplication of column M and column X of this spreadsheet. It is the total reimbursement or credit per measure.
Note on S19: Font is RED if Wattage Reduction is NOT between 20 and 50%. The value(s) below are only related to each measure.
Note on T19: Font is RED if Change in Light Level is NOT between -10% and +10%. Calculates total change in light output of lamp(s) only. Ignores luminaire efficiency. Use the below value(s) to determine how close you are to the existing light level.
Note on R18: Per measure summary info. Use this info to check yourself.
Note on R14: This value is only related to the lighting wattage affected by the installation. Does not depict total building wattage reduction.
Note on D16: Input the project cost into the cell to the right. Includes labor and materials from the installation contractors' invoices. Also, can include in-house labor costs. Direct installation labor costs only.
Note on L16: This workbook automatically calculates the lesser of the reimbursement amount or 70% of project cost and shows the answer in the cell to the right.
Note on E14: See the cell below.
Note on D14: See the cell below.
Note on L14: See the cell below.
Note on M14: See the cell below.
Note on W19: This value is taken from the Data Proposed tab column E.
Note on W18: CAA or CRC Reimbursement or Credit per unit and total per measure
Note on R8: Charlie Grist: Electric Savings including estimated interactive effects of lighting and HVAC
Note on C5: Charlie Grist: Select building type from list. If multiple building types are present consider separate audit sheets for separate buildings. Or select the type that most closely matches the primary areas of the building where proposed lighting measures occur. This value is used to estimate interactive effects of lighting energy savings on HVAC.
Note on C6: Charlie Grist: Select dominant space heat type from list. If multiple space heat types are present, consider separate audit sheets for separate buildings. Or select the type that most closely matches the primary areas of the building where proposed lighting measures occur. This value is used to estimate interactive effects of lighting energy savings on HVAC.
Note on C10: Input building for this project
Note on W15: This value takes into account the energy interaction between the lighting system and the HVAC system.
Note on C9: Input street address, city, and stare. Enter enough info to locate the facility.

## Verification Report
Effective 10/1/2006
C&ILO - Commercial and Industrial Lighting Schedule (ESO) - FY07
| Street Address: | 123 West C&I Avenue | Project Name: | Lighting Measure Examples
| Facility City: | Longview | Invoice # : | Pick a unique # that you will remember
Existing Equipment |  | Measure Description |  | Incentive Per Unit | Number of Units | Total by Measure
| A | High Performance T8 Fluorescent Lamps and Electronic Ballast
T12 Fluorescent, | Includes T8, 2' to 8' lamps: Ballast: PF>95%, THD<20%. Lamp: Lumen Maint.>94%, CRI>80, lamp life>24,000 hrs, (4' lamp<5000K, lumens>3,100) or (4' lamp>5000K, lumens>3,000), Initial System Lumens/Watt>95. See the CEE List of qualifying products for additional guidance. Refer to the following link: http://www.cee1.org/com/com-lt/com-lt-prod.pdf
T8 De-Lamp, | 1 | 1 lamp and electronic ballast (15 to 44 input watts) |  | 15
| 2 | 2 to 4 lamps and electronic ballast (45 to 114 input watts) |  | 30
Incandescent, | B | T8 or T5 Fluorescent Lamps and Standard Electronic Ballast
or | Includes T8 and T5, 2' to 8' lamps. Ballast: PF>90%, THD<20%. Lamp: Lumen Maint.>90%, CRI>80, 4' lamp lumens>2,800, 4' lamp life>20,000 hrs, Initial System Lumens/Watt > 80
Mercury Vapor | 1 | 1 lamp and standard electronic ballast (15 to 44 input watts) |  | 8
| 2 | 2 to 4 lamps and standard electronic ballast (45 to 114 input watts) |  | 15
| C | Hardwired Compact Fluorescent
Hardwired ballast and replaceable lamp, CRI > 80, see Specifications for lumens/Watt requirement
| 1 | 7 to 49 Watts (Nominal Lamp Watts) |  | 30
| 2 | 50 to 99 Watts |  | 50
| D | Ceramic Metal Halide Luminaire (New Fixture)
CRI > 80, lumen maintenance ≥ 80%, and maximum color shift over life of lamp ≤ 200K
Incandescent | 1 | 20 to 100 Watts (Nominal Lamp Watts) |  | 50
| 2 | 101 to 250 Watts |  | 80
| E | Screw-in Compact Fluorescent Lamps (Lamp Only)
or | Includes one Piece or Modular, Energy Star compliant where applicable. Includes Cold Cathode Lamps.
| 1 | 3 to 24 Watts (Nominal Lamp Watts) |  | 3
Mercury Vapor | 2 | 25 to 45 Watts |  | 6
| 3 | over 45 Watts |  | 12
| F | LED or Cold Cathode Signs
Energy Star compliant where applicable, Input Watts < 5
| 1 | Retrofit kit or Replace existing incandescent sign |  | 30
| G | Induction Lamp Luminaire
Lamp Life > 80,000 hours, CRI > 80
| 1 | 100 Watts or less (Nominal Lamp Watts) |  | 60
| 2 | over 100 Watts |  | 120
| H | High Output Fluorescent Luminaire (New Fixture)
HO/VHO T12 | Includes T8, T5, long twin tube T5; 4' and 8'. Ballast: PF>90%, THD<20%. Lamp: Lumen Maint.>90%, CRI>80, lamp life>18,000 hrs, Initial System Lumens/Watt > 80
or | 1 | 85 to 129 Watts (Ballast Input Watts) |  | 80
MV / HPS | 2 | 130 to 189 Watts |  | 100
or | 3 | 190 to 249 Watts |  | 120
Probe-Start | 4 | 250 to 600 Watts |  | 140
Metal Halide | I | Pulse Start Metal Halide Luminaire (New Fixture)
or | Lamp Life > 20,000 hrs., Lumen Maint. > 75%, CRI > 65, Initial System Lumens/Watt > 89
Incandescent | 1 | 300 to 399 Watts (Nominal Lamp Watts) |  | 100
| 2 | 400 to 750 Watts |  | 150
Manual Control | J | Occupancy Sensors and/or Timers
Includes infrared, ultrasonic & dual-technology sensors and/or Timers
| 1 | 100 to 200 Watts controlled |  | 35
| 2 | over 200 Watts controlled |  | 45
| K | Retrofit High Output Fixtures with T8 Lamps & Ballasts
'8' T12 HO/VHO | Includes lamp/ballast retrofits & kits; Ballast: PF>90%, THD<20%. Lamp: 8' or 4' T8 Slimline or HO. Lumen Maint.>90%, CRI>80, lamp life>18,000 hrs, Initial System Lumens/Watt > 80
4' HO de-lamp | 1 | 1 T8 8' lamp and standard electronic high output ballast |  | 20
| 2 | (2 to 6) 4' T8 lamps and standard electronic high output ballast |  | 40
| L | Retrofit Very High Output Fixtures with T5 Lamps & Ballasts
''8' T12 | Includes lamp/ballast retrofits only; Ballast: PF > 90%,THD < 20%. Lamp: 4' T5 HO. Lumen Maint.>90%, CRI > 80, lamp life > 20,000 hrs, Initial System Lumens/Watt > 80
VHO | 1 | 2 T5 lamps and high output ballast |  | 25
| 2 | 3 to 4 T5 lamps and high output ballast |  | 50
| M | Other "one time" measure with pre-approval from BPA
Any existing | Includes lighting measures that are not on the above list (A-L). One-time deemed credit/reimbursement can be given to measures that receive pre-approval from BPA.
condition | 1 | Put measure description here and deemed value in next cell>>
| 2 | Put measure description here and deemed value in next cell>>
[5 empty] | A. Incentive Item Total ($): | 0
B. Total Project Cost:
C. 70% of Project Cost:
D. Reimbursement/Credit = Lower of "A" or "C" above:
[5 empty] | Percent (%) Wattage Reduction: | 48.35%
[5 empty] | Annual kWh Savings: | 316501.9635
Useful Information
1. Has the installed equipment met the project requirements and specifications? |  |  |  |  | (yes/no)
2. Are the measures listed properly installed and operating? |  |  |  |  | (yes/no)
3. Has the Sub-Project achieved a 30% or greater Wattage Reduction or kWh reduction? |  |  |  |  | (yes/no)
4. Have invoices been labeled with the unique identifying number from the RTF reporting system? |  |  |  |  | (yes/no)
Completed By:________________________________________________ |  |  |  | Date: | 2007-01-03 11:55
Inspected By:____________________________________ Date: ___________
Inspected By:____________________________________ Date: ___________
Inspected By:____________________________________ Date: ___________
Inspected By:____________________________________ Date: ___________
Inspected By:____________________________________ Date: ___________
Inspected By:____________________________________ Date: ___________

## Letter
INSTALLERS' COMPANY NAME
COMPANY ADDRESS
COMPANY CITY, STATE, Zip
COMPANY PHONE NUMBERS
2007-01-03 11:55
Dear: | Main Warehouse
Attached is a completed lighting energy audit of: |  | Lighting Measure Examples
|  | Our bid for this project is: | 32000
|  | The Estimated Utility Rebate is: | 12686
|  | Your Estimated project cost after the Utility Rebate is: | 19314
|  | The Estimated kilowatt-hour savings per year is: | 316501.9635 | kwh
|  | The Estimated dollar savings per year is: | 20524.3357
|  | The Estimated percent lighting wattage reduction is: | 48.35% | Lighting Only
|  | For a simple payback for the project of: | 0.94103 | years
I have attached a copy of the program requirements and specifications for your review.
In order to receive a utility rebate, you need to follow these program requirements.
If you have any questions regarding this proposal, please call; |  |  | 503-230-5865 Office
We look forward to working with you on this important project.
Sincerely,
Craig Ciranny

## Data Existing
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Updated November 21, 2005. This list is not meant to be complete, you can add equipment to this list. | [14 empty] | Default lamp life and cost data used for estimating life-cycle periodic replacement costs.
Description of Existing Lamp/Ballast Combination | Input Watts | Mean System Lumens | Suggested Retrofits / Notes | [11 empty] | Rated Average Lamp Life (hours/lamp for RS ballast @ 12 hours/start) | Lamp Cost ($/lamp) | Lamp Change Labor (hours/lamp)
Describe existing lamp/ballast combination here |  |  | <<Input a wattage and mean system lumens
----------------------------
Incandescent, 1-A 15W, no ballast | 15 | 95.45 | Screw-In CFL, 1-CF 9W, 1-Mag | [11 empty] | 1500 | 0.67 | 0.05
Incandescent, 1-A 25W, no ballast | 25 | 169.85 | Screw-In CFL, 1-CF 9W, 1-Mag | [11 empty] | 1500 | 0.67 | 0.05
Incandescent, 1-A 40W, no ballast | 40 | 402.5 | Screw-In CFL, 1-CF 9W, 1-Mag | [11 empty] | 1500 | 0.67 | 0.05
Incandescent, 1-A 50W, no ballast | 50 | 428.75 | Screw-In CFL, 1-CF 11W, 1-Mag | [11 empty] | 1200 | 0.67 | 0.05
Incandescent, 1-A 60W, no ballast | 60 | 799.8 | Screw-In CFL, 1-CF 15W, 1-Mag | [11 empty] | 1200 | 0.52 | 0.05
Incandescent, 1-A 75W, no ballast | 75 | 1085.6 | Hard-Wired CFL, 1-PL 20W, 1-Mag | [11 empty] | 1200 | 0.52 | 0.05
Incandescent, 1-A 100W, no ballast | 100 | 1548 | Hard-Wired CFL, 1-PL 26W, 1-Mag | [11 empty] | 1000 | 0.52 | 0.05
Incandescent, 1-A 150W, no ballast | 150 | 2536.5 | Hard-Wired CFL, 2-PL 23W, 2-Mag | [11 empty] | 1000 | 0.52 | 0.05
----------------------------
Incandescent, 2-A 15W, no ballast | 30 | 190.9 | Screw-In CFL, 1-CF 9W, 1-Mag | [11 empty] | 1500 | 0.67 | 0.05
Incandescent, 2-A 25W, no ballast | 50 | 339.7 | Screw-In CFL, 1-CF 11W, 1-Mag | [11 empty] | 1500 | 0.67 | 0.05
Incandescent, 2-A 40W, no ballast | 80 | 805 | Hard-Wired CFL, 1-PL 23W, 1-Mag | [11 empty] | 1500 | 0.67 | 0.05
Incandescent, 2-A 50W, no ballast | 100 | 857.5 | Hard-Wired CFL, 1-PL 26W, 1-Mag | [11 empty] | 1200 | 0.67 | 0.05
Incandescent, 2-A 60W, no ballast | 120 | 1599.6 | Hard-Wired CFL, 1-PL 32W, 1-Mag | [11 empty] | 1200 | 0.52 | 0.05
Incandescent, 2-A 75W, no ballast | 150 | 2171.2 | Hard-Wired CFL, 2-PL 23W, 2-Mag | [11 empty] | 1200 | 0.52 | 0.05
Incandescent, 2-A 100W, no ballast | 200 | 3096 | Hard-Wired CFL, 2-2D 28W, 1-Elec | [11 empty] | 1000 | 0.52 | 0.05
Incandescent, 2-A 150W, no ballast | 300 | 5073 | Hard-Wired CFL, 2-2D 38W, 1-Elec | [11 empty] | 1000 | 0.52 | 0.05
----------------------------
Incandescent, 3-A 15W, no ballast | 45 | 286.35 | Screw-In CFL, 1-CF 9W, 1-Mag | [11 empty] | 1500 | 0.67 | 0.05
Incandescent, 3-A 25W, no ballast | 75 | 509.55 | Hard-Wired CFL, 1-PL 20W, 1-Mag | [11 empty] | 1500 | 0.67 | 0.05
Incandescent, 3-A 40W, no ballast | 120 | 1207.5 | Hard-Wired CFL, 1-PL 32W, 1-Mag | [11 empty] | 1500 | 0.67 | 0.05
Incandescent, 3-A 50W, no ballast | 150 | 1286.25 | Hard-Wired CFL, 2-PL 23W, 2-Mag | [11 empty] | 1200 | 0.67 | 0.05
Incandescent, 3-A 60W, no ballast | 180 | 2399.4 | Hard-Wired CFL, 2-PL 23W, 2-Mag | [11 empty] | 1200 | 0.52 | 0.05
Incandescent, 3-A 75W, no ballast | 225 | 3256.8 | Hard-Wired CFL, 2-2D 28W, 1-Elec | [11 empty] | 1200 | 0.52 | 0.05
Incandescent, 3-A 100W, no ballast | 300 | 4644 | Hard-Wired CFL, 2-2D 38W, 1-Elec | [11 empty] | 1000 | 0.52 | 0.05
----------------------------
Incandescent, 4-A 40W, no ballast | 160 | 1610 | Hard-Wired CFL, 2-2D 28W, 1-Elec | [11 empty] | 1500 | 0.67 | 0.05
Incandescent, 4-A 60W, no ballast | 240 | 3199.2 | Hard-Wired CFL, 2-2D 28W, 1-Elec | [11 empty] | 1200 | 0.67 | 0.05
Incandescent, 4-A 75W, no ballast | 300 | 4342.4 | Hard-Wired CFL, 2-2D 28W, 1-Elec | [11 empty] | 1200 | 0.52 | 0.05
Incandescent, 4-A 100W, no ballast | 400 | 6192 | Hard-Wired CFL, 2-2D 28W, 1-Elec | [11 empty] | 1200 | 0.52 | 0.05
----------------------------
Incandescent, 1-R 75W, no ballast | 75 | 801 | Hard-Wired CFL, 1-PL 20W, 1-Mag | [11 empty] | 2000 | 7 | 0.09
Incandescent, 1-R 90W, no ballast | 90 | 1071 | Hard-Wired CFL, 1-PL 23W, 1-Mag | [11 empty] | 2000 | 7 | 0.09
Incandescent, 1-R 100W, no ballast | 100 | 1071 | Hard-Wired CFL, 1-PL 26W, 1-Mag | [11 empty] | 2000 | 7 | 0.09
Incandescent, 1-R 120W, no ballast | 120 | 1440 | Hard-Wired CFL, 1-PL 32W, 1-Mag | [11 empty] | 2000 | 7 | 0.09
Incandescent, 1-R 150W, no ballast | 150 | 1710 | Ceramic Metal Halide, 1-PAR 39W, 1-Elec | [11 empty] | 2000 | 7 | 0.09
----------------------------
Incandescent, 1-PAR 65W, no ballast | 65 | 607.5 | Screw-In CFL, 1-CF 15W, 1-Mag | [11 empty] | 2000 | 4 | 0.09
Incandescent, 1-PAR 75W, no ballast | 75 | 688.5 | Hard-Wired CFL, 1-PL 20W, 1-Mag | [11 empty] | 2000 | 4 | 0.09
Incandescent, 1-PAR 85W, no ballast | 85 | 837 | Hard-Wired CFL, 1-PL 23W, 1-Mag | [11 empty] | 2000 | 4 | 0.09
Incandescent, 1-PAR 100W, no ballast | 100 | 1260 | Hard-Wired CFL, 1-PL 26W, 1-Mag | [11 empty] | 2000 | 4 | 0.09
Incandescent, 1-PAR 150W, no ballast | 150 | 1566 | Ceramic Metal Halide, 1-PAR 39W, 1-Elec | [11 empty] | 2000 | 4 | 0.09
Incandescent, 2-PAR 150W, no ballast | 300 | 3132 | Hard-Wired CFL, 2-2D 38W, 1-Elec | [11 empty] | 2000 | 4 | 0.09
----------------------------
Incandescent, 1-PS30 200W, no ballast | 200 | 3153.5 | Hard-Wired CFL, 2-2D 28W, 1-Elec | [11 empty] | 750 | 4.29 | 0.09
Incandescent, 1-PS35 300W, no ballast | 300 | 4801.5 | Hard-Wired CFL, 2-2D 38W, 1-Elec | [11 empty] | 750 | 4.92 | 0.09
Incandescent, 1-PS40 500W, no ballast | 500 | 8811 | Ceramic Metal Halide, 1-SE 150W, 1-Elec | [11 empty] | 750 | 10.84 | 0.09
Incandescent, 1-PS40 620W, no ballast | 620 | 9350 | Ceramic Metal Halide, 1-SE 150W, 1-Elec | [11 empty] | 750 | 15.36 | 0.09
----------------------------
MR-16 or MRC-16 Halogen Display Lamps, 20W, no ballast | 20 | 240 | Ceramic Metal Halide, 1-39W, 1-Elec | [11 empty] | No Default | No Default | No Default
MR-16 or MRC-16 Halogen Display Lamps, 35W, no ballast | 35 | 490 | Ceramic Metal Halide, 1-39W, 1-Elec | [11 empty] | No Default | No Default | No Default
MR-16 or MRC-16 Halogen Display Lamps, 40W, no ballast | 40 | 600 | Ceramic Metal Halide, 1-70W, 1-Elec | [11 empty] | No Default | No Default | No Default
MR-16 or MRC-16 Halogen Display Lamps, 50W, no ballast | 50 | 790 | Ceramic Metal Halide, 1-100W, 1-Elec | [11 empty] | No Default | No Default | No Default
MR-16 or MRC-16 Halogen Display Lamps, 75W, no ballast | 75 | 1320 | Ceramic Metal Halide, 1-150W, 1-Elec | [11 empty] | No Default | No Default | No Default
----------------------------
Halogen, 1-T3 100W, no ballast | 100 | 1440 | Ceramic Metal Halide, 1-39W, 1-Elec | [11 empty] | 1500 | 5.99 | 0.09
Halogen, 1-T3 150W, no ballast | 150 | 2160 | Ceramic Metal Halide, 1-39W, 1-Elec | [11 empty] | 1500 | 5.99 | 0.09
Halogen, 1-T3 250W, no ballast | 250 | 3600 | Ceramic Metal Halide, 1-70W, 1-Elec | [11 empty] | 1500 | 6.55 | 0.09
Halogen, 1-T3 300W, no ballast | 300 | 4680 | Ceramic Metal Halide, 1-100W, 1-Elec | [11 empty] | 1500 | 7.05 | 0.09
Halogen, 1-T3 500W, no ballast | 500 | 8550 | Ceramic Metal Halide, 1-150W, 1-Elec | [11 empty] | 1500 | 6.98 | 0.09
Halogen, 1-T5 750W, no ballast | 750 | 13500 | Ceramic Metal Halide, 1-250W, 1-Elec | [11 empty] | 1500 | 14 | 0.09
Halogen, 1-T3 1000W, no ballast | 1000 | 18900 | Ceramic Metal Halide, 1-320W, 1-Elec | [11 empty] | 1500 | 14 | 0.09
Halogen, 1-T3 1500W, no ballast | 1500 | 29700 | Ceramic Metal Halide, 1-400W, 1-Elec | [11 empty] | 1500 | 14 | 0.09
=================================
T12 2' Fluorescent, 1-F24T12/CW 20W, 1-Mag | 24 | 960 | T5, 1-F14T5 | [11 empty] | 7500 | 2.17 | 0.09
T12 3' Fluorescent, 1-F36T12/CW 30W, 1-Mag | 36 | 1630 | T5, 1-F21T5 | [11 empty] | 18000 | 3.29 | 0.09
T12 2'x2' Fluorescent, 1-F40T12 40W U-Tube, 1-Mag | 48 | 2775 | T5, 2-F14T5 | [11 empty] | 20000 | 4.8 | 0.09
T12 2'x2' Fluorescent, 2-F40T12 40W U-Tube, 1-Mag | 86 | 5550 | T5, 3-F14T5 | [11 empty] | 20000 | 4.8 | 0.09
T12 6' Fluorescent, 1-F72T12/CW 56W, 1-Mag | 65 | 4000 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP | [11 empty] | 12000 | 4.28 | 0.09
----------------------------
T12 4' Fluorescent, 1-F40T12ES 34W, 1-Mag EE | 43 | 1890.51 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP RLO | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 1-F40T12 40W, 1-Mag EE | 46 | 2433.9 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 1-F40T12ES 34W, 1-Mag | 48 | 1933.97 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP RLO | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 1-F40T12 40W, 1-Mag | 52 | 2433.9 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP | [11 empty] | 20000 | 1.12 | 0.09
----------------------------
T12 4' Fluorescent, 2-F40T12ES 34W, 1-Mag EE | 72 | 3781.02 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 2-F40T12ES 34W, 1-Mag | 82 | 3867.94 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 2-F40T12 40W, 1-Mag EE | 88 | 4867.8 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 96 | 4867.8 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | [11 empty] | 20000 | 1.12 | 0.09
----------------------------
T12 4' Fluorescent, 3-F40T12ES 34W, 2-Mag EE | 106 | 5671.53 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 3-F40T12ES 34W, 2-Mag EE | 112 | 5671.53 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 126 | 7301.7 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 3-F40T12ES 34W, 2-Mag | 130 | 5801.91 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 134 | 7301.7 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 3-F40T12 40W, 2-Mag | 148 | 7301.7 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO | [11 empty] | 20000 | 1.12 | 0.09
----------------------------
T12 4' Fluorescent, 4-F40T12ES 34W, 2-Mag EE | 144 | 7562.04 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 4-F40T12ES 34W, 2-Mag | 164 | 7735.88 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 4-F40T12 40W, 2-Mag EE | 176 | 9735.6 | T8 High Performance, 4-F32T8HP 32W, 1-Elec HP RLO | [11 empty] | 20000 | 1.12 | 0.09
T12 4' Fluorescent, 4-F40T12 40W, 2-Mag | 192 | 9735.6 | T8 High Performance, 4-F32T8HP 32W, 1-Elec HP RLO | [11 empty] | 20000 | 1.12 | 0.09
=================================
T12 8' Fluorescent, 1-F96T12ES 60W, 1-Mag | 83 | 4258.65 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | [11 empty] | 12000 | 6 | 0.09
T12 8' Fluorescent, 1-F96T12 75W, 1-Mag | 100 | 5145.09 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP | [11 empty] | 12000 | 7.02 | 0.09
T12 8' Fluorescent, 1-F96T12HOES 95W, 1-Mag | 125 | 5728.8 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP | [11 empty] | 12000 | 7.63 | 0.09
T12 8' Fluorescent, 1-F96T12HO 110W, 1-Mag | 140 | 6715.94 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP HLO | [11 empty] | 12000 | 7.02 | 0.09
T12 8' Fluorescent, 1-F96T12VHOES 185W, 1-Mag | 200 | 8370 | T8 Fluorescent, 1-F96T8 59W, 1-Elec | [11 empty] | 12000 | 12.58 | 0.09
T12 8' Fluorescent, 1-F96T12VHO 215W, 1-Mag | 230 | 9525.6 | T8 Fluorescent, 1-F96T8 59W, 1-Elec | [11 empty] | 12000 | 11.58 | 0.09
----------------------------
T12 8' Fluorescent, 2-F96T12ES 60W, 1-Mag EE | 123 | 8321.5 | T8 Fluorescent, 4-F32T8 32W, 1-Elec | [11 empty] | 12000 | 6 | 0.09
T12 8' Fluorescent, 2-F96T12ES 60W, 1-Mag | 138 | 8517.3 | T8 Fluorescent, 4-F32T8 32W, 1-Elec | [11 empty] | 12000 | 6 | 0.09
T12 8' Fluorescent, 2-F96T12 75W, 1-Mag EE | 158 | 10180.71 | T8 Fluorescent, 4-F32T8 32W, 1-Elec | [11 empty] | 12000 | 7.02 | 0.09
T12 8' Fluorescent, 2-F96T12 75W, 1-Mag | 173 | 10290.18 | T8 Fluorescent, 4-F32T8 32W, 1-Elec | [11 empty] | 12000 | 7.02 | 0.09
T12 8' Fluorescent, 2-F96T12HOES 95W, 1-Mag | 227 | 11457.6 | T8 Fluorescent, 4-F32T8 32W, 2-Elec HLO | [11 empty] | 12000 | 7.63 | 0.09
T12 8' Fluorescent, 2-F96T12HO 110W, 1-Mag EE | 237 | 13431.88 | T8 Fluorescent, 4-F32T8 32W, 2-Elec HLO | [11 empty] | 12000 | 7.02 | 0.09
T12 8' Fluorescent, 2-F96T12HO 110W, 1-Mag | 252 | 13431.88 | T8 Fluorescent, 4-F32T8 32W, 2-Elec HLO | [11 empty] | 12000 | 7.02 | 0.09
T12 8' Fluorescent, 2-F96T12VHOES 185W, 1-Mag | 325 | 16740 | T8 Fluorescent, 2-F96T8HO 86W, 1-Elec | [11 empty] | 12000 | 12.58 | 0.09
T12 8' Fluorescent, 2-F96T12VHO 215W, 1-Mag | 440 | 19051.2 | T8 Fluorescent, 2-F96T8HO 86W, 1-Elec | [11 empty] | 12000 | 11.58 | 0.09
----------------------------
T12 8' Fluorescent, 3-F96T12ES 60W, 2-Mag | 220 | 12775.95 | T8 Fluorescent, 2-F96T8HO 86W, 1-Elec | [11 empty] | 12000 | 6 | 0.09
T12 8' Fluorescent, 3-F96T12 75W, 2-Mag | 274 | 15435.27 | T8 Fluorescent, 6-F32T8 32W, 1-Elec | [11 empty] | 12000 | 7.02 | 0.09
T12 8' Fluorescent, 3-F96T12HOES 95W, 2-Mag | 352 | 17186.4 | T8 Fluorescent, 6-F32T8 32W, 2-Elec HLO | [11 empty] | 12000 | 7.63 | 0.09
T12 8' Fluorescent, 3-F96T12HO 110W, 2-Mag EE | 392 | 20147.82 | T8 Fluorescent, 6-F32T8 32W, 2-Elec HLO | [11 empty] | 12000 | 7.02 | 0.09
----------------------------
T12 8' Fluorescent, 4-F96T12ES 60W, 2-Mag EE | 246 | 16643 | T8 Fluorescent, 4-F32T8 32W, 2-Elec HLO | [11 empty] | 12000 | 6 | 0.09
T12 8' Fluorescent, 4-F96T12ES 60W, 2-Mag | 276 | 17034.6 | T8 Fluorescent, 4-F32T8 32W, 2-Elec HLO | [11 empty] | 12000 | 6 | 0.09
T12 8' Fluorescent, 4-F96T12 75W, 2-Mag EE | 316 | 20361.42 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec | [11 empty] | 12000 | 7.02 | 0.09
T12 8' Fluorescent, 4-F96T12 75W, 2-Mag | 346 | 20580.36 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec | [11 empty] | 12000 | 7.02 | 0.09
T12 8' Fluorescent, 4-F96T12HOES 95W, 2-Mag EE | 416 | 22915.2 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec | [11 empty] | 12000 | 7.63 | 0.09
T12 8' Fluorescent, 4-F96T12HOES 95W, 2-Mag | 454 | 22915.2 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec | [11 empty] | 12000 | 7.02 | 0.09
T12 8' Fluorescent, 4-F96T12HO 110W, 2-Mag EE | 474 | 26863.76 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec | [11 empty] | 12000 | 7.02 | 0.09
T12 8' Fluorescent, 4-F96T12HO 110W, 2-Mag | 504 | 26863.76 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec | [11 empty] | 12000 | 7.02 | 0.09
T12 8' Fluorescent, 4-F96T12VHOES 185W, 2-Mag | 650 | 33480 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec | [11 empty] | 12000 | 12.58 | 0.09
T12 8' Fluorescent, 4-F96T12VHO 215W, 2-Mag | 880 | 38102.4 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec | [11 empty] | 12000 | 11.58 | 0.09
=================================
T12 Other Fluorescent, 1-F4T5 4W, 1-Mag Pre | 8 | 81.405 | None | [11 empty] | 6000 | 4.92 | 0.09
T12 Other Fluorescent, 1-F6T5 6W, 1-Mag Pre | 10 | 177.885 | None | [11 empty] | 7500 | 2.93 | 0.09
T12 Other Fluorescent, 1-F8T5 8W, 1-Mag Pre | 12 | 270 | None | [11 empty] | 7500 | 6.46 | 0.09
T12 Other Fluorescent, 1-F15T12 15W, 1-Mag Pre | 19 | 554.04 | None | [11 empty] | 7500 | 7.32 | 0.09
T12 Other Fluorescent, 1-F15T8 15W, 1-Mag Pre | 19 | 586.575 | None | [11 empty] | 7500 | 2.47 | 0.09
T12 Other Fluorescent, 1-F20T12 20W, 1-Mag Pre | 25 | 943.5 | None | [11 empty] | 9000 | 2.17 | 0.09
T12 Other Fluorescent, 1-FC6T9 20W, 1-Mag | 25 | 504 | None | [11 empty] | 10000 | 4.55 | 0.09
T12 Other Fluorescent, 1-FC8T9 22W, 1-Mag | 27 | 675 | None | [11 empty] | 10000 | 4.55 | 0.09
T12 Other Fluorescent, 1-F30T12ES 25W, 1-Mag | 42 | 1513.5312 | None | [11 empty] | 18000 | 3.89 | 0.09
T12 Other Fluorescent, 1-FC12T9 32W, 1-Mag | 45 | 1231.875 | None | [11 empty] | 10000 | 4.55 | 0.09
T12 Other Fluorescent, 1-F30T12 30W, 1-Mag | 46 | 1790.5688 | None | [11 empty] | 18000 | 3.29 | 0.09
T12 Other Fluorescent, 1-F30T12 30W, 1-Mag Pre | 46 | 1667.0813 | None | [11 empty] | 18000 | 3.29 | 0.09
T12 Other Fluorescent, 1-F30T8 30W, 1-Mag Pre | 46 | 1589.3813 | None | [11 empty] | 7500 | 3.85 | 0.09
T12 Other Fluorescent, 1-FB40T12 40W, 1-Mag EE | 48 | 2234.4 | None | [11 empty] | 18000 | 5.09 | 0.09
T12 Other Fluorescent, 1-FC16T9 40W, 1-Mag | 57 | 1822.5 | None | [11 empty] | 10000 | 4.55 | 0.09
----------------------------
T12 Other Fluorescent, 2-F20T12 20W, 1-Mag Pre | 50 | 1887 | None | [11 empty] | 9000 | 2.17 | 0.09
T12 Other Fluorescent, 2-F30T12ES 25W, 1-Mag EE | 66 | 3027.0625 | None | [11 empty] | 18000 | 3.89 | 0.09
T12 Other Fluorescent, 2-F30T12 30W, 1-Mag Pre EE | 74 | 3581.1375 | None | [11 empty] | 18000 | 3.29 | 0.09
T12 Other Fluorescent, 2-F30T12ES 25W, 1-Mag | 74 | 3027.0625 | None | [11 empty] | 18000 | 3.89 | 0.09
T12 Other Fluorescent, 2-F30T12 30W, 1-Mag | 79 | 3334.1625 | None | [11 empty] | 18000 | 3.29 | 0.09
T12 Other Fluorescent, 2-F30T12 30W, 1-Mag Pre | 79 | 3334.1625 | None | [11 empty] | 18000 | 3.29 | 0.09
T12 Other Fluorescent, 2-F30T8 30W, 1-Mag Pre | 79 | 3178.7625 | None | [11 empty] | 7500 | 3.85 | 0.09
T12 Other Fluorescent, 2-FB40T12 40W, 1-Mag EE | 86 | 4468.8 | None | [11 empty] | 18000 | 5.09 | 0.09
=================================
High Pressure Sodium, 35W, 1-Std Mag | 45 | 1845 | None | [11 empty] | 24000 | 15.72 | 0.4
High Pressure Sodium, 50W, 1-Std Mag | 68 | 3280 | None | [11 empty] | 24000 | 15.72 | 0.4
High Pressure Sodium, 70W, 1-Std Mag | 86 | 5166 | None | [11 empty] | 24000 | 15.72 | 0.4
High Pressure Sodium, 100W, 1-Std Mag | 120 | 7790 | None | [11 empty] | 24000 | 15.72 | 0.4
High Pressure Sodium, 150W, 1-Std Mag | 170 | 13120 | None | [11 empty] | 24000 | 15.72 | 0.4
High Pressure Sodium, 200W, 1-Std Mag | 245 | 18040 | None | [11 empty] | 24000 | 15.72 | 0.4
High Pressure Sodium, 250W, 1-Std Mag | 295 | 22550 | None | [11 empty] | 24000 | 15.72 | 0.4
High Pressure Sodium, 310W, 1-Std Mag | 365 | 30340 | None | [11 empty] | 24000 | 15.72 | 0.4
High Pressure Sodium, 400W, 1-Std Mag | 457 | 41000 | None | [11 empty] | 24000 | 15.72 | 0.4
High Pressure Sodium, 1000W, 1-Std Mag | 1100 | 114800 | None | [11 empty] | 24000 | 47.92 | 0.4
=================================
Mercury Vapor, 100W, 1-Std Mag | 125 | 3400 | Hard-Wired CFL, 2-PL 32W, 1-Elec | [11 empty] | 24000 | 12.35 | 0.4
Mercury Vapor, 175W, 1-Std Mag | 205 | 7600 | T8 Fluorescent, 2-F32T8 32W, 1-Elec HLO | [11 empty] | 24000 | 12.35 | 0.4
Mercury Vapor, 250W, 1-Std Mag | 285 | 10700 | T5HO Fluorescent, 2-F54T5HO 54W, 1-Elec | [11 empty] | 24000 | 13.85 | 0.4
Mercury Vapor, 400W, 1-Std Mag | 454 | 19100 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec | [11 empty] | 24000 | 18.34 | 0.4
Mercury Vapor, 1000W, 1-Std Mag | 1080 | 45000 | MH Pulse Start, 1-PS 400W, 1-Elec | [11 empty] | 24000 | 64.08 | 0.4
=================================
Metal Halide, 50W, 1-Std Mag | 62 | 2006 | Hard-Wired CFL, 1-PL 32W, 1-Elec | [11 empty] | 10000 | 23.01 | 0.4
Metal Halide, 70W, 1-Std Mag | 90 | 2950 | Hard-Wired CFL, 2-PL 26W, 1-Elec | [11 empty] | 10000 | 23.01 | 0.4
Metal Halide, 100W, 1-Std Mag | 129 | 5440 | Hard-Wired CFL, 2-PL 42W, 1-Elec | [11 empty] | 10000 | 18.4 | 0.4
Metal Halide, 150W, 1-Std Mag | 185 | 8640 | T8 High Performance, 4-F32T8HP 32W, 1-Elec HP | [11 empty] | 10000 | 18.4 | 0.4
Metal Halide, 175W, 1-Std Mag | 210 | 9400 | T5HO Fluorescent, 2-F54T5HO 54W, 1-Elec | [11 empty] | 10000 | 18.4 | 0.4
Metal Halide, 250W, 1-Std Mag | 295 | 11300 | T5HO Fluorescent, 3-F54T5HO 54W, 1-Elec | [11 empty] | 10000 | 18.4 | 0.4
Metal Halide, 400W, 1-Std Mag | 458 | 26000 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec | [11 empty] | 10000 | 18.4 | 0.4
Metal Halide, 1000W, 1-Std Mag | 1080 | 78000 | MH Pulse Start, 750W, 1-PS Mag | [11 empty] | 10000 | 41.41 | 0.4
Metal Halide, 1500W, 1-Std Mag | 1605 | 132000 | MH Pulse Start, 1000W, 1-PS Mag | [11 empty] | 10000 | 47.41 | 0.4
=================================
Exit Sign, 2-inc 5W, no ballast | 10 | 2 | New Exit Sign, 1-LED <5W, 1-None | [11 empty] | 10000 | 2.31 | 0.1
Exit Sign, 2-inc 8W, no ballast | 16 | 2 | New Exit Sign, 1-LED <5W, 1-None | [11 empty] | 10000 | 2.31 | 0.1
Exit Sign, 2-Inc 10W, no ballast | 20 | 2 | New Exit Sign, 1-LED <5W, 1-None | [11 empty] | 10000 | 2.31 | 0.1
Exit Sign, 2-Inc 11W, no ballast | 22 | 2 | New Exit Sign, 1-LED <5W, 1-None | [11 empty] | 10000 | 2.31 | 0.1
Exit Sign, 2-Inc 15W, no ballast | 30 | 2 | New Exit Sign, 1-LED <5W, 1-None | [11 empty] | 10000 | 2.31 | 0.1
Exit Sign, 2-Inc 20W, no ballast | 40 | 2 | New Exit Sign, 1-LED <5W, 1-None | [11 empty] | 10000 | 2.31 | 0.1
Exit Sign, 2-Inc 25W, no ballast | 50 | 2 | New Exit Sign, 1-LED <5W, 1-None | [11 empty] | 10000 | 2.31 | 0.1
Exit Sign, 2-Inc 40W, no ballast | 80 | 2 | New Exit Sign, 1-LED <5W, 1-None | [11 empty] | 10000 | 2.31 | 0.1
=================================

## Data Proposed
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Updated October 1, 2006. This list is not meant to be complete, you can add qualifying equipment to this list. | [14 empty] | Default lamp life and cost data used for estimating life-cycle periodic replacement costs.
Description of Proposed Lamp/Ballast Combination | Input Watts | Mean System Lumens | Measure Category | Rebate Amount | Notes / Alternate Suggestions |  | # lamps | bf | lumen lamp | lumen maint | ballast type | BEF | LPW |  | Rated Average Lamp Life (hrs/lamp for RS ballast @ 12 hrs/start) | Lamp Cost ($/lamp) | Lamp Change Labor (hours/lamp)
Add qualifying measure(s) here. See the technical specifications for guidance. |  |  |  | 0 | <<Input a wattage and mean system lumens
No recommendation (leave fixture as-is) |  |  |  |  | Leave fixture as-is
Decommission (Permanently Remove) Lighting Fixture | 0 | 0 | N/A | 0 | Permanently remove unneeded light fixtures
----------------------------
T8HP 4', 1-F32T8, 3100+lumen, 1-RLO Sylvania Quicktronic QHE/UNV ISL-SC | 25 | 2297.1 | A1 | 15 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD |  | 1 | 0.78 | 3100 | 0.95 | ISL | 3.12 | 96.72 |  | 30000 | 3.25 | 0.09
T8HP 4', 1-F32T8, 3100+lumen, 1-RLO Universal Triad Ultim8 B132IUNVEL-A | 25 | 2267.65 | A1 | 15 | Universal-Voltage, Instant-Start, Reduced Output |  | 1 | 0.77 | 3100 | 0.95 | PRS | 3.08 | 95.48 |  | 30000 | 3.25 | 0.09
T8HP 4', 1-F32T8, 3100+lumen, 1-RLO GE-132-Ultramax-L | 25 | 2267.65 | A1 | 15 | Universal-Voltage, Instant-Start, Low-Output |  | 1 | 0.77 | 3100 | 0.95 | ISL | 3.08 | 95.48 |  | 30000 | 3.25 | 0.09
T8HP 4', 1-F32T8, 3100+lumen, 1-RLO Advance Optanium IOP-2P32-LW-SC | 25 | 2267.65 | A1 | 15 | High Efficiency, Intellivolt, Instant-Start |  | 1 | 0.77 | 3100 | 0.95 | ISL | 3.08 | 95.48 |  | 30000 | 3.25 | 0.09
T8HP 4', 1-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QHE/UNV ISN-SC | 28 | 2591.6 | A1 | 15 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD |  | 1 | 0.88 | 3100 | 0.95 | ISN | 3.1429 | 97.4286 |  | 30000 | 3.25 | 0.09
T8HP 4', 1-F32T8, 3100+lumen, 1-NLO Universal Triad Ultim8 B132IUNVHE-A | 28 | 2562.15 | A1 | 15 | Universal-Voltage, Instant-Start, Normal-Output |  | 1 | 0.87 | 3100 | 0.95 | PRS | 3.1071 | 96.3214 |  | 30000 | 3.25 | 0.09
T8HP 4', 1-F32T8, 3100+lumen, 1-NLO GE-132/232-Ultramax-N | 28 | 2562.15 | A1 | 15 | Universal-Voltage, Instant-Start, Normal-Output |  | 1 | 0.87 | 3100 | 0.95 | ISN | 3.1071 | 96.3214 |  | 30000 | 3.25 | 0.09
T8HP 4', 1-F32T8, 3100+lumen, 1-NLO Advance Optanium IOP/ROP/VOP-2P32-SC | 28 | 2562.15 | A1 | 15 | Intellivolt or Dedicated-Voltage, Instant-Start, Normal-Output |  | 1 | 0.87 | 3100 | 0.95 | ISN | 3.1071 | 96.3214 |  | 30000 | 3.25 | 0.09
T8HP 4', 1-F32T8, 3100+lumen, 1-NLO Advance Optanium RCN/VCN-132-MC | 29 | 2886.1 | A1 | 15 | Dedicated-Voltage, Optanium, Centium, Micro Can |  | 1 | 0.98 | 3100 | 0.95 | ISN | 3.3793 | 104.7586 |  | 30000 | 3.25 | 0.09
T8HP 4', 1-F32T8, 3100+lumen, 1-NLO Advance Optanium IOP-2S32-SC | 29 | 2650.5 | A1 | 15 | Intellivolt, Optanium 2-lamp Program-Start operating 1 lamp |  | 1 | 0.9 | 3100 | 0.95 | PRS | 3.1034 | 96.2069 |  | 30000 | 3.25 | 0.09
T8HP 4', 1-F32T8, 3100+lumen, 1-HLO Universal B232PUNVHP-A | 32 | 2945 | A1 | 15 | Universal-Voltage, 2-lamp Program-Start operating 1 lamp |  | 1 | 1 | 3100 | 0.95 | PRS | 3.125 | 96.875 |  | 30000 | 3.25 | 0.09
T8HP 4', 1-F32T8, 3100+lumen, 1-HLO Universal B232I120HE | 33 | 3033.35 | A1 | 15 | 120 Volt, High-Efficency 2-lamp Instant-Start operating 1 lamp |  | 1 | 1.03 | 3100 | 0.95 | ISH | 3.1212 | 96.7576 |  | 30000 | 3.25 | 0.09
---------------------------- | [11 empty] | 1.6/1.58/1.55/1.48/1.47 | 95
T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Sylvania Extreme/UNV PSX-TC | 46 | 4181.9 | A2 | 30 | Use Program-Rapid-Start on frequently switched circuits |  | 2 | 0.71 | 3100 | 0.95 | PRS | 1.5435 | 95.6957 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Sylvania Quicktronic QHE/UNV ISL-SC | 48 | 4594.2 | A2 | 30 | Best Energy Efficient Choice, High-Eff, Univ-Volt, IS, Low-THD |  | 2 | 0.78 | 3100 | 0.95 | ISL | 1.625 | 100.75 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Advance Optanium IOP/ROP/VOP-2P32-LW-SC | 48 | 4594.2 | A2 | 30 | Best Energy Efficient Choice, Dedicated-Voltage, Instant-Start |  | 2 | 0.78 | 3100 | 0.95 | ISL | 1.625 | 100.75 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Universal Ultim8 B232I120EL or 277EL | 48 | 4594.2 | A2 | 30 | Best Energy Efficient Choice, Dedicated-Voltage, Instant-Start |  | 2 | 0.78 | 3100 | 0.95 | ISL | 1.625 | 100.75 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-RLO GE-232-Ultramax-L | 48 | 4535.3 | A2 | 30 | Best Energy Efficient Choice, Universal-Voltage, Low-Output |  | 2 | 0.77 | 3100 | 0.95 | ISL | 1.6042 | 99.4583 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Advance Centium RCN/VCN-2P32-LW | 50 | 4594.2 | A2 | 30 | Dedicated-Voltage, Centium Low-THD, Low-Output |  | 2 | 0.78 | 3100 | 0.95 | ISL | 1.56 | 96.72 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO GE-232/332-Ultramax-N | 53 | 5124.3 | A2 | 30 | Universal-Voltage, Instant-Start, Normal-Output |  | 2 | 0.87 | 3100 | 0.95 | ISN | 1.6415 | 101.7736 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QHE/UNV ISN-SC | 55 | 5183.2 | A2 | 30 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD |  | 2 | 0.88 | 3100 | 0.95 | ISN | 1.6 | 99.2 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO Advance Optanium IOP/ROP/VOP-2P32-SC | 55 | 5183.2 | A2 | 30 | Intellivolt or Dedicated-Voltage, Instant-Start, Normal-Output |  | 2 | 0.88 | 3100 | 0.95 | ISN | 1.6 | 99.2 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO Universal Ultim8 B232I120HE or 277HE | 55 | 5183.2 | A2 | 30 | Dedicated-Voltage, High-Efficiency Instant-Start, Normal-Output |  | 2 | 0.88 | 3100 | 0.95 | ISN | 1.6 | 99.2 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO Advance Optanium IOP-2S32-SC | 56 | 5183.2 | A2 | 30 | Intellivolt (120, 230, or 277 Volt), Optanium Program-Start |  | 2 | 0.88 | 3100 | 0.95 | PRS | 1.5714 | 97.4286 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3150+lumen, 1-NLO Universal Ultim8 B232IUNV | 58 | 5266.8 | A2 | 30 | Universal-Voltage, 2 lamp Instant-Start, Normal-Output |  | 2 | 0.88 | 3150 | 0.95 | ISN | 1.5172 | 95.5862 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Centium Intellivolt ICN-3P32 | 65 | 5948.9 | A2 | 30 | Use Intellivolt Low-THD Centium ballasts only if needed |  | 2 | 1.01 | 3100 | 0.95 | ISH | 1.5538 | 96.3385 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO GE-232-Ultramax-H | 74 | 6773.5 | A2 | 30 | Universal-Voltage, Instant-Start, High-Output |  | 2 | 1.15 | 3100 | 0.95 | ISH | 1.5541 | 96.3514 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Elec REL/VEL-2P32-HL-SC | 77 | 7068 | A2 | 30 | Dedicated-Voltage, standard electronic HLO can be efficient |  | 2 | 1.2 | 3100 | 0.95 | ISH | 1.5584 | 96.6234 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Sylvania Quicktronic QT2x32/120/277 Plus | 78 | 7068 | A2 | 30 | Dedicated-Voltage, standard electronic HLO can be efficient |  | 2 | 1.2 | 3100 | 0.95 | ISH | 1.5385 | 95.3846 |  | 30000 | 3.25 | 0.09
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Elec REL/VEL-3P32-HL-SC | 85 | 7774.8 | A2 | 30 | Dedicated-Voltage, standard electronic VHLO ballast |  | 2 | 1.32 | 3100 | 0.95 | ISH | 1.5529 | 96.2824 |  | 30000 | 3.25 | 0.09
---------------------------- | [12 empty] | 95
T8HP 8', 2-F96T8, 5780+lumens Alto+, 1-Universal B259I277HE | 106 | 9664.16 | A2 | 30 | Best Energy Efficient Choice, 277 Volt, High-Eff Instant-Start |  | 2 | 0.88 | 5780 | 0.95 | ISN | 0.83019 | 95.9698 |  | 18000 | 8.99 | 0.09
T8HP 8', 2-F96T8, 5900+lumens Alto+, 1-Universal B259I120HE | 106 | 9864.8 | A2 | 30 | Best Energy Efficient Choice, 120 Volt, High-Eff Instant-Start |  | 2 | 0.88 | 5900 | 0.95 | ISN | 0.83019 | 97.9623 |  | 18000 | 8.99 | 0.09
T8HP 8', 2-F96T8, 5900+lumens Alto+, 1-Universal B259I277HE | 108 | 9864.8 | A2 | 30 | Best Energy Efficient Choice, 277 Volt, High-Eff Instant-Start |  | 2 | 0.88 | 5900 | 0.95 | ISN | 0.81481 | 96.1481 |  | 18000 | 8.99 | 0.09
T8HP 8', 2-F96T8, 5950+lumens GE XL Starcoat, 1-Universal B259I120HE | 106 | 9948.4 | A2 | 30 | Best Energy Efficient Choice, 120 Volt, High-Eff Instant-Start |  | 2 | 0.88 | 5950 | 0.95 | ISN | 0.83019 | 98.7925 |  | 18000 | 8.99 | 0.09
T8HP 8', 2-F96T8, 5950+lumens GE XL Starcoat, 1-Universal B259I277HE | 108 | 9948.4 | A2 | 30 | Best Energy Efficient Choice, 277 Volt, High-Eff Instant-Start |  | 2 | 0.88 | 5950 | 0.95 | ISN | 0.81481 | 96.963 |  | 18000 | 8.99 | 0.09
T8HP 8', 2-F96T8, 6100+lumens, 1-Sylvania Quicktronic 2x59/120 or 277v IS | 110 | 10199.2 | A2 | 30 | Dedicated-Voltage, Instant-Start, 12 hours per start |  | 2 | 0.88 | 6100 | 0.95 | ISN | 0.8 | 97.6 |  | 18000 | 8.99 | 0.09
T8HP 8', 2-F96T8, 6100+lumens, 1-Advance Centium RCN/VCN-2P59 | 110 | 10199.2 | A2 | 30 | Dedicated-Voltage, Instant-Start, 12 hours per start |  | 2 | 0.88 | 6100 | 0.95 | ISN | 0.8 | 97.6 |  | 18000 | 8.99 | 0.09
---------------------------- | [11 empty] | 1.04/1.05/1.04/0.97/1.0 | 95
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO TCP 4/3/2IS32-120U | 65.8 | 6184.5 | A2 | 30 | Best Energy Efficient Choice with significant light reduction |  | 3 | 0.7 | 3100 | 0.95 | ISL | 1.0638 | 98.9362 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Universal Ultim8 B332I277EL | 70 | 6891.3 | A2 | 30 | Best Energy Efficient Choice, 277 Volt, standard electronic |  | 3 | 0.78 | 3100 | 0.95 | ISL | 1.1143 | 103.6286 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Universal Ultim8 B332I120EL | 71 | 6891.3 | A2 | 30 | Best Energy Efficient Choice, 120 Volt, standard electronic |  | 3 | 0.78 | 3100 | 0.95 | ISL | 1.0986 | 102.169 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Optanium IOP/ROP/VOP-3P32-LW-SC | 72 | 6891.3 | A2 | 30 | Intellivolt or Dedicated-Voltage, Instant-Start, Low-Output |  | 3 | 0.78 | 3100 | 0.95 | ISL | 1.0833 | 100.75 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Sylvania Quicktronic QHE/UNV ISL-SC | 73 | 6891.3 | A2 | 30 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD |  | 3 | 0.78 | 3100 | 0.95 | ISL | 1.0685 | 99.3699 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO GE-332-Ultramax-L | 73 | 6802.95 | A2 | 30 | Universal-Voltage, Instant-Start, Low-Output |  | 3 | 0.77 | 3100 | 0.95 | ISL | 1.0548 | 98.0959 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Maxlite 50014 | 74 | 6802.95 | A2 | 30 | Reduced-Output |  | 3 | 0.77 | 3100 | 0.95 | ISL | 1.0405 | 96.7703 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Centium RCN/VCN-3P32-LW-SC | 75 | 6979.65 | A2 | 30 | Dedicated-Voltage, Low-THD, Low-Output |  | 3 | 0.79 | 3100 | 0.95 | ISL | 1.0533 | 97.96 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Universal Ultim8 B332I277HE | 80 | 7774.8 | A2 | 30 | 277 Volt, High-Efficiency Instant-Start |  | 3 | 0.88 | 3100 | 0.95 | ISN | 1.1 | 102.3 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Universal Ultim8 B332I120HE | 81 | 7774.8 | A2 | 30 | 120 Volt, High-Efficiency, Instant-Start |  | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0864 | 101.037 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Optanium IOP/ROP/VOP-3P32-SC | 82 | 7774.8 | A2 | 30 | Intellivolt or Dedicated-Voltage, Instant-Start, Normal-Output |  | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0732 | 99.8049 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Optanium IOP-3S32-SC | 82 | 7774.8 | A2 | 30 | Intellivolt (120, 230, or 277 Volt), Optanium Program-Start |  | 3 | 0.88 | 3100 | 0.95 | PRS | 1.0732 | 99.8049 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO GE-332-Ultramax-N | 82 | 7686.45 | A2 | 30 | Universal-Voltage, Instant-Start, Normal Light Output |  | 3 | 0.87 | 3100 | 0.95 | ISN | 1.061 | 98.6707 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QHE/UNV ISN-SC | 83 | 7774.8 | A2 | 30 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD |  | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0602 | 98.6024 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Optanium ROP/VOP-3P32-SC | 83 | 7774.8 | A2 | 30 | Dedicated-Voltage, Instant-Start |  | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0602 | 98.6024 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Elec REL/VEL-3P32-SC | 85 | 7774.8 | A2 | 30 | Dedicated-Voltage, standard Instant-Start |  | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0353 | 96.2824 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Centium RCN/VCN-3P32-SC | 85 | 7774.8 | A2 | 30 | Dedicated-Voltage, Centium Low-THD |  | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0353 | 96.2824 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Centium Intellivolt ICN-3P32 | 85 | 7774.8 | A2 | 30 | Intellivolt, Centium Low-THD |  | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0353 | 96.2824 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Universal Ultim8 B332IUNVHP-A | 86 | 7774.8 | A2 | 30 | Universal-Voltage, Instant-Start, Normal Light Output |  | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0233 | 95.1628 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QT3x32/120/277/ISN-SC | 87 | 7863.15 | A2 | 30 | Dedicated-Voltage, standard Instant-Start, Normal Light Output |  | 3 | 0.89 | 3100 | 0.95 | ISN | 1.023 | 95.1379 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-Advance Bi-Level REL/VEL-4P32-2LS | 93 | 8481.6 | A2 | 30 | Use Bi-Level Switching where possible |  | 3 | 0.96 | 3100 | 0.95 | ISN | 1.0323 | 96 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-HLO Advance Elec REL/VEL-3P32-HL-SC | 111 | 10513.65 | A2 | 30 | Use HLO system only if absolutely necessary |  | 3 | 1.19 | 3100 | 0.95 | ISH | 1.0721 | 99.7027 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-HLO GE-332-Ultramax-H | 111 | 10160.25 | A2 | 30 | Use HLO system only if absolutely necessary |  | 3 | 1.15 | 3100 | 0.95 | ISH | 1.036 | 96.3514 |  | 30000 | 3.25 | 0.09
T8HP 4', 3-F32T8, 3100+lumen, 1-HLO Sylvania Quicktronic QT3X32/120/277/IS Plus | 112 | 10425.3 | A2 | 30 | Use HLO system only if absolutely necessary |  | 3 | 1.18 | 3100 | 0.95 | ISH | 1.0536 | 97.9821 |  | 30000 | 3.25 | 0.09
---------------------------- | [11 empty] | 0.79/0.8/0.77/0.76/0.75 | 95
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO TCP 4/3/2IS32-120U | 82 | 8128.2 | A2 | 30 | Best Energy Efficient Choice with significant light reduction |  | 4 | 0.69 | 3100 | 0.95 | ISL | 0.84146 | 104.3415 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Sylvania Extreme/UNV PSX-SC | 91 | 8363.8 | A2 | 30 | Use Program-Rapid-Start Ballasts on frequently switched circuits |  | 4 | 0.71 | 3100 | 0.95 | PRS | 0.78022 | 96.7473 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 2-RLO Sylvania Extreme/UNV PSX-TC | 92 | 8363.8 | A2 | 30 | Use Bi-Level Program-Rapid-Start where possible |  | 4 | 0.71 | 3100 | 0.95 | PRS | 0.77174 | 95.6957 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Universal Ultim8 B432I277EL | 94 | 9188.4 | A2 | 30 | Best Energy Efficient Choice, 277 Volt, standard Instant-Start |  | 4 | 0.78 | 3100 | 0.95 | ISL | 0.82979 | 102.8936 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Sylvania Quicktronic QHE/UNV ISL-SC | 95 | 9188.4 | A2 | 30 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD |  | 4 | 0.78 | 3100 | 0.95 | ISL | 0.82105 | 101.8105 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Universal Ultim8 B432I120EL | 95 | 9188.4 | A2 | 30 | 120 Volt, standard Instant-Start |  | 4 | 0.78 | 3100 | 0.95 | ISL | 0.82105 | 101.8105 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Advance Optanium IOP/ROP/VOP-4P32-LW-SC | 95 | 9188.4 | A2 | 30 | Intellivolt or Dedicated-Voltage, Instant-Start, Low-Output ballast |  | 4 | 0.78 | 3100 | 0.95 | ISL | 0.82105 | 101.8105 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO GE-432-Ultramax-L | 97 | 9070.6 | A2 | 30 | Universal-Voltage, Instant-Start, Low-Output |  | 4 | 0.77 | 3100 | 0.95 | ISL | 0.79381 | 98.433 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Sylvania Quicktronic QT4x32/120/277 LP | 98 | 9070.6 | A2 | 30 | Dedicated-Voltage, standard Instant-Start, Low-Output |  | 4 | 0.77 | 3100 | 0.95 | ISL | 0.78571 | 97.4286 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Advance Centium RCN/VCN-4P32-LW-SC | 99 | 8952.8 | A2 | 30 | Dedicated-Voltage, Centium Low-THD, Low-Output, Small-Can |  | 4 | 0.76 | 3100 | 0.95 | ISL | 0.76768 | 95.1919 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Universal Ultim8 B432I277HE | 107 | 10366.4 | A2 | 30 | 277 Volt, High Efficiency Instant-Start |  | 4 | 0.88 | 3100 | 0.95 | ISN | 0.82243 | 101.9813 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QHE/UNV ISN-SC | 108 | 10366.4 | A2 | 30 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD |  | 4 | 0.88 | 3100 | 0.95 | ISN | 0.81481 | 101.037 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Universal Ultim8 B432I120HE | 108 | 10366.4 | A2 | 30 | 120 Volt, High-Efficiency Instant-Start |  | 4 | 0.88 | 3100 | 0.95 | ISN | 0.81481 | 101.037 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Advance Optanium IOP/ROP/VOP-4P32-SC | 108 | 10366.4 | A2 | 30 | Intellivolt or Dedicated-Voltage, Instant-Start, Norm-Output, |  | 4 | 0.88 | 3100 | 0.95 | ISN | 0.81481 | 101.037 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO GE-432-Ultramax-N | 109 | 10248.6 | A2 | 30 | Universal-Voltage, Instant-Start, Normal-Output |  | 4 | 0.87 | 3100 | 0.95 | ISN | 0.79817 | 98.9725 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Advance Optanium IOP-2S32-SC | 110 | 10366.4 | A2 | 30 | Intellivolt (120, 230, or 277 Volt), Optanium Program-Start |  | 4 | 0.88 | 3100 | 0.95 | PRS | 0.8 | 99.2 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-Advance Bi-Level REL/VEL-4P32-2LS | 110 | 10248.6 | A2 | 30 | Use Bi-Level Switching where possible |  | 4 | 0.87 | 3100 | 0.95 | ISN | 0.79091 | 98.0727 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Advance Elec REL/VEL-4P32-SC | 112 | 10366.4 | A2 | 30 | Dedicated-Voltage, standard Instant-Start, Small-Can |  | 4 | 0.88 | 3100 | 0.95 | ISN | 0.78571 | 97.4286 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Advance Centium RCN/VCN-4P32-SC | 112 | 10366.4 | A2 | 30 | Dedicated-Voltage, Centium Low-THD, Normal-Output |  | 4 | 0.88 | 3100 | 0.95 | ISN | 0.78571 | 97.4286 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Advance Centium Intellivolt ICN-4P32-SC | 112 | 10366.4 | A2 | 30 | Intellivolt, Centium Low-THD |  | 4 | 0.88 | 3100 | 0.95 | ISN | 0.78571 | 97.4286 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QT/120/277ISN-SC | 114 | 10484.2 | A2 | 30 | Dedicated-Voltage, standard Instant-Start |  | 4 | 0.89 | 3100 | 0.95 | ISN | 0.7807 | 96.807 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QTP4x32/UNV-ISN-SC | 114 | 10366.4 | A2 | 30 | Universal-Voltage, standard Instant-Start |  | 4 | 0.88 | 3100 | 0.95 | ISN | 0.77193 | 95.7193 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 2-HLO Advance Elec REL/VEL-3P32-SC | 130 | 12133.4 | K2 | 40 | Use 2-2 lamp HLO ballasts only if absolutely necessary |  | 4 | 1.03 | 3100 | 0.95 | ISH | 0.79231 | 98.2462 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 1-HLO GE-432-Ultramax-H | 147 | 13547 | K2 | 40 | Universal-Voltage, Instant-Start, High-Output |  | 4 | 1.15 | 3100 | 0.95 | ISH | 0.78231 | 97.0068 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 2-HLO GE-232-Ultramax-H | 148 | 13547 | K2 | 40 | Use 2-2 lamp HLO ballasts only if absolutely necessary |  | 4 | 1.15 | 3100 | 0.95 | ISH | 0.77703 | 96.3514 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 2-HLO Advance Elec REL/VEL-2P32-HL-SC | 154 | 14136 | K2 | 40 | Use 2-2 lamp HLO ballasts only if absolutely necessary |  | 4 | 1.2 | 3100 | 0.95 | ISH | 0.77922 | 96.6234 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 2-HLO Sylvania Quicktronic QT2x32/120/277 Plus | 156 | 14136 | K2 | 40 | Dedicated-Voltage, standard electronic HLO can be efficient |  | 4 | 1.2 | 3100 | 0.95 | ISH | 0.77 | 95.38 |  | 30000 | 3.25 | 0.09
T8HP 4', 4-F32T8, 3100+lumen, 2-HLO Advance Elec REL/VEL-3P32-HL-SC | 170 | 15549.6 | K2 | 40 | Use 2-3 lamp HLO ballasts only if absolutely necessary |  | 4 | 1.32 | 3100 | 0.95 | ISH | 0.77647 | 96.2824 |  | 30000 | 3.25 | 0.09
New T8HP Fixture 4', 4-F32T8, 3100+lumen, 1-HLO GE-432-Ultramax-H | 147 | 13547 | H2 | 100 | Universal-Voltage, Instant-Start, High-Output |  | 4 | 1.15 | 3100 | 0.95 | ISH | 0.78231 | 97.0068 |  | 30000 | 3.25 | 0.09
---------------------------- | [12 empty] | 95
T8HP 4', 6-F32T8, 3100+lumen, 1-2 lamp & 1-4 lamp RLO Sylvania Extreme | 137 | 12545.7 | K2 | 40 | Use Bi-Level ProgStart System on frequently switched circuits |  | 6 | 0.71 | 3100 | 0.95 | ISL | 0.51825 | 96.3942 |  | 30000 | 3.25 | 0.09
T8HP 4', 6-F32T8, 3100+lumen, 2-HLO GE-332-Ultramax-H | 222 | 20320.5 | K2 | 40 | Use 2-3 lamp HLO system only if absolutely necessary |  | 6 | 1.15 | 3100 | 0.95 | ISH | 0.51802 | 96.3514 |  | 30000 | 3.25 | 0.09
T8HP 4', 6-F32T8, 3100+lumen, 2-HLO Advance Elec REL/VEL-4P32-HL-SC | 222 | 21027.3 | K2 | 40 | Use 2-4 lamp HLO ballasts only if absolutely necessary |  | 6 | 1.19 | 3100 | 0.95 | ISH | 0.53604 | 99.7027 |  | 30000 | 3.25 | 0.09
T8HP 4', 6-F32T8, 3100+lumen, 2-HLO Sylvania Quicktronic QT/3x32/120/277 Plus | 224 | 20850.6 | K2 | 40 | Use 2-3 lamp HLO system only if absolutely necessary |  | 6 | 1.18 | 3100 | 0.95 | ISH | 0.52679 | 97.9821 |  | 30000 | 3.25 | 0.09
T8HP 4', 6-F32T8, 3100+lumen, 3-HLO Advance Elec REL/VEL-3P32-HL-SC | 255 | 23324.4 | K2 | 40 | Use 3-3 lamp HLO ballasts only if absolutely necessary |  | 6 | 1.32 | 3100 | 0.95 | ISH | 0.51765 | 96.2824 |  | 30000 | 3.25 | 0.09
New T8HP Fixture 4', 6-F32T8, 3100+lumen, 1-2 lamp & 1-4 lamp RLO Sylvania Extreme | 137 | 12545.7 | H2 | 100 | Use Bi-Level ProgStart System on frequently switched circuits |  | 6 | 0.71 | 3100 | 0.95 | ISL | 0.51825 | 96.3942 |  | 30000 | 3.25 | 0.09
New T8HP Fixture 4', 6-F32T8, 3100+lumen, 2-HLO GE-332-Ultramax-H | 222 | 20320.5 | H3 | 120 | Use 2-3 lamp HLO system only if absolutely necessary |  | 6 | 1.15 | 3100 | 0.95 | ISH | 0.51802 | 96.3514 |  | 30000 | 3.25 | 0.09
New T8HP Fixture 4', 6-F32T8, 3100+lumen, 2-HLO Advance Elec REL/VEL-4P32-HL-SC | 222 | 21027.3 | H3 | 120 | Use 2-4 lamp HLO ballasts only if absolutely necessary |  | 6 | 1.19 | 3100 | 0.95 | ISH | 0.53604 | 99.7027 |  | 30000 | 3.25 | 0.09
New T8HP Fixture 4', 6-F32T8, 3100+lumen, 2-HLO Sylvania Quicktronic QT/3x32/120/277 Plus | 224 | 20850.6 | H3 | 120 | Use 2-3 lamp HLO system only if absolutely necessary |  | 6 | 1.18 | 3100 | 0.95 | ISH | 0.52679 | 97.9821 |  | 30000 | 3.25 | 0.09
New T8HP Fixture 4', 6-F32T8, 3100+lumen, 3-HLO Advance Elec REL/VEL-3P32-HL-SC | 255 | 23324.4 | H4 | 140 | Use 3-3 lamp HLO ballasts only if absolutely necessary |  | 6 | 1.32 | 3100 | 0.95 | ISH | 0.51765 | 96.2824 |  | 30000 | 3.25 | 0.09
---------------------------- | [12 empty] | 95
New T8HP Fixture 4', 8-F32T8, 3100+lumen, 2-4 lamp RLO Sylvania Extreme | 182 | 16727.6 | H2 | 100 | Use Bi-Level ProgStart System on frequently switched circuits |  | 8 | 0.71 | 3100 | 0.95 | ISL | 0.39011 | 96.7473 |  | 30000 | 3.25 | 0.09
New T8HP Fixture 4', 8-F32T8, 3100+lumen, 2-NLO Sylvania Quicktronic QT/120/277ISN-SC | 228 | 20968.4 | H3 | 120 | Dedicated-Voltage, standard Instant-Start |  | 8 | 0.89 | 3100 | 0.95 | ISN | 0.39035 | 96.807 |  | 30000 | 3.25 | 0.09
New T8HP Fixture 4', 8-F32T8, 3100+lumen, 2-HLO GE-432-Ultramax-H | 294 | 27094 | H4 | 140 | Universal-Voltage, Instant-Start, High-Output |  | 8 | 1.15 | 3100 | 0.95 | ISH | 0.39116 | 97.0068 |  | 30000 | 3.25 | 0.09
================================= | [6 empty] | # lamps | bf | lumen lamp | lumen maint | ballast type | BEF | LPW
Standard Electronic T8 lamp/ballast combinations
T8 Standard Electronic, 1-F17T8 17W, 1-Elec | 16 | 1102.5 | B1 | 8 | None | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 1-F25T8 25W, 1-Elec | 23 | 1752.1875 | B1 | 8 | None | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 1-F32T8, 2950+lumen, 1-Elec RLO | 27 | 1991.25 | B1 | 8 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP RLO | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 1-F32T8, 2950+lumen, 1-Elec | 31 | 2400 | B1 | 8 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP RLO | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 1-F96T8 59W, 1-Elec | 68 | 4513.5 | B1 | 8 | None | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 1-F96T8HO 86W, 1-Elec | 99 | 7380 | B1 | 8 | None | [9 empty] | 24000 | 2.5 | 0.09
----------------------------
T8 Standard Electronic, 2-F17T8 17W, 1-Elec | 31 | 2205 | B2 | 15 | None | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 2-F25T8 25W, 1-Elec | 46 | 3504.375 | B2 | 15 | None | [6 empty] | 1.6/1.58/1.55/1.48/1.47 |  |  | 24000 | 2.5 | 0.09
T8 Standard Electronic, 2-F32T8, 2950+lumen, 1-Elec VRLO | 51 | 4315.85 | B2 | 15 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO |  | 2 | 0.77 | 2950 | 0.95 | ISL | 1.5098 | 89.0784 |  | 24000 | 2.5 | 0.09
T8 Standard Electronic, 2-F32T8, 2950+lumen, 1-Elec RLO | 55 | 4371.9 | B2 | 15 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO |  | 2 | 0.78 | 2950 | 0.95 | ISL | 1.4182 | 83.6727 |  | 24000 | 2.5 | 0.09
T8 Standard Electronic, 2-F32T8, 2950+lumen, 1-ISElec | 59 | 4932.4 | B2 | 15 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO |  | 2 | 0.88 | 2950 | 0.95 | ISN | 1.4915 | 88 |  | 24000 | 2.5 | 0.09
T8 Standard Electronic, 2-F32T8, 2950+lumen, 1-RSElec | 62 | 4932.4 | B2 | 15 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO |  | 2 | 0.88 | 2950 | 0.95 | ISN | 1.4194 | 83.7419 |  | 24000 | 2.5 | 0.09
T8 Standard Electronic, 2-F32T8, 2950+lumen, 1-Elec HLO | 76 | 6265.8 | B2 | 15 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP HLO |  | 2 | 1.15 | 2950 | 0.95 | ISH | 1.5132 | 89.2763 |  | 24000 | 2.5 | 0.09
T8 Standard Electronic, 2-F96T8 59W, 1-Elec | 105 | 9027 | B2 | 15 | T8 High Performance, 4-F32T8HP 32W, 1-Elec HP RLO | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 2-F96T8HO 86W, 1-Elec | 155 | 12693.6 | B2 | 15 | T8 High Performance, 4-F32T8HP 32W, 2-Elec HP HLO | [9 empty] | 24000 | 2.5 | 0.09
----------------------------
T8 Standard Electronic, 3-F17T8 17W, 1-Elec | 46 | 3307.5 | B2 | 15 | None | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 3-F25T8 25W, 1-Elec | 66 | 5256.5625 | B2 | 15 | None | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 3-F32T8, 2950+lumen, 1-Elec RLO | 80 | 5973.75 | B2 | 15 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 3-F32T8, 2950+lumen, 1-Elec | 90 | 6969.375 | B2 | 15 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO | [9 empty] | 24000 | 2.5 | 0.09
----------------------------
T8 Standard Electronic, 4-F17T8 17W, 1-Elec | 63 | 4410 | B2 | 15 | None | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 4-F25T8 25W, 1-Elec | 90 | 7008.75 | B2 | 15 | None | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 4-F32T8, 2950+lumen, 1-Elec RLO | 98 | 7728 | B2 | 15 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 4-F32T8, 2950+lumen, 1-Elec RLO | 101 | 7965 | B2 | 15 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 4-F32T8, 2950+lumen, 1-Elec | 114 | 9292.5 | B2 | 15 | T8 High Performance, 4-F32T8HP 32W, 1-Elec HP RLO | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 4-F32T8, 2950+lumen, 2-Elec HLO | 172 | 13593.6 | K2 | 40 | T8 High Performance, 4-F32T8HP 32W, 2-Elec HP HLO | [9 empty] | 24000 | 2.5 | 0.09
----------------------------
T8 Standard Electronic, 6-F32T8, 2950+lumen, 2-Elec | 175 | 13938.75 | K2 | 40 | None | [9 empty] | 24000 | 2.5 | 0.09
T8 Standard Electronic, 6-F32T8, 2950+lumen, 2-Elec HLO | 228 | 18797.4 | K2 | 40 | None | [9 empty] | 24000 | 2.5 | 0.09
=========================== | [6 empty] | # lamps | bf | lumen lamp | lumen maint | ballast type | BEF | LPW
High Output T5 fluorescent lamp/ballast combinations | [11 empty] | 2.84/1.47/1.00/0.75
T5HO Fluorescent, 1-F54T5HO 54W, 1-Program Start | 62 | 4750 | B1 | 8 | None |  | 1 | 1 | 5000 | 0.95 | PRS | 1.6129 | 80.6452 |  | 20000 | 8.22 | 0.09
T5HO Fluorescent, 2-F54T5HO 54W, 1-Program Start | 118 | 9500 | H1 | 80 | None |  | 2 | 1 | 5000 | 0.95 | PRS | 0.84746 | 84.7458 |  | 20000 | 8.22 | 0.09
T5HO Fluorescent, 3-F54T5HO 54W, 2-Program Start | 179 | 14250 | H2 | 100 | None |  | 3 | 1 | 5000 | 0.95 | PRS | 0.55866 | 83.7989 |  | 20000 | 8.22 | 0.09
T5HO Fluorescent, 4-F54T5HO 54W, 2-Program Start | 234 | 19000 | H3 | 120 | None |  | 4 | 1 | 5000 | 0.95 | PRS | 0.42735 | 85.4701 |  | 20000 | 8.22 | 0.09
T5HO Fluorescent, 5-F54T5HO 54W, 3-Program Start | 298 | 23750 | H4 | 140 | None |  | 5 | 1 | 5000 | 0.95 | PRS | 0.33557 | 83.8926 |  | 20000 | 8.22 | 0.09
T5HO Fluorescent, 6-F54T5HO 54W, 3-Program Start | 352 | 28500 | H4 | 140 | None |  | 6 | 1 | 5000 | 0.95 | PRS |  |  |  | 20000 | 8.22 | 0.09
T5HO Fluorescent, 8-F54T5HO 54W, 4-Program Start | 472 | 38000 | H4 | 140 | None |  | 8 | 1 | 5000 | 0.95 | PRS |  |  |  | 20000 | 8.22 | 0.09
T5HO Fluorescent, 12-F54T5HO 54W, 3-Program Start | 704 | 57000 | H4 | 140 | None |  | 12 | 1 | 5000 | 0.95 | PRS |  |  |  | 20000 | 8.22 | 0.09
Retrofit to T5HO Fluorescent, 2-F54T5HO 54W, 1-Program Start | 118 | 9500 | L1 | 25 | None |  | 2 | 1 | 5000 | 0.95 | PRS | 0.84746 | 84.7458 |  | 20000 | 8.22 | 0.09
Retrofit to T5HO Fluorescent, 4-F54T5HO 54W, 2-Program Start | 234 | 19000 | L2 | 50 | None |  | 4 | 1 | 5000 | 0.95 | PRS | 0.42735 | 85.4701 |  | 20000 | 8.22 | 0.09
===========================
New Hard-Wired CFL fixture, 1-bi-ax 13W, 1-Elec | 16 | 765 | C1 | 30 | None | [9 empty] | 10000 | 1.91 | 0.09
New Hard-Wired CFL fixture, 1-bi-ax 18W, 1-Elec | 19 | 1062.5 | C1 | 30 | None | [9 empty] | 10000 | 1.91 | 0.09
New Hard-Wired CFL fixture, 1-bi-ax 26W, 1-Elec | 27 | 1530 | C1 | 30 | None | [9 empty] | 10000 | 3.3 | 0.09
New Hard-Wired CFL fixture, 1-bi-ax 32W, 1-Elec | 33 | 2040 | C1 | 30 | None | [9 empty] | 10000 | 5.2 | 0.09
New Hard-Wired CFL fixture, 1-bi-ax 42W, 1-Elec | 43 | 2720 | C1 | 30 | None | [9 empty] | 10000 | 5.5 | 0.09
New Hard-Wired CFL fixture, 1-bi-ax 55W, 1-Mag | 54 | 2677.5 | C2 | 50 | None | [9 empty] | 10000 | 8 | 0.09
New Hard-Wired CFL fixture, 1-bi-ax 65W, 1-Mag | 63 | 3213 | C2 | 50 | None | [9 empty] | 10000 | 8 | 0.09
New Hard-Wired CFL fixture, 1-bi-ax 85W, 1-Mag | 82 | 4207.5 | C2 | 50 | None | [9 empty] | 10000 | 8 | 0.09
----------------------------
New Hard-Wired CFL fixture, 2-bi-ax 5W, 2-Mag | 14 | 475.83 | C1 | 30 | None | [9 empty] | 10000 | 1.91 | 0.09
New Hard-Wired CFL fixture, 2-bi-ax 7W, 2-Mag | 18 | 691.56 | C1 | 30 | None | [9 empty] | 10000 | 1.91 | 0.09
New Hard-Wired CFL fixture, 2-bi-ax 9W, 2-Mag | 22 | 908.82 | C1 | 30 | None | [9 empty] | 10000 | 1.91 | 0.09
New Hard-Wired CFL fixture, 2-bi-ax 13, 1-Elec | 29 | 1530 | C1 | 30 | None | [9 empty] | 10000 | 1.91 | 0.09
New Hard-Wired CFL fixture, 2-bi-ax 18W, 1-Elec | 35 | 2125 | C1 | 30 | None | [9 empty] | 10000 | 1.91 | 0.09
New Hard-Wired CFL fixture, 2-bi-ax 26W, 1-Elec | 52 | 3060 | C2 | 50 | None | [9 empty] | 10000 | 3.3 | 0.09
New Hard-Wired CFL fixture, 2-bi-ax 28W, 2-Mag | 58 | 2965.14 | C2 | 50 | None | [9 empty] | 10000 | 3.3 | 0.09
New Hard-Wired CFL fixture, 2-bi-ax 32W, 2-Mag | 64 | 3398.13 | C2 | 50 | None | [9 empty] | 10000 | 5.2 | 0.09
New Hard-Wired CFL fixture, 2-bi-ax 32W, 1-Elec | 68 | 4080 | C2 | 50 | None | [9 empty] | 10000 | 5.2 | 0.09
New Hard-Wired CFL fixture, 2-bi-ax 42W, 1-Elec | 93 | 5440 | C2 | 50 | None | [9 empty] | 10000 | 5.5 | 0.09
----------------------------
New Hard-Wired CFL fixture, 1-2D 16W, 1-Elec | 15 | 803.25 | C1 | 30 | None | [9 empty] | 10000 | 15.77 | 0.09
New Hard-Wired CFL fixture, 1-2D 21W, 1-Elec | 21 | 1032.75 | C1 | 30 | None | [9 empty] | 10000 | 10.5 | 0.09
New Hard-Wired CFL fixture, 1-2D 28W, 1-Elec | 28 | 1568.25 | C1 | 30 | None | [9 empty] | 10000 | 12.55 | 0.09
New Hard-Wired CFL fixture, 1-2D 38W, 1-Elec | 37 | 2180.25 | C1 | 30 | None | [9 empty] | 10000 | 13.28 | 0.09
----------------------------
New Hard-Wired CFL fixture, 2-2D 16W, 1-Elec | 30 | 1606.5 | C1 | 30 | None | [9 empty] | 10000 | 15.77 | 0.09
New Hard-Wired CFL fixture, 2-2D 21W, 1-Elec | 42 | 2065.5 | C1 | 30 | None | [9 empty] | 10000 | 10.5 | 0.09
New Hard-Wired CFL fixture, 2-2D 28W, 1-Elec | 56 | 3136.5 | C2 | 50 | None | [9 empty] | 10000 | 12.55 | 0.09
New Hard-Wired CFL fixture, 2-2D 38W, 1-Elec | 74 | 4360.5 | C2 | 50 | None | [9 empty] | 10000 | 13.28 | 0.09
===========================
Ceramic Metal Halide, 1-Single End 20W, 1-Elec | 28 | 1100 | D1 | 50 | Great option for retail display lighting - ie. track or recessed can | [9 empty] | 9000 | 43.25 | 0.15
Ceramic Metal Halide, 1-Single End or Double End 39W, 1-Elec | 45 | 2600 | D1 | 50 | Great option for retail display lighting - ie. track or recessed can | [9 empty] | 9000 | 43.25 | 0.15
Ceramic Metal Halide, 1-Single End or Double End 70W, 1-Elec | 80 | 5200 | D1 | 50 | Great option for retail display lighting - ie. track or recessed can | [9 empty] | 20000 | 43.25 | 0.15
Ceramic Metal Halide, 1-Single End or Double End 150W, 1-Elec | 168 | 10200 | D2 | 80 | Great option for retail display lighting - ie. track or recessed can | [9 empty] | 20000 | 43.25 | 0.15
Ceramic Metal Halide, 1-Bulb 50W, 1-Elec | 55 | 2640 | D1 | 50 | Great option for general retail lighting | [9 empty] | 9000 | 43.25 | 0.15
Ceramic Metal Halide, 1-Bulb 70W, 1-Elec | 80 | 4700 | D1 | 50 | Great option for general retail lighting | [9 empty] | 20000 | 43.25 | 0.15
Ceramic Metal Halide, 1-Bulb 100W, 1-Elec | 112 | 6800 | D1 | 50 | Great option for general retail lighting | [9 empty] | 20000 | 43.25 | 0.15
Ceramic Metal Halide, 1-Bulb 150W, 1-Elec | 168 | 9920 | D2 | 80 | Great option for general retail lighting | [9 empty] | 20000 | 43.25 | 0.15
Ceramic Metal Halide, 1-PAR 39W, 1-Elec | 45 | 1600 | D1 | 50 | Great option for retail display lighting - ie. track or recessed can | [9 empty] | 9000 | 43.25 | 0.15
Ceramic Metal Halide, 1-PAR 70W, 1-Elec | 80 | 3840 | D1 | 50 | Great option for retail display lighting - ie. track or recessed can | [9 empty] | 20000 | 43.25 | 0.15
Ceramic Metal Halide, 1-PAR 100W, 1-Elec | 112 | 5440 | D1 | 50 | Great option for retail display lighting - ie. track or recessed can | [9 empty] | 20000 | 43.25 | 0.15
===========================
Screw-In CFL, 1-3W capsule, 1-Elec | 3 | 128 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-5W capsule, 1-Elec | 5 | 213 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-7W capsule, 1-Elec | 7 | 298 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-7W, 1-Elec | 7 | 327 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-9W capsule, 1-Elec | 9 | 383 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-9W, 1-Elec | 9 | 421 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-10W, 1-Elec | 10 | 450 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-11W capsule, 1-Elec | 11 | 468 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-11W, 1-Elec | 11 | 550 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-13W, 1-Elec | 13 | 680 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-14W capsule, 1-Elec | 14 | 595 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-14W, 1-Elec | 14 | 720 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-2D 15W, 1-Elec | 15 | 640 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-15W bullet capsule, 1-Elec | 15 | 701 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-15W, 1-Elec | 15 | 791 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-16W, 1-Elec | 16 | 833.085 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-18W, 1-Elec | 18 | 978 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-20W capsule, 1-Elec | 20 | 723 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-20W bullet capsule, 1-Elec | 20 | 935 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-20W, 1-Elec | 20 | 1020 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-22W circline, 1-Elec | 22 | 1020 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-2D 22W, 1-Elec | 22 | 1105 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-22W, 1-Elec | 22 | 1158.21 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-23W, 1-Elec | 23 | 1190 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
Screw-In CFL, 1-24W, 1-Elec | 24 | 1290 | E1 | 3 | None | [9 empty] | 10000 | 4 | 0.09
----------------------------
Screw-In CFL, 1-25W bullet capsule, 1-Elec | 25 | 1169 | E2 | 6 | None | [9 empty] | 10000 | 8 | 0.09
Screw-In CFL, 1-25W, 1-Elec | 25 | 1360 | E2 | 6 | None | [9 empty] | 10000 | 8 | 0.09
Screw-In CFL, 1-26W, 1-Elec | 26 | 1488 | E2 | 6 | None | [9 empty] | 10000 | 8 | 0.09
Screw-In CFL, 1-27W, 1-Elec | 27 | 1488 | E2 | 6 | None | [9 empty] | 10000 | 8 | 0.09
Screw-In CFL, 1-28W bullet capsule, 1-Elec | 28 | 1309 | E2 | 6 | None | [9 empty] | 10000 | 8 | 0.09
Screw-In CFL, 1-28W, 1-Elec | 28 | 1482.57 | E2 | 6 | None | [9 empty] | 10000 | 8 | 0.09
Screw-In CFL, 1-30W, 1-Elec | 30 | 1530 | E2 | 6 | None | [9 empty] | 10000 | 8 | 0.09
Screw-In CFL, 1-30W circline, 1-Elec | 30 | 1530 | E2 | 6 | None | [9 empty] | 10000 | 8 | 0.09
Screw-In CFL, 1-32W, 1-Elec | 32 | 1785 | E2 | 6 | None | [9 empty] | 10000 | 8 | 0.09
Screw-In CFL, 1-35W, 1-Elec | 35 | 1785 | E2 | 6 | None | [9 empty] | 10000 | 8 | 0.09
Screw-In CFL, 1-36W circline, 1-Elec | 36 | 1785 | E2 | 6 | None | [9 empty] | 10000 | 9 | 0.09
Screw-In CFL, 1-2D 39W, 1-Elec | 39 | 2360 | E2 | 6 | None | [9 empty] | 10000 | 9 | 0.09
Screw-In CFL, 1-40W circline, 1-Elec | 40 | 2380 | E2 | 6 | None | [9 empty] | 10000 | 9 | 0.09
Screw-In CFL, 1-42W, 1-Elec | 42 | 2380 | E2 | 6 | None | [9 empty] | 10000 | 13 | 0.09
Screw-In CFL, 1-44W, 1-Elec | 44 | 2040 | E2 | 6 | None | [9 empty] | 10000 | 16 | 0.09
----------------------------
Screw-In CFL, 1-55W, 1-Elec | 55 | 2975 | E3 | 12 | None | [9 empty] | 10000 | 18 | 0.09
Screw-In CFL, 1-65W, 1-Elec | 65 | 3570 | E3 | 12 | None | [9 empty] | 10000 | 18 | 0.09
Screw-In CFL, 1-75W LuxMagic, 1-Elec | 75 | 5250 | E3 | 12 | None | [9 empty] | 10000 | 18 | 0.09
Screw-In CFL, 1-85W, 1-Elec | 85 | 4675 | E3 | 12 | None | [9 empty] | 10000 | 22 | 0.09
Screw-In CFL, 1-100W, 1-Elec | 100 | 5100 | E3 | 12 | None | [9 empty] | 10000 | 22 | 0.09
Screw-In CFL, 1-105W, 1-Elec | 105 | 5865 | E3 | 12 | None | [9 empty] | 10000 | 22 | 0.09
Screw-In CFL, 1-125W, 1-Elec | 125 | 6375 | E3 | 12 | None | [9 empty] | 10000 | 22 | 0.09
Screw-In CFL, 1-150W, 1-Elec | 150 | 7650 | E3 | 12 | None | [9 empty] | 10000 | 22 | 0.09
===========================
New Exit Sign, 1 face Cold Cathode, 4W, no ballast | 4 | 2 | F1 | 30 | None | [9 empty] | 50000 | 55 | 0.2
New Exit Sign, 1 face LED, 1.5W, no ballast | 1.5 | 2 | F1 | 30 | None | [9 empty] | 100000 | 25 | 0.2
New Exit Sign, 2 faced Cold Cathode, 4W/face, no ballast | 8 | 2 | F1 | 30 | None | [9 empty] | 50000 | 55 | 0.2
New Exit Sign, 2 faced LED, 1.5W/face, no ballast | 3 | 2 | F1 | 30 | None | [9 empty] | 100000 | 25 | 0.2
New Exit Sign, 2 faced LED with battery back-up, no ballast | 9 | 2 | F1 | 30 | None | [9 empty] | 100000 | 25 | 0.2
===========================
Induction, 1-QL 55W, 1-RF Generator | 55 | 2800 | G1 | 60 | Great option for Street & Area lighting - 100,000 hr life | [9 empty] | 100000 | 400 | 0.3
Induction, 1-QL 85W, 1-RF Generator | 85 | 4800 | G1 | 60 | Great option for Street & Area lighting - 100,000 hr life | [9 empty] | 100000 | 400 | 0.3
Induction, 1-Icetron 100W donut, 1-RF Generator | 157 | 5920 | G1 | 60 | Great option for Street & Area lighting - 100,000 hr life | [9 empty] | 100000 | 400 | 0.3
Induction, 1-QL 165W, 1-RF Generator | 165 | 9600 | G2 | 120 | Great option for Street & Area lighting - 100,000 hr life | [9 empty] | 100000 | 400 | 0.3
===========================
MH Pulse Start, 1-PS 300W, 1-LLRPSL, 277V only, low voltage swing tolerance | 324 | 24400 | I1 | 100 | None | [9 empty] | 20000 | 27.6064 | 0.4
MH Pulse Start, 1-PS 300W, 1-SCWA typical ballast | 342 | 24400 | I1 | 100 | None | [9 empty] | 20000 | 27.6064 | 0.4
MH Pulse Start, 1-PS 320W, 1-LLRPSL, 277V only, low voltage swing tolerance | 349 | 26400 | I1 | 100 | None | [9 empty] | 20000 | 27.6064 | 0.4
MH Pulse Start, 1-PS 320W, 1-SCWA typical ballast | 370 | 26400 | I1 | 100 | None | [9 empty] | 20000 | 27.6064 | 0.4
MH Pulse Start, 1-PS 350W, 1-LLRPSL, 277V only, low voltage swing tolerance | 380 | 29600 | I1 | 100 | None | [9 empty] | 20000 | 27.6064 | 0.4
MH Pulse Start, 1-PS 350W, 1-SCWA typical ballast | 400 | 29600 | I1 | 100 | None | [9 empty] | 20000 | 27.6064 | 0.4
MH Pulse Start, 1-PS 400W, 1-Elec | 425 | 36120 | I2 | 150 | None | [9 empty] | 20000 | 34.55 | 0.4
MH Pulse Start, 1-PS 400W, 1-LLRPSL, 277V only, low voltage swing tolerance | 435 | 31500 | I2 | 150 | None | [9 empty] | 20000 | 34.55 | 0.4
MH Pulse Start, 1-PS 400W, 1-SCWA typical ballast | 455 | 31500 | I2 | 150 | None | [9 empty] | 20000 | 34.55 | 0.4
MH Pulse Start, 1-PS 400W, 1-RPB handles voltage swings | 467 | 31500 | I2 | 150 | None | [9 empty] | 20000 | 34.55 | 0.4
MH Pulse Start, 1-PS 450W, 1-LLRPSL, 277V only, low voltage swing tolerance | 485 | 40000 | I2 | 150 | None | [9 empty] | 20000 | 34.55 | 0.4
MH Pulse Start, 1-PS 450W, 1-SCWA typical ballast | 514 | 40000 | I2 | 150 | None | [9 empty] | 20000 | 34.55 | 0.4
MH Pulse Start, 1-PS 450W, 1-RPB handles voltage swings | 530 | 40000 | I2 | 150 | None | [9 empty] | 20000 | 34.55 | 0.4
MH Pulse Start, 1-PS 750W, 1-SCWA is the only option | 818 | 60000 | I2 | 150 | None | [9 empty] | 20000 | 62.5745 | 0.4
MH Pulse Start, 1-PS 875W, 1-SCWA is the only option | 940 | 80500 | I2 | 150 | None | [9 empty] | 20000 | 62.5745 | 0.4
MH Pulse Start, 1-PS 1000W, 1-SCWA is the only option | 1080 | 96000 | I2 | 150 | None | [9 empty] | 20000 | 62.5745 | 0.4
===========================
Occupancy Sensor or Timer controlling 100 to 200 watts (see above) |  |  | J1 | 35 | None | [9 empty] | No Default | No Default | No Default
Occupancy Sensor or Timer controlling over 200 watts (see above) |  |  | J2 | 45 | None | [9 empty] | No Default | No Default | No Default
===========================
Non-Standard Measures
MH Pulse Start, 1-PS 50W, 1-SCWA typical ballast | 68 | 2100 |  |  | Venture Lighting Catalog | [9 empty] | 7500 | 26.67 | 0.4
MH Pulse Start, 1-PS 70W, 1-SCWA typical ballast | 90 | 3400 |  |  | Venture Lighting Catalog | [9 empty] | 12000 | 26.67 | 0.4
MH Pulse Start, 1-PS 100W, 1-SCWA typical ballast | 125 | 5500 |  |  | Venture Lighting Catalog | [9 empty] | 12000 | 26.67 | 0.4
MH Pulse Start, 1-PS 150W, 1-SCWA typical ballast | 185 | 9500 |  |  | Venture Lighting Catalog | [9 empty] | 12000 | 28.08 | 0.4
MH Pulse Start, 1-PS 175W, 1-SCWA typical ballast | 208 | 14000 |  |  | Venture Lighting Catalog | [9 empty] | 12000 | 31.04 | 0.4
MH Pulse Start, 1-PS 200W, 1-SCWA typical ballast | 232 | 16000 |  |  | Venture Lighting Catalog | [9 empty] | 12000 | 31.04 | 0.4
MH Pulse Start, 1-PS 250W, 1-SCWA typical ballast | 291 | 19000 |  |  | Venture Lighting Catalog | [9 empty] | 12000 | 31.04 | 0.4
----------------------------
High Pressure Sodium, 35W, 1-Std Mag | 45 | 1845 |  |  | Hardwired CFL | [9 empty] | 16000 | 15.72 | 0.4
High Pressure Sodium, 50W, 1-Std Mag | 68 | 3280 |  |  | Hardwired CFL | [9 empty] | 24000 | 15.72 | 0.4
High Pressure Sodium, 70W, 1-Std Mag | 86 | 5166 |  |  | Hardwired CFL | [9 empty] | 24000 | 15.72 | 0.4
High Pressure Sodium, 100W, 1-Std Mag | 120 | 7790 |  |  | Hardwired CFL | [9 empty] | 24000 | 15.72 | 0.4
High Pressure Sodium, 150W, 1-Std Mag | 170 | 13120 |  |  | Ceramic Metal Halide, 1-70W, 1-Elec | [9 empty] | 24000 | 11.89 | 0.4
High Pressure Sodium, 200W, 1-Std Mag | 245 | 18040 |  |  | Ceramic Metal Halide, 1-100W, 1-Elec | [9 empty] | 24000 | 14.24 | 0.4
High Pressure Sodium, 250W, 1-Std Mag | 295 | 22550 |  |  | Ceramic Metal Halide, 1-150W, 1-Elec | [9 empty] | 24000 | 14.24 | 0.4
High Pressure Sodium, 310W, 1-Std Mag | 365 | 30340 |  |  | Ceramic Metal Halide, 1-250W, 1-Elec | [9 empty] | 24000 | 14.24 | 0.4
High Pressure Sodium, 400W, 1-Std Mag | 457 | 41000 |  |  | Ceramic Metal Halide, 1-320W, 1-Elec | [9 empty] | 24000 | 14.24 | 0.4
----------------------------
MR-16 or MRC-16 Halogen Display Lamps, 20W, no ballast | 20 | 240 |  |  | Ceramic Metal Halide, 1-39W, 1-Elec | [9 empty] | No Default | No Default | No Default
MR-16 or MRC-16 Halogen Display Lamps, 35W, no ballast | 35 | 490 |  |  | Ceramic Metal Halide, 1-39W, 1-Elec | [9 empty] | No Default | No Default | No Default
MR-16 or MRC-16 Halogen Display Lamps, 40W, no ballast | 40 | 600 |  |  | Ceramic Metal Halide, 1-70W, 1-Elec | [9 empty] | No Default | No Default | No Default
MR-16 or MRC-16 Halogen Display Lamps, 50W, no ballast | 50 | 790 |  |  | Ceramic Metal Halide, 1-100W, 1-Elec | [9 empty] | No Default | No Default | No Default
MR-16 or MRC-16 Halogen Display Lamps, 75W, no ballast | 75 | 1320 |  |  | Ceramic Metal Halide, 1-150W, 1-Elec | [9 empty] | No Default | No Default | No Default
----------------------------
Halogen, 1-T3 100W, no ballast | 100 | 1440 |  |  | Ceramic Metal Halide, 1-39W, 1-Elec | [9 empty] | 1500 | 5.99 | 0.09
Halogen, 1-T3 150W, no ballast | 150 | 2160 |  |  | Ceramic Metal Halide, 1-39W, 1-Elec | [9 empty] | 1500 | 5.99 | 0.09
Halogen, 1-T3 250W, no ballast | 250 | 3600 |  |  | Ceramic Metal Halide, 1-70W, 1-Elec | [9 empty] | 1500 | 6.55 | 0.09
Halogen, 1-T3 300W, no ballast | 300 | 4680 |  |  | Ceramic Metal Halide, 1-100W, 1-Elec | [9 empty] | 1500 | 7.05 | 0.09
Halogen, 1-T3 500W, no ballast | 500 | 8550 |  |  | Ceramic Metal Halide, 1-150W, 1-Elec | [9 empty] | 1500 | 6.98 | 0.09
Halogen, 1-T5 750W, no ballast | 750 | 13500 |  |  | Ceramic Metal Halide, 1-250W, 1-Elec | [9 empty] | 1500 | 14 | 0.09
Halogen, 1-T3 1000W, no ballast | 1000 | 18900 |  |  | Ceramic Metal Halide, 1-320W, 1-Elec | [9 empty] | 1500 | 14 | 0.09
Halogen, 1-T3 1500W, no ballast | 1500 | 29700 |  |  | Ceramic Metal Halide, 1-400W, 1-Elec | [9 empty] | 1500 | 14 | 0.09
=================================

## ProjectBC (hidden)
Benefit/Cost Ratio Calculation | Cost | Benefit | Calculation of Present Value of O&M (savings(-) or costs (+) |  |  |  | PMT*[1-((1/(1+i))^N)]/I
Capital Cost | 32000 | 0 | Real Discount Rate | 4% |  |  | Where:
PV Cleaning or Other O&M Cost | 0 | 0 | Periods | 12 |  |  | PV = Present Value Stream of Equal Payments
Present Value of Change in Gas Heating Cost | 1295.6734 | 0 | Annual Cleaning or Other O&M | 0
PV Lamp Periodic Replacement Cost | 0 | 0 | PV Cleaning or Other O&M Cost | 0 |  |  | PMT = Amount of each payment
PV Energy Savings | 0 | 157455.2325 |  |  |  |  | i = Discount Rate Per Period
Total | 33295.6734 | 157455.2325 |  |  |  |  | N = Number of Periods
|  |  | PV Lamp Periodic Replacement Cost | 0 | from Site Audit
B/C Ratio | 4.729
0
|  |  |  | 0 | 0 | 1
|  |  |  | 0 | 0 | 2
|  |  |  | 0 | 0 | 3
|  |  |  | 0 | 0 | 4
|  |  |  | 0 | 0 | 5
|  |  |  | 0 | 0 | 6
|  |  |  | 0 | 0 | 7
|  |  |  | 0 | 0 | 8
|  |  |  | 0 | 0 | 9
|  |  |  | 0 | 0 | 10
|  |  |  | 0 | 0 | 11
|  |  |  | 0 | 0 | 12

## LSYield (hidden)
|  |  | Btype | SpaceHeat | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
|  |  | 17 | 3 | 8: Discounted Levelized $ per therm
| Look-Up Ids |  |  |  | 2: Lighting Savings Yield by Predominant Space Heat Fuel Source; 8: 0.4645; 9: Load Shape Look Up
| 5th Plan Name | ShapeType | Synergy | Space Heat Fuel Source | Synergy Building Type Name | Electric Resistance | Heat Pump | Gas | Unconditioned | Default Hours of Lighitng | Gas Heat Interaction (therms saved per kWh lighting saved) | Gas Heat NPV per kWh electric lighting saved | Electric Resistance | Heat Pump | Gas | Unconditioned | Default Measure Life
1 | Large Off | LgOff | Office 20,000 to 100,000 sf | Electric Resistance | Office 20,000 to 100,000 sf | 91.61% | 102% | 107.9% | 100% | 4200 | -0.0081888 | -0.0038037 | ExLgOffElecHt | ExLgOffHtPmpHt | ExLgOffGasHt | ExLgOff | 12
2 | Medium Off | LgOff | Office >100,000 sf | Heat Pump | Office >100,000 sf | 90.51% | 102% | 106.8% | 100% | 3600 | -0.0081888 | -0.0038037 | ExLgOffElecHt | ExLgOffHtPmpHt | ExLgOffGasHt | ExLgOff | 12
3 | Small Off | SmOff | Office <20,000 sf | Gas | Office <20,000 sf | 69.09% | 95.5% | 111.7% | 100% | 3000 | -0.021382 | -0.0099319 | ExSmOffElecHt | ExSmOffHtPmpHt | ExSmOffGasHt | ExSmOff | 12
4 | Big Box | LgRet | Retail Big Box >50,000 sf One-Story | Unconditioned | Retail Big Box >50,000 sf One-Story | 81.86% | 102.5% | 111.8% | 100% | 4800 | -0.015013 | -0.0069734 | ExLgRetElecHt | ExLgRetHtPmpHt | ExLgRetGasHt | ExLgRet | 12
5 | Small Box | SmRet | Retail 5,000 to 50,000 sf |  | Retail 5,000 to 50,000 sf | 68.09% | 92.5% | 103.4% | 100% | 3900 | -0.017742 | -0.0082413 | ExSmRetElecHt | ExSmRetHtPmpHt | ExSmRetGasHt | ExSmRet | 12
6 | High End | SmRet | Retail Boutique <5,000 sf |  | Retail Boutique <5,000 sf | 76.31% | 97.5% | 104.4% | 100% | 3400 | -0.014103 | -0.0065508 | ExSmRetElecHt | ExSmRetHtPmpHt | ExSmRetGasHt | ExSmRet | 12
7 | Anchor | LgRet | Retail Anchor Store >50,000 sf Multistory |  | Retail Anchor Store >50,000 sf Multistory | 71.08% | 96.5% | 110.1% | 100% | 4000 | -0.019562 | -0.0090866 | ExLgRetElecHt | ExLgRetHtPmpHt | ExLgRetGasHt | ExLgRet | 12
8 | K-12 | School | School K-12 |  | School K-12 | 56.88% | 86% | 100.4% | 100% | 2400 | -0.021837 | -0.010143 | ExSchoolElecHt | ExSchoolHtPmpHt | ExSchoolGasHt | ExSchool | 12
9 | University | School | College or University |  | College or University | 68.21% | 95.5% | 110.8% | 100% | 3000 | -0.021382 | -0.0099319 | ExSchoolElecHt | ExSchoolHtPmpHt | ExSchoolGasHt | ExSchool | 12
10 | Warehouse | Wareh | Warehouse |  | Warehouse | 61% | 80.5% | 96.36% | 100% | 3500 | -0.017742 | -0.0082413 | ExWarehElecHt | ExWarehHtPmpHt | ExWarehGasHt | ExWareh | 12
11 | Supermarket | Groc | Retail Supermarket |  | Retail Supermarket | 85.3% | 97% | 105.2% | 100% | 6500 | -0.010009 | -0.004649 | ExGrocElecHt | ExGrocHtPmpHt | ExGrocGasHt | ExGroc | 12
12 | MIniMart | Groc | Retail Mini Mart |  | Retail Mini Mart | 69.5% | 94.5% | 104.9% | 100% | 6500 | -0.017742 | -0.0082413 | ExGrocElecHt | ExGrocHtPmpHt | ExGrocGasHt | ExGroc | 12
13 | Restaurant | Rest | Restaurant |  | Restaurant | 42.51% | 72.5% | 96.01% | 100% | 5000 | -0.026841 | -0.012468 | ExRestElecHt | ExRestHtPmpHt | ExRestGasHt | ExRest | 12
14 | Lodging | Hotel | Lodging |  | Lodging | 68.53% | 90% | 104.8% | 100% | 3600 | -0.018197 | -0.0084527 | ExHotelElecHt | ExHotelHtPmpHt | ExHotelGasHt | ExHotel | 12
15 | Hospital | Health | Hospital |  | Hospital | 28.91% | 65% | 94.19% | 100% | 5900 | -0.032755 | -0.015215 | ExHealthElecHt | ExHealthHtPmpHt | ExHealthGasHt | ExHealth | 12
16 | OtherHealth | Health | Other Health, Nursing, Medical Clinic |  | Other Health, Nursing, Medical Clinic | 91.87% | 102% | 108.2% | 100% | 3600 | -0.0081888 | -0.0038037 | ExHealthElecHt | ExHealthHtPmpHt | ExHealthGasHt | ExHealth | 12
17 | Other | CommLight | Other Commercial |  | Other Commercial | 86.68% | 102% | 103% | 100% | 4000 | -0.0081888 | -0.0038037 | ExCommLight | ExCommLight | ExCommLight | ExCommLight | 12
18 |  | Ind | Industrial Plant with One Shift |  | Industrial Plant with One Shift | 61% | 80.5% | 96.36% | 100% | 2250 | -0.017742 | -0.0082413 | IndShift1 | IndShift1 | IndShift1 | IndShift1 | 12
19 |  | Ind | Industrial Plant with Three Shifts |  | Industrial Plant with Three Shifts | 61% | 80.5% | 96.36% | 100% | 8400 | -0.017742 | -0.0082413 | IndShift3 | IndShift3 | IndShift3 | IndShift3 | 12
20 |  | Ind | Industrial Plant with Two Shifts |  | Industrial Plant with Two Shifts | 61% | 80.5% | 96.36% | 100% | 4500 | -0.017742 | -0.0082413 | IndShift2 | IndShift2 | IndShift2 | IndShift2 | 12
21 |  | Flat | Exterior 24 Hour Operation |  | Exterior 24 Hour Operation | 100% | 100% | 100% | 100% | 8760 | 0 | 0 | Flat | Flat | Flat | Flat | 12
22 |  | StreetLight | Street & Area Lighting (Photo Sensor Controlled) |  | Street & Area Lighting (Photo Sensor Controlled) | 100% | 100% | 100% | 100% | 5400 | 0 | 0 | StreetLight | StreetLight | StreetLight | StreetLight | 12
23
24
25
26
27
28
29
30
Note on G3: Charlie Grist: Lighting Savings Yield is the fraction of lighting energy savings that is realized after taking into account interactions between energy use in the lighting, heating and cooling systems. These values include region-wide estimates of the average saturation of cooling systems. Multiply lighting savings by LSYield to get energy savings net of electric space heat & cooling interactions. Does not include gas interactions. Values are from a series of several hundred DOE 2 runs performed by Mike Kennedy in 2003 on several prototypes in several configurations of shell, lpd, ventilation rates, HVAC system configuration and climate. Adopted by RTF in 2004. Values are default estimates for common cases of building and system configuration and operating conditions thought to represent the population. Over 600 results were synthesized into the categories represented in the tables as a simplification for regional conservation analysis and for default values for the RTF calculators and deemed savings calculations. As a result the default values may not represent specific cases. Specific cases which are thought to have significantly different interactions than the defaults should be modeled under RTF protocols. Original work in file: InteractionsBldgType01082004.xls Default annual hours of lighting operation are estimated from twelve sources by Grist and adopted by RTF in 2004. See file R:\CG\Main\Plan 5\Commercial\Assessment\Data\hours.xls

## ShapePV (hidden)
Values are from | ..\..\..\..\TE\RTF\Software\Deemed Calcs Final\PostFY06 Calcs\CreditCalc_kWh_FY07v1_7.xls
For 12-year measure life all retrofit measures, including industrial lighting
| End Use/Measure | Shape Pointer | NPV/kWh for Selected Measure & Lifetime
| Retrofit of Existing Lighting System, Unspecified Heating Fuel | ExCommLight | 0.46224
| Lighting in Grocery, Air Source Heat Pump Heating and Cooling | ExGrocHtPmpHt | 0.43012
| Lighting in Grocery, Electric Resistance Heating | ExGrocElecHt | 0.4686
| Lighting in Grocery, Gas Heating | ExGrocGasHt | 0.42378
| Lighting in Grocery, Unspecified Heating Fuel | ExGroc | 0.43002
| Lighting in Health Care Facility, Air Source Heat Pump Heating and Cooling | ExHealthHtPmpHt | 0.45966
| Lighting in Health Care Facility, Electric Resistance Heating | ExHealthElecHt | 0.6223
| Lighting in Health Care Facility, Gas Heating | ExHealthGasHt | 0.43944
| Lighting in Health Care Facility, Unspecified Heating Fuel | ExHealth | 0.4677
| Lighting in Hotel, Air Source Heat Pump Heating and Cooling | ExHotelHtPmpHt | 0.4598
| Lighting in Hotel, Electric Resistance Heating | ExHotelElecHt | 0.50822
| Lighting in Hotel, Gas Heating | ExHotelGasHt | 0.44824
| Lighting in Hotel, Unspecified Heating Fuel | ExHotel | 0.46314
| Lighting in Large Office, Air Source Heat Pump Heating and Cooling | ExLgOffHtPmpHt | 0.46784
| Lighting in Large Office, Electric Resistance Heating | ExLgOffElecHt | 0.50966
| Lighting in Large Office, Gas Heating | ExLgOffGasHt | 0.4666
| Lighting in Large Office, Unspecified Heating Fuel | ExLgOff | 0.48412
| Lighting in Large Retail, Air Source Heat Pump Heating and Cooling | ExLgRetHtPmpHt | 0.45566
| Lighting in Large Retail, Electric Resistance Heating | ExLgRetElecHt | 0.46234
| Lighting in Large Retail, Gas Heating | ExLgRetGasHt | 0.45566
| Lighting in Large Retail, Unspecified Heating Fuel | ExLgRet | 0.45676
| Lighting in Lighting, Unspecified Heating Fuel and Building Type | ExCommLight | 0.46224
| Lighting in Existing Restaurant, Air Source Heat Pump Heating and Cooling | ExRestHtPmpHt | 0.44024
| Lighting in Existing Restaurant, Electric Resistance Heating | ExRestElecHt | 0.49806
| Lighting in Existing Restaurant, Gas Heating | ExRestGasHt | 0.42888
| Lighting in Existing Restaurant, Unspecified Heating Fuel | ExRest | 0.43938
| Lighting in Existing School, Air Source Heat Pump Heating and Cooling | ExSchoolHtPmpHt | 0.46434
| Lighting in Existing School, Electric Resistance Heating | ExSchoolElecHt | 0.54624
| Lighting in Existing School, Gas Heating | ExSchoolGasHt | 0.4395
| Lighting in Existing School, Unspecified Heating Fuel | ExSchool | 0.4522
| Lighting in Existing Small Retail, Air Source Heat Pump Heating and Cooling | ExSmRetHtPmpHt | 0.48394
| Lighting in Existing Small Retail, Gas Heating | ExSmRetGasHt | 0.47044
| Lighting in Existing Small Retail, Unspecified Heating Fuel | ExSmRet | 0.48022
| Lighting in Existing Small Office, Air Source Heat Pump Heating and Cooling | ExSmOffHtPmpHt | 0.43458
| Lighting in Existing Small Office, Electric Resistance Heating | ExSmOffElecHt | 0.48548
| Lighting in Existing Small Office, Gas Heating | ExSmOffGasHt | 0.4302
| Lighting in Existing Small Office, Unspecified Heating Fuel | ExSmOff | 0.44314
| Lighting in Existing Small Retail, Electric Resistance Heating | ExSmRetElecHt | 0.51482
| Lighting in Existing Warehouse, Air Source Heat Pump Heating and Cooling | ExWarehHtPmpHt | 0.4606
| Lighting in Existing Warehouse, Electric Resistance Heating | ExWarehElecHt | 0.48148
| Lighting in Existing Warehouse, Gas Heating | ExWarehGasHt | 0.45498
| Lighting in Existing Warehouse, Unspecified Heating Fuel | ExWareh | 0.46304
| Flat Load Profile | FLAT | 0.40406
| PNW System Load Shape | SysLoad | 0.44352
| Street & Area Lighting (Photo Sensor Controlled) | StreetLight | 0.36022
| Generic Plant with One Shift | IndShift1 | 0.492
| Generic Plant with Three Shifts | IndShift3 | 0.4254
| Generic Plant with Two Shifts | IndShift2 | 0.47816

## BugList (hidden)
Item | Bug | Discovery Date | Bug Version | Who | Disposition | Revised Version | Revision Date
1 | "NA" shows on Project summary under "Unit Value of Electric Savings (NPV/kWh)" cell H31 when Btype is "Other Commercial" | 2006-12-16 | CommercialLightingCalculator FY07 V1_1.xls | Nora | Due to misnamed load shape in tab ShapePV. Fixed by Grist on 12/16/2005. | CommercialLightingCalculator FY07 V1_2.xls | 2005-12-16
2 | Outdated values for PV of energy saved by shape and btype in Shape PV. | 2006-12-16 | CommercialLightingCalculator FY07 V1_1.xls | Grist | Bug due to earlier version 2 of CreditCalc with embedded error that put values off by one row. Corrected to PV Values of Credit Calc Version 7. | CommercialLightingCalculator FY07 V1_2.xls | 2005-12-16
3 | User could input negative capital cost and Site Audit would report negative reimbursement. | 2006-12-07 | CommercialLightingCalculator FY07 V1_1.xls | Grist | Added test to screen for input negative capital cost and set reimbursement to zero in cell R16 of tab 'Site Audit'. | CommercialLightingCalculator FY07 V1_2.xls | 2005-12-16
4 | Wrong value for interaction on industrial one-shift, two-shift and three shift. RTF recommended default values be same as for warehouse. | 2006-12-16 | CommercialLightingCalculator FY07 V1_1.xls | Grist | Corrected so that conditioned space interaction same as for warehouse. Still use no interaction for unconditioned industrial. | CommercialLightingCalculator FY07 V1_2.xls | 2005-12-16
5 | Rearranged facilities data on Site Audit tab and reflected all relevant data to Summary tab. Protected Summary tab | 2006-06-06 | CommercialLightingCalculator FY07 V1_3.xls | Nora | New version uploaded to live site | CommercialLightingCalculator FY07 V1_4.xls | 2006-06-06

## Apps
Lighting Technology Application Guide - March 16, 2005
Technology | Important Characteristics | Typical Applications | Typical Locations | Best Replacement for
High Performance T8s | Best efficacy over life. Great color rendering. | General illumination. | Commercial spaces; office, retail, stairwells. | T12 fluorescent
| Most color temperature choices. | Low-bay applications. | Industrial spaces; manufacturing areas, warehouse.
| Great lumen maintenance. | 8' to 20' mounting height. | Indoor & outdoor signage, parking garages.
Hardwired CFLs | Good efficacy. Great color rendering. | General & task illumination. | Hallways, foyers, bathrooms, closets, task lighting, | Incandescent or
| Shorter life than T8s. Good lumen maint. | Up to 15' mounting height. | table & floor lamps, wall packs & sconces. | Mercury Vapor.
Ceramic Metal Halide Luminaires | Great efficacy, excellent color rendering. | Spot, flood, and general illumination. | Retail display, lobbies, atriums, foyers, museums, | Directional incandescent,
| Good color temps. Dimmable to 50%. | Directional Display lighting. | art galleries, anywhere light quality is important. | i.e., incandescent track lighting.
Screw-in CFLs | Good efficacy. Great color rendering. | General & task illumination. | Hallways, foyers, closets, task lighting, | Non-directional incandescent.
| Shorter life than T8s. Good lumen maint. | Up to 15' mounting height. | table & floor lamps, wall packs & sconces.
LED or | Super long life. Low wattage. | Signage - Exit, Open/Closed, | Over outside doors or pointing toward exit paths. | Incandescent signage.
Cold Cathode | Low light output. | Order Here, etc.. | Over counters. In storefront windows. | Incandescent task lighting.
Induction Lamps & Luminaires | Super long life. Great color rendering. | Places where it is expensive or | Street, roadway, parking lot, and area lighting. | Mercury Vapor or
| Can withstand high temperatures. | dangerous to change bulbs. | Over machinery & other difficult locations. | Incandescent.
| 3000K & 4000K color temp choices. | High temperature applications. | Low-bay applications.
High Output Fluorescent T8, T5, & long bi-ax | Great efficacy over life. | General & task illumination. | Most industrial & some commercial applications. | Incandescent, Mercury Vapor,
| Great color rendering. | Low & high-bay applications. | Gymnasiums, ice rinks, malls, etc.. | T12HO & T12VHO,
| Great lumen maintenance. | 15' to 60' mounting height. | Indoor & outdoor signage, parking garages. | Probe-Start Metal Halide.
Pulse-Start Metal Halide | Higher wattages have high initial efficacy. | General & task illumination. | Industrial high bay general illumination. | Incandescent, Mercury Vapor,
| Good lumen maintenance. | High-bay applications. | Industrial high bay task illumination. | Probe-Start Metal Halide,
| Can withstand high temperatures. | Over 40' mounting height. | Some commercial high-bay. | High Pressure Sodium.
Occupancy Sensors | Tends to cycle lamps on and off. | Infrequently occupied areas. | Conference rooms, copy rooms, individual offices. | Manual wall switches.
Timers | Use program-start ballasts. |  | Warehouse space, storage areas, closets, etc..

## Lamps
Bonneville Power Administration - ESO Lighting Rebates
High Performance 4' Fluorescent Lamp Qualification Worksheet
Potential Qualifying 4' Lamps as of September 3, 2004
PHILIPS - Alto Advantage (ADV) T8 Series
|  | Lamp | Rated Average Life |  |  |  |  | Color | Lamp
Manufacturers | Lamp | Length | IS | IS | RS | Approximate Lumens |  | Rendering | Lumen
Ordering Code | Description | (in.) | 3hrs/start | 12hrs/start | 12hrs/start | Initial | Mean | Index | Maintenance
F32T8/ADV830/Alto | 800 series, 3000K | 48" | 24000 | 30000 | 36000 | 3100 | 2950 | 86 | 95%
F32T8/ADV835/Alto | 800 series, 3500K | 48" | 24000 | 30000 | 36000 | 3100 | 2950 | 86 | 95%
F32T8/ADV841/Alto | 800 series, 4100K | 48" | 24000 | 30000 | 36000 | 3100 | 2950 | 86 | 95%
F32T8/ADV850/Alto | 800 series, 5000K | 48" | 24000 | 30000 | 36000 | 3100 | 2950 | 86 | 95%
SYLVANIA - Extended Performance SUPER (XPS) T8 Octron Series
|  | Lamp | [5 empty] | Color | Lamp
Manufacturers | Lamp | Length | Rated Average Life |  |  | Approximate Lumens |  | Rendering | Lumen
Ordering Code | Description | (in.) | IS | RS or PRS | PSX | Initial | Mean | Index | Maintenance
FO32/830XPS/ECO | 800 series, 3000K | 48" | 15000 | 20000 | 30000 | 3100 | 2945 | 85 | 95%
FO32/835XPS/ECO | 800 series, 3500K | 48" | 15000 | 20000 | 30000 | 3100 | 2945 | 85 | 95%
FO32/841XPS/ECO | 800 series, 4100K | 48" | 15000 | 20000 | 30000 | 3150 | 2992 | 85 | 95%
GE LIGHTING - ULTRA High Lumen w/Starcoat HL T8 Series |  |  |  |  | GE High Performance Lamp Spec Sheet
|  | Lamp | Rated Average Life |  |  |  |  | Color | Lamp
Manufacturers | Lamp | Length | IS | RS | any | Approximate Lumens |  | Rendering | Lumen
Ordering Code | Description | (in.) | 3hrs/start | 3hrs/start | continuous | Initial | Mean | Index | Maintenance
F32T8/XL/SPX30/HLEC | 800 series, 3000K | 48" | 24000 | 24000 | 29000 | 3100 | 2915 | 85 | 94%
F32T8/XL/SPX35/HLEC | 800 series, 3500K | 48" | 24000 | 24000 | 29000 | 3100 | 2915 | 85 | 94%
F32T8/XL/SPX41/HLEC | 800 series, 4100K | 48" | 24000 | 24000 | 29000 | 3100 | 2915 | 85 | 94%
Bonneville Power Administration - ESO Lighting Rebates
High Performance 8' Fluorescent Lamp Qualification Worksheet
Potential Qualifying 8' Lamps as of October 20, 2004
PHILIPS - Alto Plus Slimline T8 Series
|  | Lamp | [5 empty] | Color | Lamp
Manufacturers | Lamp | Length | Rated Average Life |  |  | Approximate Lumens |  | Rendering | Lumen
Ordering Code | Description | (in.) | 3hrs/start |  | 12hrs/start | Initial | Mean | Index | Maintenance
F96T8/TL830/Plus Alto | 800 series, 3000K | 96" | 24000 |  | 30000 | 5900 | 5490 | 85 | 95%
F96T8/TL835/Plus Alto | 800 series, 3500K | 96" | 24000 |  | 30000 | 5900 | 5490 | 85 | 95%
F96T8/TL841/Plus Alto | 800 series, 4100K | 96" | 24000 |  | 30000 | 5900 | 5490 | 85 | 95%
F96T8/TL850/Plus Alto | 800 series, 5000K | 96" | 24000 |  | 30000 | 5780 | 5375 | 85 | 95%
SYLVANIA - Extended Performance (XP) T8 Octron Series
|  | Lamp | [5 empty] | Color | Lamp
Manufacturers | Lamp | Length | Rated Average Life |  |  | Approximate Lumens |  | Rendering | Lumen
Ordering Code | Description | (in.) | 3hrs/start |  | 12hrs/start | Initial | Mean | Index | Maintenance
FO96/830XP/ECO | 800 series, 3000K | 96" | 18000 |  | 26000 | 6100 | 5795 | 85 | 95%
FO96/835XP/ECO | 800 series, 3500K | 96" | 18000 |  | 26000 | 6100 | 5795 | 85 | 95%
FO96/841XP/ECO | 800 series, 4100K | 96" | 18000 |  | 26000 | 6100 | 5795 | 85 | 95%
FO96/850XP/ECO | 800 series, 5000K | 96" | 18000 |  | 26000 | 6100 | 5795 | 85 | 95%
GE LIGHTING - Extra Life Starcoat
|  | Lamp | [5 empty] | Color | Lamp
Manufacturers | Lamp | Length | Rated Average Life |  |  | Approximate Lumens |  | Rendering | Lumen
Ordering Code | Description | (in.) | 3hrs/start |  | 12hrs/start | Initial | Mean | Index | Maintenance
F96T8/XL/SPX30 | 800 series, 3000K | 96" | 18000 |  | 26000 | 5950 | 5650 | 86 | 95%
F96T8/XL/SPX35 | 800 series, 3500K | 96" | 18000 |  | 26000 | 5950 | 5650 | 86 | 95%
F96T8/XL/SPX41 | 800 series, 4100K | 96" | 18000 |  | 26000 | 5950 | 5650 | 86 | 95%
F96T8/XL/SPX50 | 800 series, 5000K | 96" | 18000 |  | 26000 | 5950 | 5650 | 86 | 95%

## Tips
Updated April 7, 2005
Drop-Down Workbook User Tips & Nomenclature
USER TIPS for this Drop-Down Workbook
1 | Check Row 2 for the latest Drop-Down version. Row 2 shows when the spreadsheet was updated.
2 | Row 4-10 - Fill in pertinent information in cells with blue font. Cells with black font are calculated cells. Input into black font cells will erase the equation in that cell.
3 | Row 12-13 - The summary table automatically calculates if any row between 18 and the bottom of the spreadsheet is filled in. Do not type over these cells. Cells with black font are calculated cells.
4 | Cell D13, E13, and J13 - If the calculated numbers are not acurate, make sure these cells sum the correct range.
5 | Cell J13 - This calculated annual kWh savings value will automatically copy into the verification report.
6 | Cell O13 - This calculated value needs to be 30% or greater in order to get a rebate. This value is automatically put into the verification report.
7 | You can move the curser across cells that have a small red triangle in the top right corner of the cell to review comments associated with that cell.
8 | In the Location column, input a specific location. (i.e.. 1st floor, room 123).
9 | In the Annual Operating Hours column - Fill this in for the spreadsheet to work properly.
10 | You need to pick an Existing and Proposed Lamp/Ballast Combination in order for the spreadsheet to work properly. The lamp/ballast combination could be a retrofit or a new luminaire.
11 | If you have trouble reading inside the drop-down boxes, you can look under the data Existing or Proposed tabs for easier reading, then go back to the drop-down to find what you are looking for. Or, you can make the spreadsheet larger by clicking on view and zoom. Zooming to 100% should make it easier to read. Zoom back down to 77% if you want to see the whole page. Your particular computer screen may require a different zoom percentage.
12 | Input the quantity of Existing fixtures. The quantity of Proposed fixtures automatically calculates unless you over-ride with an input value.
13 | When picking Proposed Lamp/Ballast Combinations, check the change in light level column to see if it is within limits. If the calculated value turns red, it is outside of the normal (+10%) limit. This doesn't mean you shouldn't recommend it. It just means you should be cautious about the recommendation.
14 | In order to get the desired light levels, you can change the proposed lamp/ballast combination, or the quantity of proposed fixtures. Try to pick the lowest wattage lamp/ballast combination that gets the desired light levels. Lamp/ballast combinations are arranged from low to high wattage within lamp types. Typically, a reduction of up to 15% will not degrade lighting due to the better quality of light, less lumen depreciation, and electronic operation of the latest lighting systems.
15 | When you click the add a row button at the bottom of the spreadsheet, Excel will automatically protect the worksheet. To unprotect it; click on tools, protection, and unprotect sheet. There is no password.
16 | Some of the information that is filled in on the drop-down sheet will populate the Verification Report and the End-Use Customer Letter. Fill in/select only the blue font cells on the Drop-Down spreadsheet and only the yellow shaded cells on the Verification Report. The white cells on the Verification Report automatically fill in. Print and sign the Verification Report. The date is automatically filled in.
17 | Most of the information automatically fills in on the end-use customer letter. Just type in your company name, address, phone numbers, etc..
18 | You can add Existing and Proposed lamp/ballast combinations to the Data Existing and Proposed spreadsheets if they qualify for a rebate under the program.
NOMENCLATURE for this Drop-Down workbook (typical)
1 | In the following example - 2-F32T8; the 2 indicates a two lamp fixture, the F indicates fluorescent, the 32 indicates a 4' long, 32 watt tube, and T8 indicates an 8/8s inch diameter tube.
2 | In the following example - 2-F96T8; the 2 indicates a two lamp fixture, the F indicates fluorescent, the 96 indicates an 8' long tube, and T8 indicates an 8/8s inch diameter tube.
3 | The "Sylvania Extreme Lighting System" is a reduced-light-output, program-rapid-start, universal-voltage system. This system will work well with occupancy sensors or other frequently switched conditions. Universal voltage ballasts were designed for industrial applications where different voltages exist. Universal/GE has similar products. Look for "PUNV" in the Universal/GE ballast model #. Advance Transformer has similar products as well. Look for "IOP" in the model number.
4 | "Ultramax" is GE's trade name for their high performance ballast product line. They are universal-voltage instant-start ballasts. These ballasts are manufactured by Universal.
5 | "Optanium" is Advance Transformer's trade name for their high performance ballast line. Instant and Program start ballasts are available.
6 | "Centium" is Advance Transformer's trade name for their low THD ballast product line. THD stands for Total Harmonic Distortion. A measure of how close the ballast's waveform is to a perfect sine-wave.
7 | "Advance Centium Intellivolt" is Advance Transformer's trade name for their low THD, universal-voltage ballast product line. THD stands for Total Harmonic Distortion. A measure of how close the ballast's waveform is to a perfect sine-wave.
8 | Quicktronic is Sylvania's trade name for their electronic ballast lines.
9 | When you see an "I or IS" in the model number of a ballast, it indicates an instant-start ballast.
10 | When you see a "RS" in the model number of a ballast, it indicates a rapid-start ballast.
11 | When you see a "P" in the model number of a ballast, it usually indicates a program-start ballast.
12 | When you see a "PRS" in the model number of a ballast, it indicates a program-rapid-start ballast.
13 | When you see a "P" in the model number of an Advance ballast, it indicates "parallel-wired".
14 | When you see a "UNV" in the model number of a ballast, it indicates a universal-voltage ballast.
15 | When you see a "U" in the model number of a TCP ballast, it indicates a universal lamp ballast (i.e. the same ballast can drive 2, 3, or 4 lamps).
16 | When you see a "120 or 277" in the model number of a ballast, it indicates the ballast is dedicated to that specific line voltage.
17 | When you see Universal/GE in the model number of a ballast, it indicates a ballast that was manufactured by Universal but could be sold by Universal or GE.
18 | T8HP indicates a high performance T8 lighting system
19 | IOP indicates an Intellivolt Optanium ballast (120 to 277 volt) manufactured by Advance
20 | ROP indicates a 120 volt Optanium ballast manufactured by Advance
21 | VOP indicates a 277 volt Optanium ballast manufactured by Advance
22 | ICN indicates an Intellivolt Centium ballast (120 to 277 volt) manufactured by Advance
23 | REL indicates a 120 volt standard electronic ballast manufactured by Advance
24 | VEL indicates a 277 volt standard electronic ballast manufactured by Advance
25 | HE indicates a high efficiency ballast manufactured by Universal
26 | Elec or EL indicates a standard electronic ballast. Solid-state electronics.
27 | EE indicates an energy efficient ballast. A hybrid ballast (between "magnetic" and "electronic").
28 | Mag indicates a standard magnetic ballast. A simple transformer with some electronic components.
29 | HLO or HL or H indicates a high light output ballast. Ballast factor greater than 0.95.
30 | NLO or N indicates a normal light output ballast. Ballast factor between 0.8 and 0.95.
31 | RLO or LW or L indicates a reduced light output ballast. Ballast factor less than 0.8.
32 | SC indicates a small can ballast (one that can fit in a small space)
33 | MC indicates a "micro can" ballast (very small)
34 | Bi-Level indicates a single ballast that is capable of dual-switching (high/low system)
35 | 3100+ lumen indicates a 4' lamp that has a nominal (stamped on the tube) lumen output of 3100 or greater. Examples; Philips Advantage, Sylvania Extended Performance, GE Starcoat, etc..
36 | CFL indicates a compact fluorescent lamp
37 | Hard-Wired CFL indicates a fixture that will only accept snap-in bi-ax, D shaped, circline, or other non screw-in CFLs. Making it impossible for an incandescent to be screwed in.
38 | MH indicates a metal halide HID lamp
39 | Single end indicates a single end lamp that is designed to be plugged into place.
40 | Double end indicates a double end lamp that is designed to be snapped into place.
41 | PAR indicates a parabolic reflector lamp (flood or spot)
42 | Induction indicates a light source that is powered by high frequency radio waves.
43 | QL stands for Quality Light (Philips trade name for their induction lamps)
44 | RF stands for radio frequency. Induction technology uses a high frequency of 2.65 megahertz.
45 | LED stands for light emitting diode. A semiconductor "chip" that glows when current is passed through it.

## Definitions
Bonneville Power Administration - ESO Lighting Rebates
Definitions - Updated November 15, 2004
2-F32T8 - indicates two fluorescent lamps in a fixture designed for 4', 32 watt T8 lamps. The T indicates tube. The 8 indicates 8/8's of an inch (or a one inch) diameter tube.
2800K - or 2800 degrees Kelvin (see Kelvin) is a typical color temperature for incandescent bulbs. Tungsten melts at around 3800 degrees Kelvin. Tungsten filaments become very fragile around 2800 degrees Kelvin. Therefore, standard incandescent technology is limited to around 2800 Kelvin CCT. At this temperature, the tungsten filament gives off a yellowish glow. Quartz Halogen is able to increase the color temperature to around 3100K. Because fluorescent technology does not depend on burning a filament to produce light, a wide range of color temperatures is possible.
Annual Operating Hours - is usually a calculated value equal to the total weekday, weekend, and holiday hours that the lighting system is operating during a one year period.
Color Temperature - or Correlated Color Temperature (CCT) is a measure of the light source's appearance to the eye. Color temperatures below 3000 degrees Kelvin indicate a yellowish, (or warm) tint. Medium color temperatures of 3500K indicate a neutral, whitish tint. Color temperatures above 4000K indicate a bluish, (or cool) tint. Kelvin is the absolute celsius temperature scale.
Drop-Down - is a slang term for a spreadsheet or webpage that has drop-down boxes that allow a user to easily pick an item of interest.
Efficacy - is a measure of a light source's relative efficiency. Measured in lumens per watt. High performance fluorescent lights have an efficacy greater than or equal to 95.
Elec - indicates a standard electronic ballast. The electronic ballast drives the lamp(s).
ESO - stands for Expanded Standard Offer. It is an expanded version of Bonneville Power Administration's Limited Standard Offer program. The ESO is designed to rebate end use power customers for significant improvements in lighting technologies and systems.
Fixture - is the housing for the lamp, ballast, lens, and reflector. Fixtures screwed together (butted up against each other) can be considered separate fixtures.
Fluorescent - is a lighting technology that produces light by exciting organic phosphor material on the inner wall of a glass tube or bulb.
Foot-candle - One foot-candle is equal to one lumen spread over one square foot.
HID - or high intensity discharge is a light source that produces light by creating an arc of electricity across two electrodes (think arc welding).
High Pressure Sodium - is an outdated, very yellowish looking HID light source.
HP - indicates high performance fluorescent products. So far, only T8 products have high performance capabilities. High performance is a generic term which is defined in the ESO contract.
IES - The Illuminating Engineering Society is responsible for setting standards and providing engineering support for the lighting industry. IES produces a handbook that is considered the bible of the industry.
Incandescent - was the first man-made, commercially usable, electrically driven light source invented by Thomas Edison over one hundred years ago. Basically, light is produced by burning a tungsten filament. When the filament burns, it gives off light. When the filament is burned out, the light goes out. Incandescent technology is limited to around 3100 degrees Kelvin because the tungsten filament cannot get any hotter without disintegrating.
Kelvin - is the absolute Celsius temperature scale. Zero degrees Kelvin represents absolute zero. Zero degrees Celsius corresponds to 273 degrees Kelvin.
Kilowatt - One kilowatt is = one volt * one amp * 1000 * power factor.
kWh - is a unit of energy typically used in the electrical industry. It is equivalent to one average kilowatt acting over a one hour period.
Lamp - is a generic term for an artificial light source.
Lighting System - typically refers to all of the luminaires inside and/or outside of a building. The term is also used interchangeably with luminaire. It is desirable to look at a luminaire as a system.
Lumen - is a measure of total light output of a lamp or luminaire.
Luminaire - includes the lamp, ballast, fixture, lens, reflector, etc.. In other words, the whole lighting unit.
Mean Lumens - or design lumens is an IES standard. Basically, the "mean or design" lumen output is the measured lumen output of the lamp or luminaire at 40% of the rated lamp life. To get the values used in the data tables, multiply lamp lumens * # lamps * bf * lumen maintenance factor.
Mercury - is a heavy metal used in fluorescent and HID lamps to conduct electricity and excite the fluorescent material (phosphors).
Mercury Vapor - is a very outdated HID light source. These are targeted for upgrade.
Metal Halide - is a neutral white appearing HID light source.
Phosphor - is a rare earth material that fluoresces under an electrical energy (ion) stimulus.
Tungsten - is the metal with the highest melting temperature. Thus, it is well suited for lighting technologies. Tungsten melts at around 3800 degrees Kelvin. However, tungsten becomes fragile around 2800 degrees Kelvin (typical incandescent temperature).
T8HP - a fluorescent tube 1 inch in diameter that has High Performance characteristics