SPECIAL SPECIFICATION

SECTION 15161

PUMPS - GENERAL

Page

PART 1 - GENERAL

1.01  	Work Included	2

1.02  	Related Work	2

1.03  	Pump Selection	2

1.04  	Pump Size And Type	3

1.05  	Certified Data	3

PART 2 - PRODUCTS

2.01  	Centrifugal Pumps	3

2.02  	Circulators	5

SPECIAL SPECIFICATION

SECTION 15161

PUMPS - GENERAL

PART 1 - GENERAL

1.01	WORK INCLUDED

This section provides general characteristics for pumps specified in Division 15 -Mechanical.

1.02	RELATED WORK

A.	Division 15 - Mechanical

1.	Insulation - Mechanical Systems, Section 15250.

2.	Piping Systems, Section 15051.

3.	System Component Checkout and Balance, Section 15901.

B.	Division 16 - Electrical.  Motors.

1.03	PUMP SELECTION

A.	Select pumps conservatively for scheduled conditions.  Furnish pumps which have reasonably high efficiencies, with peak efficiency at or near rated conditions.  Select pumps that will operate stably at 15-foot suction lift despite substantial reduction in head or substantial increase in delivery.

B.	If the pumps proposed are not considered suitable, submit manufacturer's data on other pumps, for review.

1.04	PUMP SIZE AND TYPE

Provide motor-driven pumps of the type, speed, and pump connection sizes scheduled on drawings.  Select pumps that are not overloaded throughout the entire range of pump operation.

1.05	CERTIFIED DATA

Submit manufacturer's certified pump curves for review.

PART 2 - PRODUCTS

2.01	CENTRIFUGAL PUMPS

A.	Acceptable Manufacturers

1.	Weinman.

2.	Aurora.

3.	Weil.

4.	ITT Bell & Gossett.

B.	Casing.  Provide a cast iron, volute type, centrifugal pump with screwed or Class 125 ANSI flanged connection and tapped openings for vent and drain, equipped with petcocks.  Casing for pumps 3"x4" and larger must accommodate an impeller 15 percent greater in diameter than the impeller actually selected to meet specified performance.  Design casings to provide for complete removal of bearing, seals and impeller without disturbing connection piping.

C.	Impeller.  Furnish an enclosed, cast bronze impeller, keyed and locked to the shaft, statically and hydraulically balanced.

D.	Wearing Rings.  Provide bronze, renewable wearing rings on all pumps 1-1/2 inches and larger.

E.	Shaft.  Furnish a stainless steel shaft, turned and ground to accurate dimension, of ample size to prevent deflection and key slotted as required.

F.	Bearing.  Provide antifriction type bearings, grease lubricated.

G.	Stuffing Box and Shaft Sleeves.  Furnish a deep, integral stuffing box, packed with suitable die-formed ring packing.  Provide a leakage water-cooled, bronze gland with stainless steel studs and nuts.  Furnish one-piece, machined-bronze shaft sleeves, keyed and locked to the shaft, extending from the impeller hub through the stuffing box, with a compression seal to prevent leakage between shaft and sleeve.  Provide bronze, water-deflection ring on the outboard end of the sleeve, and a galvanized metal cover over stuffing box.  Provide seal cage and seal piping on pumps operating at 5 feet (1.5m) of water pressure or less.  Design pump so that mechanical seals may be installed in lieu of packing at a later date.

H.	Support Bracket.  Furnish a cast iron, pump support bracket for close-coupled pumps.  Machine the bracket for rabbet jointing to pump casing and motor-end bracket to maintain rigid assembly and accurate alignment between pump and motor.

I.	Pedestals.  Furnish a cast iron pump and bearing pedestal for pedestal-mounted pumps.  Machine the pump bracket for rabbet jointing to pump casing.  precision bore the bearing support to provide accurate alignment between bearings and pump.

J.	Motor Extension Shaft.  For close-coupled pumps, provide a motor with an extension shaft and a special end bracket.  Machine the end bracket to receive the pump support bracket for rigid bolted assembly to ensure permanent, accurate alignment of pump and motor.

K.	Couplings.  Provide a flexible mechanical coupling rated for the full rated horsepower of the driving motor at motor speed.

L.	Base Plates.  Mount the pump assembly and the motor on a common rigid steel or cast iron base fabricated and arranged to ensure rigid and true alinement of pump and motor shafts.

1.	Provide a cast iron base where pump is VFD driven.

2.	Furnish base plate with drop pan having tapped drain opening.

3.	Use chilled water pumps with extended steel base big enough to receive all drip from suction and discharge flanges.

M.	Motors.  All motors for pumps shall be 1750 rpm, TEFC.  Baldor, high efficiency variable torque.

N.	Two-speed motors shall be high efficiency, ODP, separate winding, variable torque.

2.02	CIRCULATORS

Furnish an all-bronze centrifugal circulator designed for in-line mounting, with a resiliently mounted motor, a centrifugal impeller, an alloy-steel shaft with thrust collar, a bronze sleeve bearing, a mechanical seal, a spring-type flexible coupling, and a wick-type oil circulating system.

END OF SECTION