4 June 2007

CMS FPIX Vulnerability Assessment Workshop Review Findings

30 May 2007 Presentations

Session: Slow Controls and Fast Interlock

Facilitators: M. Chertok, B. Cooper, L. Bagby, R. Schmitt

FPIX Technical contact: C. Newsom, L. Cremaldi

General comments from facilitators

These general comments are intended to outline an approach to monitoring, interlocks, and controls and to serve as a reminder of issues to be considered as the systems are developed.  In no way are they intended to suggest that issues have been overlooked.

We consider monitoring, alarms, and interlocks to be critical for the long-term, safe operation of the FPIX system.  Hazards which are potentially specific to FPIX include excessive irradiation, operation at an improper temperature, major loss of cooling, and exposure to water vapor with a concentration sufficient to lead to condensation.  We assume that other hazards, such as fire, flooding, leaks of cooling systems associated with other sub-detectors, magnet quenches, and electrical power fluctuations or disruptions are more likely to affect multiple detector sub-systems than to be specific to FPIX.  Verification should be made that a more global response leads to a proper response for FPIX.

Monitoring can serve the dual purposes of providing parameters useful during data analysis and providing inputs to the alarm and interlock systems.  The alarm system provides a warning that parameters have deviated significantly from normal; that may allow abnormal parameters to be corrected before they are sufficiently out-of-range to cause an interlock trip.  Interlocks should place the system into a safe state without human intervention if parameters are sufficiently out-of-range.

We note that experts could automatically be notified via an auto-dialer triggered by monitoring, alarm, and interlock systems.  That can allow a faster response to abnormal conditions, particularly if the operations crew is overwhelmed by multiple fault conditions.  The current plan is to have email automatically sent to all experts whenever there is a failure at a critical level.

It is useful to flag the first, and perhaps the second, fault condition of all alarm and interlock systems, thereby allowing the cause of a problem to be identified more easily.

The flags and times of the flags are automatically archived.

We understand that the ability to change alarm and interlock logic and set-points will be controlled administratively and, perhaps, by a system of keys.  That should be documented. This is very important. When I visited CERN Andromachi showed us just such a system. I will get more details from her during my next visit.

We suggest that interlock logic should be general enough and reviewed carefully enough to allow all FPIX operations to be conducted without the need for hardware jumpers, bypass keys, or software alterations.  We recognize that alarm and interlock set-points may need to be different for initial system check-out and final system operation.  It may be possible to accomplish that, while still ensuring safe operation, by limiting the range available for each set-point.   No hardware jumpers are possible. All bypasses are handled by the State Machine software. Special administrative priviledges (in the software) are required to do this.

The interlock system should be “fail-safe”, that is, it should place FPIX into a safe condition under single-component and plausible multiple component failures.  That may require some degree of redundancy.  For example, if FPIX power is to be removed to achieve a safe condition, multiple means to ensure power is removed may be needed.  There are multiple shut-down paths. The first one is through the PVSS system commands. The second is the PLC. The third is through the DSS system, for certain types of failures. For power failure, there is only the PLC and DSS. Since the DSS may not be activated for “lesser” crises (local power failure) so only one path exists in that case.

Full interlock system functionality should be checked by triggering a fault condition for each interlock input and appropriate combinations of inputs and verifying that the response is appropriate.  That check should be made before initial FPIX operation and at periodic intervals thereafter.  If the interlock system is serviced or modified, portions of the system that could be affected should be checked.  Initial testing is foreseen. Additional testing is clearly needed if we change anything.

As outlined in the document on DCS commissioning plans, there are still many steps that need completion. Clearly, integration with the CMS-wide DCS will be a critical step.  In a few places, more hardware (electronics, etc) is needed.  Is there a foreseen issue with procuring any of the necessary parts?  No. We have been following this closely. The integration will occur in many steps. An initial CMS integration test will be over ethernet (software exercise only). A stand alone system will be tested first at TIF, then at P5, then we will integrate it with CMS.

The PVSS software and integration sections are not written up yet.  It would be good to see a clear plan for completing this documentation.  Yes!

Comments from facilitators related to specific presentations

Forward Pixel DCS and DSS Systems (presentation by C. Newsom)

The detector safety system, as presented, is composed of monitoring the temperature and humidity of the detector in addition to experiment utilities, radiation levels, and solenoid magnet status. Status signals are sent to a PLC which generates trip signals to power supply modules.

It is unknown if the utility and global alarms are provided individually to the Pixel PLC or as a summated signal. We suggest understanding this issue so that appropriate reactions can be determined.  A written description of the interlock actions is recommended. It should include signals to and from the DSS, to and from the chiller and brine systems, whether interlocks reset automatically or have manual reset.  As far as I know communication to us is only one way over the hard lines. The summation of lines is not foreseen at this time.  The exact makeup of this part of the system is not yet fully designed. Work in this area is ongoing.

There are no mechanical type interlocks, Klixon or dry contact relays, in the system. We suggest that the group conduct a Risk Assessment with reference to the Safety Instrumented Systems standards IEC 61511-1, IEC 61511-2, and IEC 61511-3 to determine if the PLC generated trip signals are adequate. If not, mechanical devices should be included in the design.  It may be appropriate to provide a separate path which allows a minimal set of hard-wired devices to ensure FPIX safety.  The relay modules do not require PLC input during a failure exercise, only during setup. These are effectively “mechanical” once setup. In the case of a DSS signal, if the relay fails the rack power will be killed using the hardened rack DSS system.

It was stated that remote controlled coolant flow valves were requested on Pixel detector pipes. It wasn’t clear as to whether or not this request is actually being implemented. We suggest that the mechanism for controlling the coolant flow be understood. Remote controlled pneumatic valves are installed in the system. Additional fine flow balancing valves will be manually adjusted.  They will be in a radiation area when there is beam.

It appears that there is no mechanism to monitor the coolant flow rate to individual Pixel cooling loops. We suggest investigating how the flow rate can be monitored such that appropriate individual cooling loops can be controlled.  (At least one facilitator believes that flow rate monitoring of individual loops has already been planned). There is a calibrated reduction aperture with differential pressure gauges on each loop. The purpose of this system is to remotely measure the flow for each half cylinder.

The correspondence between power supply distribution and cooling loops needs to be understood. In the event of a coolant leak, one would want to power down the section of the detector that corresponds to the failed cooling loop. The group should confirm the capability of controlling the appropriate power supplies based on the planned electronics crate distribution.  This has been decided during the last week. The system will be divided into 8 sections, each independently interlocked.

A clear understanding of the dry gas, warm gas, and sniffer systems would be beneficial to determine if they are possible monitoring sources. For example, is it possible to use a sniffer pipe to measure Fluorocarbons? The dry gas system is now better understood. We have requested a sniffer and it has been denied. We were invited to pay for a sniffer if we can find one that will work. No funds are available for this.

Only a few details of the nitrogen purge system were presented.  Failure modes and back-up systems should be understood and taken into account.  In particular, we think there should be a more complete understanding of the provisions to ensure that FPIX will remain above dew point during an unplanned or extended power outage.  Would FPIX be warmed?  If so, how would that be accomplished?

The humidity of the incoming gas to the CMS detector is monitored. High humidity triggers a DSS line to shut down all systems. Failure of the flow also triggers the DSS.  It seems there is no other internal monitoring, at least at the DSS level. The current plan is to turn off the power of the FPIX and rely on the heat shield, which is multiply redundant, to maintain a cold state.

How have the humidity (HMX) and temperature (RTD) sensors that will actually be used in the detector been tested?

Yes, multiple times.

It is unclear whether the planned number of HMX is sufficient.  The diagram shows their placement in an arbitrary location, far from sensors.  It seems as if the tracker components have many more HMX’s than this.  At a minimum, a second HMX could be installed in each volume to provide some redundancy.

They misunderstood a statement by Christian. I tried to correct it but apparently was unsuccessful. We have 2 HMX per cylinder.

As mentioned in the talk, the cooling plant circulating pumps have no backup and will shut down during maintenance or during failures.  Since the FC-72 coolant has a high coefficient of thermal expansion, steps must be taken to ensure that this fluid can expand as necessary without damage to the FPIX system if the cooling circulation stops.

This is really important. Simon should ask Paola for the pressure relief valve settings for our particular lines.

It is mentioned that the FPIX PLC has a battery backup.  For how long can this backup provide power?

Not long. About 15 minutes. We have not personally tested this for our system.

The NIM article states that the effect of thermal cycling on the plaquettes has been extensively tested and is under control.  How about effects of humidity changes?  Is humidity only an issue if condensation occurs, or can damage or performance change even without condensation?  Condensation is the only thing that is the biggest danger. HV breakdown has never been observed in our systems.  We can examine the question of HV beakdown further.

A sketch of the interlock hardware architecture was presented and reference was made to docdb #1136 which covers PLC hardware.  The interlocks described were to have sixteen sensors wired directly to the PLC, and 16,000 temperature sensors read through the DAQ and fed to the PLC, where they would be used for interlocking, perhaps with voting software.  We recommend that the number of sensors used to trip power be limited.  A very large numbers of interlocked sensors will not improve the reliability but will increase the amount of nuisance trips.  This is something we are very aware of. Our main line of defense are the hard wired RTDs.

A plan for controlling interlock changes and bypassing is not yet written.  CMS might have such a plan. We will investigate further as mentioned above.

Information from the TIF interlock failure should be gathered to make sure the FPIX interlock system does not have the same problem.  The system was not even close to being fully operational when they tried to use it. It had not even been tested with real hardware when the first installation/DCS expert had to return to Fermilab.  It now is.

Critical Vulnerability & Forward Pixel DCS Alarms (presentation by L. Cremaldi)

Local and Global Alarm and Interlock tables are well underway. We suggest that the tables be expanded to include subsequent steps required to recover from cited problems. Perhaps a flow chart based on a matrix of the tables would be useful. An FMEA for each component in the FPIX and circulation system is recommended.

We will  begin with a  flow chart. I may be ambitious enough to write a simulator.  With adequate manpower support an FMEA analysis  could be contracted.

Interlocks may be based on absolute temperatures, coolant level, etc., or may be based on rate-of-change.  It was stated that FPIX would run at 37C with cooling off but with heat shield on.  Also that silicon damage would occur at 20C after radiation.  A document defining all trip points is recommended.

Yes some of the above absolute temperature limits  are being understood  in tests at SiDet and CERN.  We need to further document the 37C and 20C limits.  Actually this data is in error. The actual number is 27C, or 37C above the heat shield temperature of -10C. The point is valid, however.

Careful development, review, and testing of interlock logic are critical to ensuring safe FPIX operation.  Maximum and minimum design limits for temperature, pressure, and flow throughout the system should be determined and taken into account.

As the PLC code is further developed these trip points will have to be determined.  The DSS has some protections on the cooling plant and N2 flush.  We need to determine if these also ensure safe operations for the pixel detector and implement  other fail-safes  in our DCS.

Interlock and alarm functions, operational sequences, and recovery from an interlock interrupt should be taken into account for all system modes, including warm start-up, cooldown, cold start-up, cold operation, warm-up, and servicing.

Sequenccs for all imaginable detector operations will have to be will have to be written.

You have given a core set above. We fully intend to comply.

A decision tree should be prepared providing steps that will be taken if, for example, the barrel pixels DCS system detects a problem even if the FPIX system does not.

This is possible and we need to think through the scenarios.

Conversely, we should plan to communicate the FPIX DCS readings to the other sub-detectors as well.  Finally, we should prepare for the possibility that cooling conditions of other sub-detectors might impact some FPIX alarm or interlock set points.

Yes we have been operating mostly in our Pixel space. Some interaction has already occurred and is expected to grow.  This should be formalized.