Site: 	Office of River Protection Hanford

Facility: 	Tank Farms, 291-AR Filter Building

System:  	Fire Protection System

System Classification:  	General Service System

System Safety Function:	Provide Fire Protection for the 291-AR Filter Building

OBJECTIVE:

VSS-1	This vital safety system is operational and personnel and processes are in place that ensures its continued operational readiness.

VSS-1.1	VSS safety functions are defined and understood by responsible line managers, and supporting information/documentation is available and adequate.  System testing is adequate to ensure operability.  (Review Approach items 1, 2, 3 and 7)

Discussion of Results –

This building contains no fire protection system.  This building houses an inactive HEPA exhaust filter system (shutdown in ~1986).  There is a very limited amount of combustible material located within the building (the contents consist of HEPA filters and housings located within an underground concrete structure).  The building is an unmanned facility and access is limited by Operations.  No testing is performed, because there isn’t any fire detection or suppression systems installed in the structure.  The filter building and the associated stack have been isolated from the 244-AR process building.  There are no current plans to reactivate the inactive exhaust system.  As stated in Section 2.4.7.2, “Ventilation Systems,” (for the 244-AR facility) of the Final Safety Analysis Report (HNF-SD-WM-SAR-067, Rev. 2), “These systems are not currently operable, and significant modifications or upgrades would be required to return these systems to service.”

In accordance with the Tank Farm Fire Hazards Analysis (WHC-SD-WM-FHA-020, Rev. 0) section 3.9, “244-AR Vault,” the document states that “The 244-AR Vault is currently in transition to decontamination and decommissioning.  Therefore, the facility description only summarizes the major components and structures within the facility.  All other systems within the facility are assumed to be inactive, de-energized or isolated.”  The 291-AR filter building supports the operation of the exhaust ventilation system for the 244-AR facility.  In accordance with the Tank Farm Fire Hazards Analysis (WHC-SD-WM-FHA-020, Rev. 0) Table 5-1, “Summary of Tank Farm Fire Protection Features,” the summary does not specify any fire protection requirements for the 291-AR facility.

In conclusion, the fire hazards analysis does not require any fire protection features be installed in the 291-AR filter building.

VSS-1.2	The backlog for surveillances, tests, inspections, maintenance, repair, upgrades, or other work on the system is managed and kept to an appropriate minimum.  (Review Approach item 6)

Discussion of Results –

No testing is performed.  No backlog exists for this facility.  No work occurs within the facility.  No planned or future upgrades are envisioned.  This facility and its contents will remain in their current inactive status.

VSS-1.3	Configuration Management and Maintenance programs effectively ensure operational availability of the system.  (Review Approach items 5, 8 and 9)

Discussion of Results –

Procedure HNF-IP-0842, Volume IX, Section 5.4, "Fire Hazards Analysis/Fire Protection Facility Assessment Requirements," establishes the criteria for conducting formal assessments of CHG facilities.  All Tank Farm Fire Protection Facility Assessments are conducted at frequencies established in this procedure.  The procedure is in accordance with DOE Order 5480.7A, “Fire Protection.”

A complete update/rewrite of the Tank Farm Fire Hazards Analysis has been funded and scheduled for completion during FY 2001.  The revised analysis will address the 291-AR facility.

The information provided in the next three paragraphs identify programs are in place should drawings, procedures, work packages, etc. need to be developed for a 291-AR fire protection system (should it ever be required).

Drawings and other design media (e.g., supporting documents) supporting the 291-AR filter building are maintained per the following non-inclusive list of established engineering procedures.

- HNF-IP-0842, Volume IV, Section 3.5 – Engineering Documents

- HNF-IP-0842, Volume IV, Section 4.25 – Equipment Temporary Modifications and Bypasses

- HNF-IP-0842, Volume IV, Section 4.29 – Engineering Document Change Control Requirements

- HNF-IP-0842, Volume IV, Section 5.4 – Unreviewed Safety Question Requirements

- RPP-PRO-1819 – Engineering Requirements

- HNF-PRO-224 – Document Control Program Standards

Documentation to allow field work/modifications to be performed on the 291-AR filter building shall be in accordance with the RPP work control process

(HNF-IP-0842, Volume V, Section 7.1 – Tank Farm Contractor Work Control).

Should maintenance, test or operating procedures ever be required the following procedures are applicable.  Maintenance, test, and operating procedures/ roundsheets are generated and modified per the RPP procedure (HNF-IP-0842, Volume I, Section 2.11- Technical Procedure Control and Use).  In addition, test procedures meet the requirements referenced within the RPP testing procedure (HNF-IP-0842, Volume IV, Section 4.28 – Testing Practices Requirements).

VSS-1.4	The system is operable and available to fulfill its safety function when required.  (Review Approach items 4 and 10)

Discussion of Results –

There is no safety function for the 291-AR fire protection system, because there is no installed detection or suppression systems.  Operability and availability don’t apply.

CONCLUSIONS:

All facilities are analyzed for compliance with NFPA 80A, "Recommended Practice for Protection of Buildings from Exterior Fire Exposures."  This analysis helps assure that fire from the outside of the building will not affect the facility.  The standard ground cover around/above the 291-AR filter building is gravel and pavement that provides a firebreak.  Operations crews routinely clean up transient combustibles.  This facilities replacement cost is valued at over $1M and should have a fire suppression or detection system installed.  The facility and its equipment are not operational and installing a fire suppression system for this non-occupied building is currently not planned.

A new Tank Farm Contractor fire hazards analysis (FHA) has been initiated.  The FHA is scheduled for completion in FY 2001 and is funded.  The process will include a review of all facilities especially in regards to facilities that are being decontaminated and decommissioned.  The process includes as a final step, issuing exemptions for those facilities that will not meet code requirements as specified in the Standards/Requirements Identification Document (HNF-SD-MP-SRID-001, Section 12.8).  An update to the Fire Hazards Analysis has been initiated to re-evaluate the fire hazards and determine adequate required protection.

DOE employee who reviewed this assessment  ___DOE Review Team_____ Date __2/28/01_

(*See below)

Hours required for completing the assessment.

DOE:      40      Hrs.

Contractor:    66    Hrs.

*Harkins, BA

Harp, BJ

Harwood, RG

Noorani, YG

Sullivan, RS

Trenchard, GD

Wade, KG

Williamson, BI

Wright, TC