Fort Smith National Historic Site
 Frisco Depot

Fort Smith, Arkansas

ROOFING  SPECIFICATION

PART 1  GENERAL

1.01  GENERAL REQUIREMENTS

A.	Deviations:  In the event this Specification deviates from the manufacturer's current specification, this specification prevails, except where they conflict with the manufacturer's requirements for the specified guarantee.  In this case, the manufacturer's specification prevails.

B.	Specification Amendments:  Drawings, addenda and modifications may be issued subsequent to the printing of this Specification.

C.	Contractor Acceptance:  Prior to the project start, ascertain that all aspects of this Specification and possible modifications are workable and do not conflict with the manufacturer's requirements for the specified guarantee.  Upon commencement of the work, it will be presumed that this Specification and drawings, addenda and modifications are satisfactory to both the Contractor and the manufacturer in their entirety.

D.	Supplied Materials:  Supply all materials of the roofing system, including accessory products.  The bidding Contractor, by making his bid, represents that his bid price is based on the use of the materials listed in Part 2 Products.  Refer to Part 1.03 Description of Work for specific use within each roofing assembly outlined.

1.02  REFERENCE STANDARDS

References in these specifications to standards, test methods, and codes, are implied to mean the latest edition of each such standard adopted.  The following is an abbreviated list of associations, institutions, and societies which may be used as references throughout these specifications.

ASTM	American Society for Testing and Materials

Philadelphia, PA

FM	Factory Mutual Engineering and Research

Norwood, MA

NRCA	National Roofing Contractors Association

Rosemont, IL

OSHA	Occupational Safety and Health Administrations

Washington, DC

SMACNA	Sheet Metal and Air Conditioning Contractors National Association

Chantilly, VA

UL	Underwriters Laboratories

Northbrook, IL

1.03  DESCRIPTION OF WORK

The basic work descriptions (components, layering and attachment methods) required in this specification are referenced below.

Project Type:	Tear-off	Specification #:  2030 IH-T

Deck:	Wood	Slope:  1/2 inch

Crickets:	Tapered Paratherm crickets, providing for a roof slope of 1/2 inch per foot, mechanically attached simultaneously with the top layer of insulation.

Insulation:	DensDeck DuraGuard, by Georgia Pacific Corporation, having a thickness of 1/2 inch, mechanically attached, or approved  equal

Roof system:	Paradiene 20, applied in PA-100 Asphalt; or approved equal

Paradiene 30 FR TG, torch applied or approved equal.

Flashing system:	Veral Aluminum, torch applied or approved equal.

1.04  QUALITY ASSURANCE

A.	Acceptable Products:  Primary roofing products, including each type of sheet, all manufactured in the United States, shall be supplied by a single manufacturer which has been successfully producing the specified types of primary products for not less than 10 years.  The primary roofing products shall have maintained a consistent composition for a minimum of five years.

B.	Product Quality Assurance Program:  Primary roofing materials shall be manufactured under a quality management system that is monitored regularly by a third party auditor under the ISO 9001:2000 audit process.  A certificate of analysis for reporting/confirming the tested values of the actual material being supplied for the project will be required prior to project close-out.

C.	Agency Approvals:  The proposed roof system shall conform to the following requirements.  No other testing agency approvals will be accepted.

1.	Underwriters Laboratories Class A acceptance of the proposed roofing system (including mopping asphalt or cold adhesive) without additional requirements for gravel or coatings.

D.	Acceptable Contractor:  Contractor shall have a minimum of 2 years experience in successfully installing the same or similar roofing materials and be certified in writing by the roofing materials manufacturer to install the primary roofing products.

E.	Scope of Work:  The work to be performed under this specification shall include but is not limited to the following:  Attend necessary job meetings and furnish competent and full time supervision, experienced roof mechanics, all materials, tools, and equipment necessary to complete, in an acceptable manner, the roof installation in accordance with this specification.  Comply with the latest written application instructions of the manufacturer of the primary roofing products.  In addition, application practice shall comply with requirements and recommendations contained in the latest edition of the Handbook of Accepted Roofing Knowledge (HARK) as published by the National Roofing Contractor's Association, amended to include the acceptance of a phased roof system installation.

F.	Local Regulations:  Conform to regulations of public agencies, including any specific requirements of the city and/or state of jurisdiction.

G.	Manufacturer Requirements:  Ensure that the primary roofing materials manufacturer provides direct trained company personnel to attend necessary job meetings, perform periodic inspections as necessary, and conducts a final inspection upon successful completion of the project.

1.05  GUARANTEE/WARRANTY

A.	Roof Membrane Guarantee:  Upon successful completion of the project, and after all post installation procedures have been completed, furnish the Owner with the manufacturer's ten year labor and materials membrane guarantee.  The guarantee shall be a term type, without deductibles or limitations on coverage amount, and shall be issued at no additional cost to the Owner.  This guarantee shall not exclude random areas of ponding from coverage.

>	Siplast ten year Roof Membrane Guarantee or approved equal to match Guarantee

1.06  SUBMITTALS

All submittals which do not conform to the following requirements will be rejected.

A.	Submittal of Equals:  Submit primary roof systems to be considered as equals to the specified roof system no less than 10 days prior to bid date.  Primary roof systems which have been reviewed and accepted as equals to the specified roof system will be listed in an addendum prior to bid date; only then will equals be accepted at bidding.  Submittals shall include the following:

1.	Two 3 inch x 5 inch samples of the primary roofing and flashing sheets.

2.	Latest edition of the roofing system manufacturer's specifications and installation instructions.

3.	Evidence that the manufacturer of the proposed roofing system utilizes a quality management system that is ISO 9001:2000 certified.  Documentation of ISO 9001:2000 certification of foreign subsidiaries without domestic certification will not be accepted.

4.	Evidence and description of manufacturer's quality control/quality assurance program for the primary roofing products supplied.  The quality assurance program description shall include all methods of testing for physical and mechanical property values.  Provide confirmation of manufacturer's certificate of analysis for reporting the tested values of the actual material being supplied for the project prior to issuance of the specified guarantee.

5.	Descriptive list of the materials proposed for use.

6.	Evidence of Underwriters' Laboratories Class A acceptance of the proposed roofing system (including mopping asphalt or cold adhesive) without additional requirements for gravel or coatings.  No other testing agency approvals will be accepted.

7.	Letter from the proposed primary roofing manufacturer confirming that a phased roof application, with only the modified bitumen base ply in place for a period of up to 10 weeks, is acceptable and approved for this project.

8.	List of 3 of the proposed primary roofing manufacturer's projects, located in the United States, of equal size and degree of difficulty which have been performing successfully for a period of at least 10 years.

9.	Letter from the proposed primary roofing manufacturer confirming that the filler content in the elastomeric blend of the proposed roof membrane and flashing components does not exceed 35% in weight.

10.	Complete list of material physical and mechanical properties for each sheet including: weights and thicknesses; low temperature flexibility; peak load; ultimate elongation; dimensional stability; compound stability; Compound stability; granule embedment and resistance to thermal shock for foil faced products.

11.	Sample copy of the proposed guarantee.

12.	Completed Product Substitution Request Form included with this specification section.

B.	Submittals with Bid:

1.	Submit a price per board foot to furnish/install Paraslope over the Paradiene 20 or approved equal,surface to facilitate drainage.

C.	Submittals Prior to Contract Award:

1.	Letter from the proposed primary roofing manufacturer confirming that the bidder is an acceptable Contractor authorized to install the proposed system.

2.	Letter from the primary roofing manufacturer stating that the proposed application will comply with the manufacturer's requirements in order to qualify the project for the specified guarantee.

D.	Submittals Prior to Project Close-out:

1.	Manufacturer's printed recommendations for proper maintenance of the specified roof system including inspection frequencies, penetration addition policies, temporary repairs, and leak call procedures.

1.07  PRODUCT DELIVERY STORAGE AND HANDLING

A.	Delivery:  Deliver materials in the manufacturer's original sealed and labeled containers and in quantities required to allow continuity of application.

B.	Storage:  Store materials out of direct exposure to the elements.  Store roll goods on a clean, flat and dry surface.  All material stored on the roof overnight shall be stored on pallets.  Rolls of roofing must be stored on ends.  Store materials on the roof in a manner so as to preclude overloading of deck and building structure.  Store materials such as solvents, adhesives and asphalt cutback products away from open flames, sparks or excessive heat.  Cover all material using a breathable cover such as a canvas.  Polyethylene or other non-breathable plastic coverings are not acceptable.

C.	Handling:  Handle all materials in such a manner as to preclude damage and contamination with moisture or foreign matter.  Handle rolled goods to prevent damage to edges or ends.

D.	Damaged Material:  Any materials that are found to be damaged or stored in any manner other than stated above will be automatically rejected, removed and replaced at the Contractor's expense.

1.08  PROJECT/SITE CONDITIONS

A.	Requirements Prior to Job Start

1.	Notification:  Give a minimum of 5 days notice to the Owner and manufacturer prior to commencing any work and notify both parties on a daily basis of any change in work schedule.

2.	Permits:  Obtain all permits required by local agencies and pay all fees which may be required for the performance of the work.

3.	Safety:  Familiarize every member of the application crew with all fire and safety regulations recommended by OSHA, NRCA and other industry or local governmental groups.

B.	Environmental Requirements

1.	Precipitation:  Do not apply roofing materials during precipitation or in the event there is a probability of precipitation during application.  Take adequate precautions to ensure that materials, applied roofing, and building interiors are protected from possible moisture damage or contamination.

2.	Temperature Restrictions - asphalt:  At ambient temperatures of 40(F (4(C) and below, special precautions must be taken to ensure that the specified Type IV asphalt maintains a minimum acceptable 400(F (204(C) at the point of sheet application.  The asphalt must not be overheated to compensate for cold conditions.  The use of insulated handling equipment is strongly recommended.  Hot luggers, mop carts, and kettle-to-roof supply lines should be insulated.  Hand mops should be constructed with a smaller yarn head to facilitate short moppings.  Luggers and mop carts should never be more than half filled at all times.

C.	Protection Requirements

1.	Membrane Protection:  Provide protection against staining and mechanical damage for newly applied roofing and adjacent surfaces throughout this project.

2.	Torch Safety:  Crew members handling torches shall be trained by an Authorized Certified Roofing Torch Applicator (CERTA) Trainer, be certified according to CERTA torch safety guidelines as published by the National Roofing Contractor's Association (NRCA), and follow torch safety practices as required by the contractor's insurance carrier.  Designate one person on each crew to perform a daily fire watch.  The designated crew member shall watch for fires or smoldering materials on all areas during roof construction activity, and for the minimum period required by CERTA guidelines after roofing material application has been suspended for the day.

3.	Limited Access:  Prevent access by the public to materials, tools and equipment during the course of the project.

4.	Debris Removal:  Remove all debris daily from the project site and take to a legal dumping area authorized to receive such materials.

5.	Site Condition:  Complete, to the owner's satisfaction, all job site clean-up including building interior, exterior and landscaping where affected by the construction.

PART 2  PRODUCTS

2.01  ROOFING SYSTEM ASSEMBLY/PRODUCTS

A.	Rigid Roof Insulation:  Roof insulation shall be UL and FM approved.  Insulation shall be approved in writing by the insulation manufacturer for intended use and for use with the specified roof assembly.  Maintain a maximum panel size of 4 feet by 4 feet where insulation is specified to be installed in hot asphalt or insulation adhesive.

1.	Polyisocyanurate Tapered Crickets:  Tapered panels and standard fill panels composed of a closed cell, rigid polyisocyanurate foam core material, integrally laminated between glass fiber facers, in full compliance with ASTM C 1289, Type II, Class 1, Grade 2.  The tapered system shall provide for a roof slope of 1/2 inch per foot.  Acceptable types are as follows.

>	Tapered Paratherm by Siplast; Irving, TX or approved equal

2.	Perlite Tapered Edge Panels:  A tapered panel composed of expanded volcanic minerals combined with waterproofing binders.  The top surface shall be pre-treated with an asphalt based coating.  The panels shall have a dimension sufficient to provide for a smooth transition and provide proper support for the membrane layer or subsequent layer of insulation when there are transitions of 1/4 inch or greater.

3.	Gypsum Sheathing Panel:  A panel composed of a gypsum based, non-structural water resistant core material integrally bonded with fiberglass mats on both sides having a nominal thickness of 1/2 inch.  The panel surface shall be factory coated with a low permeability, heat-cured coating.  Acceptable types are as follows:

>	DensDeck DuraGuard Gypsum Roof Board, by Georgia Pacific Corporation; Atlanta, GA or approved equal

4.	Gypsum Sheathing Panel for Wood/Plywood Substrates to Receive Flashing Coverage:  A panel composed of a gypsum based, non-structural water resistant core material integrally bonded with fiberglass mats on both sides having a nominal thickness of 1/4 inch.  The panel surface shall be factory primed with a non-asphaltic primer.  Acceptable types are as follows:

>	DensDeck Prime Gypsum Roof Board, by Georgia Pacific Corporation; Atlanta, GA or approved equal

2.02  DESCRIPTION OF SYSTEMS

A.	Roofing Membrane Assembly:  A roof membrane assembly consisting of two plies of a prefabricated, reinforced, homogeneous Styrene-Butadiene-Styrene (SBS) block copolymer modified asphalt membrane, applied over a prepared substrate.  Both reinforcement mats shall be impregnated/saturated and coated each side with an SBS modified bitumen blend.  The modified bitumen finish ply shall be coated one side with a torch grade SBS bitumen blend adhesive layer.  The cross sectional area of the sheet material shall contain no oxidized or non-SBS modified bitumen.  The adhesive layer shall be manufactured using a process that embosses the surface with a grooved pattern to provide optimum burn-off of the plastic film and to maximize application rates.  The roof system shall pass 500 cycles of ASTM D 5849 Resistance to Cyclic Joint Displacement (fatigue) at 14(F (-10(C).  Passing results shall show no signs of membrane cracking or interply delamination after 500 cycles.  The roof system shall pass 200 cycles of ASTM D 5849 after heat conditioning performed in accordance with ASTM D 5147.  The assembly shall possess waterproofing capability, such that a phased roof application, with only the modified bitumen base ply in place, can be achieved for prolonged periods of time without detriment to the watertight integrity of the entire roof system.

>	Siplast Paradiene 20/30 FR TG roof system or approved equal

1.	Modified Bitumen Base, Stripping Ply, and Flashing Reinforcing Ply

a)	Thickness (avg):  91 mils (2.3 mm)  (ASTM D 5147)

b)	Thickness (min):  87 mils (2.2 mm)  (ASTM D 5147)

c)	Weight (min per 100 ft² of coverage):  62 lb (3.0 kg/m²)

d)	Maximum filler content in elastomeric blend - 35% by weight

e)	Low temperature flexibility @ -13F (-25C):  PASS  (ASTM D 5147)

f)	Peak Load (avg) @ 73F (23C):  30 lbf/inch (5.3 kN/m) (ASTM D 5147)

g)	Peak Load (avg) @ 0F (-18C):  70 lbf/inch (12.3 kN/m) (ASTM D 5147)

h)	Ultimate Elongation (avg.) @ 73F (23C):  50%  (ASTM D 5147)

i)	Dimensional Stability (max):  0.1%  (ASTM D 5147)

j)	Compound Stability (min):  250F (121C)  (ASTM D 5147)

k)	Approvals:  UL Class listed, FM Approved (products shall bear seals of approval)

l)	Reinforcement:  fiberglass mat or other meeting the performance and dimensional stability criteria

>	Siplast Paradiene 20 or approved equal

2.	Modified Bitumen Finish Ply

a)	Thickness  (avg):  138 mils (3.5 mm)  (ASTM D 5147)

b)	Thickness at selvage (coating thickness) (avg):  118 mils (3.0 mm)  (ASTM D 5147)

c)	Thickness at selvage (coating thickness) (min):  114 mils (2.9 mm)  (ASTM D 5147)

d)	Weight (min per 100 ft² of coverage):  112 lb (5.4 kg/m²)

e)	Maximum filler content in elastomeric blend:  35% by weight

f)	Low temperature flexibility @ -13F (-25C):  PASS  (ASTM D 5147)

g)	Peak Load (avg) @ 73F (23C):  30 lbf/inch (5.3 kN/m) (ASTM D 5147)

h)	Peak Load (avg) @ 0F (-18C):  75 lbf/inch (13.2 kN/m)  (ASTM D 5147)

i)	Ultimate Elongation (avg.) @ 73F (23C):  55%  (ASTM D 5147)

j)	Dimensional Stability (max):  0.1%  (ASTM D 5147)

k)	Compound Stability (min):  250F (121 C)  (ASTM D 5147)

l)	Granule Embedment (max loss):  2.0 grams per sample  (ASTM D 5147)

m)	Approvals:  UL Class listed, FM Approved (products shall bear seals of approval)

n)	Reinforcement:  fiberglass mat or other meeting the performance and dimensional stability criteria

o)	Surfacing:  ceramic granules

>	Siplast Paradiene 30 FR - torchable grade or approved equal

B.	Flashing Membrane Assembly:  A flashing membrane assembly consisting of a prefabricated, reinforced, Styrene-Butadiene-Styrene (SBS) block copolymer modified asphalt membrane with a continuous, channel-embossed metal-foil surfacing.  The finish ply shall conform to ASTM D 6298 and the following physical and mechanical property requirements.

>	Siplast Veral flashing system, aluminum finish or approved equal

1.	Cant Backing Sheet for Wood/Plywood Surfaces to Receive Flashing Coverage

a)	Thickness (avg):  102 mils (2.6 mm)  (ASTM D 5147)

b)	Thickness (min):  98 mils (2.5 mm)  (ASTM D 5147)

c)	Weight (min per 100 ft² of coverage):  72 lb (3.5 kg/m²)

d)	Maximum filler content in elastomeric blend:  35% by weight

e)	Low temperature flexibility @ -13 F (-25 C) - PASS  (ASTM D 5147)

f)	Peak Load (avg) @ 73F (23C):  30 lbf/inch (5.3 kN/m) (ASTM D 5147)

g)	Peak Load (avg) @ 0F (-18C):  75 lbf/inch (13.2 kN/m) (ASTM D 5147)

h)	Ultimate Elongation (avg.) @ 73F (23C):  50%  (ASTM D 5147)

i)	Dimensional Stability (max):  0.1%  (ASTM D 5147)

j)	Compound Stability (min - sheet):  250F (121C)  (ASTM D 5147)

j)	Compound Stability (min – adhesive coating):  212F (100C)  (ASTM D 5147)

k)	Approvals:  UL Class listed, FM Approved (products shall bear seals of approval)

l)	Reinforcement:  fiberglass mat or other meeting the performance and dimensional stability criteria

m)	Back Surfacing:  polyolefin film

>	Siplast Paradiene 20 SA or approved equal

2.	Metal-Clad Modified Bitumen Flashing Sheet

a)	Thickness (avg):  142 mils (3.6 mm)  (ASTM D 5147)

b)	Thickness (min):  138 mils (3.5 mm)  (ASTM D 5147)

c)	Weight (min per 100 ft² of coverage):  92 lb (4.5 kg/m²)

d)	Coating Thickness – back surface (min):  40 mils (1 mm)  (ASTM D 5147)

e)	Maximum filler content in elastomeric blend:  35% by weight

f)	Low temperature flexibility @ 0 F (-18 C):  PASS  (ASTM D 5147)

g)	Peak Load (avg) @ 73F (23C):  85 lbf/inch (15 kN/m)  (ASTM D 5147)

h)	Peak Load (avg) @ 0F (-18C):  180 lbf/inch (31.7 kN/m)  (ASTM D 5147)

i)	Ultimate Elongation (avg) @ 73F (23C):  45%  (ASTM D 5147)

i)	Tear-Strength (avg):  120 lbf (0.54 kN)  (ASTM D 5147)

j)	Dimensional Stability (max):  0.2%  (ASTM D 5147)

k)	Compound Stability (min):  225F (107C)  (ASTM D 5147)

l)	Cyclic Thermal Shock Stability (maximum):  0.2%  (ASTM D 6298)

m)	Approvals:  UL Approved, FM Approved (products shall bear seals of approval)

n)	Reinforcement:  fiberglass scrim mat or other meeting the performance and dimensional stability criteria

o)	Surfacing:  aluminum metal foil

>	Siplast Veral Aluminum or approved equal

C.	Catalyzed Acrylic Resin Flashing System:  A specialty flashing system consisting of a liquid-applied, fully reinforced, multi-component acrylic membrane installed over a prepared or primed substrate.  The flashing system consists of a catalyzed acrylic resin primer, basecoat and topcoat, combined with a non-woven polyester fleece.  The resin and catalyst are pre-mixed immediately prior to installation.  The use of the specialty flashing system shall be specifically approved in advance by the membrane manufacturer for each application.

>	Parapro 123 Flashing System by Siplast; Irving, TX or approved equal

2.03  ROOFING ACCESSORIES

A.	Roofing Adhesives

1.	Mopping Asphalt:  Type IV asphalt certified for full compliance with the requirements listed in Table I, ASTM D 312.  Each container or bulk shipping ticket shall indicate the equiviscous temperature, EVT, the finished blowing temperature, FBT, and the flash point, FP.  Mopping asphalt shall be approved in writing by the roof membrane manufacturer.

>	Siplast PA-100 Asphalt by Siplast; Irving, TX or approved equal

B.	Bituminous Cutback Materials

1.	Primer:  A high flash, quick drying, asphalt solvent blend which meets or exceeds ASTM D 41 requirements.

>	Siplast PA-1125 Asphalt Primer by Siplast; Irving, TX or approved equal

2.	Mastics:  An asphalt cutback mastic, reinforced with non-asbestos fibers, used as a base for setting metal flanges conforming to ASTM D 4586 Type II requirements.

>	Siplast PA-1021 Plastic Cement by Siplast; Irving, TX or approved equal

C.	Sealant:  A moisture-curing, non-slump elastomeric sealant designed for roofing applications.  The sealant shall be approved by the roof membrane manufacturer for use in conjunction with the roof membrane materials.  Acceptable types are as follows:

>	Siplast PS-304 Elastomeric Sealant by Siplast; Irving, TX or approved equal

D.	Ceramic Granules:  No. 11 grade specification ceramic granules of color scheme matching the granule surfacing of the finish ply.

E.	Metallic Powder:  A finely graded metal dust as supplied or approved by the membrane manufacturer, used for covering of bitumen overruns over the foil surfaced membrane.

F.	Perlite Cant Strips:  A cant strip composed of expanded volcanic minerals combined with waterproofing binders.  The top surface shall be pre-treated with an asphalt based coating.  The face of the cant shall have a nominal 4 inch dimension.

G.	Fasteners

1.	Insulation Fasteners:  Insulation fasteners and plates shall be FM Approved, and/or approved by the manufacturer of the primary roofing products.  The insulation fasteners shall provide attachment required to meet the specified uplift performance and to restrain the insulation panels against the potential for ridging.  The fastening pattern for each insulation panel to be used shall be as recommended by the insulation manufacturer and approved by the manufacturer of the primary roofing products.  Acceptable insulation fastener manufacturers for specific deck types are listed below.

a)	Wood/Plywood Decks:  Insulation mechanical fasteners for wood/plywood decks shall be factory coated for corrosion resistance.  The fastener shall conform meet or exceed Factory Mutual Standard 4470 and when subjected to 30 Kesternich cycles, show less than 15% red rust.  Acceptable insulation fastener types for wood/plywood decks are listed below.

-	A fluorocarbon coated screw type roofing fastener having a minimum 0.245 inch thread diameter.  Plates used in conjunction with the fastener shall be a metal type having a minimum 3 inch diameter, as supplied by the fastener manufacturer.

>	Parafast HD Fastener by Siplast; Irving, TX or approved equal

2.	Gypsum Sheathing Panel Fasteners for Wood/Plywood Substrates to Receive Flashing Coverage:  Gypsum sheathing panel fasteners and plates shall be FM Approved, and/or approved by the manufacturer of the primary roofing products.  The fastening pattern for each panel to be used shall be as recommended by the panel manufacturer and approved by the manufacturer of the primary roofing products.  Acceptable panel fastener manufacturers for specific substrate types are listed below.

a)	Wood/Plywood Substrates to Receive Flashing Coverage:  Gypsum sheathing panel mechanical fasteners shall be factory coated for corrosion resistance.  The fastener shall conform meet or exceed Factory Mutual Standard 4470 and when subjected to 30 Kesternich cycles, show less than 15% red rust.  Acceptable fastener types for wood/plywood substrates are listed below.

-	A fluorocarbon coated screw type roofing fastener having a minimum 0.220 inch thread diameter.  Plates used in conjunction with the fastener shall be a metal type having a minimum 3 inch diameter, as supplied by the fastener manufacturer.

>	Parafast Fastener by Siplast; Irving, TX or approved  equal

3.	Flashing Reinforcing Sheet Fasteners for Wood/Plywood Substrates to Receive Flashing Coverage:  Fasteners shall be approved by the manufacturer of the primary roofing products.  Acceptable fasteners for specific substrate types are listed below.

a)	Wood/Plywood Substrates

-	A 12 gauge, spiral or annular threaded shank, zinc coated steel roofing fastener having a minimum 1 inch head.

>	Square Cap by W.H. Maze Co.; Peru, Ior equal

>	12 Gauge Simplex Nail by the Simplex Nail and Manufacturing Co., Americus, Ga or approved equal

4.	Wood Nailer Fasteners Wood blocking fasteners and plates shall be FM Approved, and/or approved by the manufacturer of the primary roofing products.  Acceptable fastener manufacturers are listed below.

a)	Wood Blocking:  Mechanical fasteners for wood blocking shall be factory coated for corrosion resistance.  Acceptable fastener types are listed below.

-	A fluorocarbon coated screw type roofing fastener having a minimum 0.220 inch thread diameter.  Plates used in conjunction with the fastener shall be a metal type having a minimum 3 inch diameter, as supplied by the fastener manufacturer.

>	Parafast Fastener by Siplast; Irving, or approved equal

H.	Walktread:  A prefabricated, puncture resistant polyester core reinforced, polymer modified bitumen sheet material topped with a ceramic-coated granule wearing surface.

1.	Thickness: 0.217 in (5.5 mm)

2.	Weight: 1.8 lb/ft² (8.8 kg/m²)

3.	Width: 30 in (76.2 cm)

>	Paratread Roof Protection Material by Siplast; Irving, TX or approved equal

2.04  RELATED COMPONENTS

A.	Rough Carpentry:  Lumber used for nailers, curbs, and cants shall be No. 2 kiln dried (19% maximum moisture content after treatment), grade marked, and surfaced on four sides.  Lumber shall be salt treated with Wolman Salts (wood shall retain 0.25 lbs. dry salt per cubic foot of wood) or an approved equal.

1.	Perimeter Nailers for Edge Metal Securement.  Lumber shall have a nominal 6 inch width with a thickness to match the height of the new insulation assembly.

2.	Wood Sleepers And Blocking:  Lumber blocking, used for supporting small rooftop and light air conditioning units shall have a 4 inch by 4 inch width and thickness.  Wood blocking used to support small pipes shall have a minimum 12 inch length.  Lengths of wood sleepers for supporting air conditioning units shall be such that a minimum of 12 inches shall extend beyond each unit at both sides.

B.	Perlite Cant Strips:  A cant strip composed of expanded volcanic minerals combined with waterproofing binders.  The top surface shall be pre-treated with an asphalt based coating.  The face of the cant shall have a nominal 4 inch dimension.

C.	Lead Drain Flashings:  Formable type, weighing a minimum of 4 lb. per square foot; in sheets of minimum 30 inch x 30 inch dimension.

D.	Lead Pipe Flashings:  Preformed from sheet stock weighing a minimum of 4 lb. per square foot, and soldered with a minimum 4 inch perimeter flange with a sleeve opening fabricated to fit closely around the penetration without forcing.  Lead sleeve length shall be of sufficient height to allow a minimum of 1 inch to be crimped inside of the pipe stack.

E.	Fabricated Metal:  Fabricate the following fabricated metal components from minimum 24 gauge, G 90 galvanized steel, primed and coated with a 70% Kynar based fluoropolymer coating of 1.0 + 0.1 mil total dry film thickness.  Color to be selected by the owner.

1.	Metal Edge/Fascia:  Fabricate metal edge/fascia incorporating a 4 inch perimeter flange with a minimum 1/4 inch gravel stop rise.  The fascia shall be of sufficient width to adequately cover the roof assembly/wall juncture.  The bottom edge of the fascia shall have a minimum 1/2 inch drip edge, hemmed and formed at 30 degrees and shall be fabricated for attachment to a continuous cleat at the outside base of the nailer.  Fabricate metal edge/fascia in maximum 10 feet sections.  Fabricate corner pieces of metal edge fascia with 1 foot sections in either direction from the corner.  Fabricate cover plates and accessory components in accordance with SMACNA guidelines.

2.	Metal Pipe Flashings:  Fabricate metal pipe flashings in a two-component assembly in accordance with the following:

-	The first component shall be a metal roof jack having a minimum 4 inch perimeter flange, and a sleeve opening to fit closely around the penetration without forcing, with a minimum 6 inch height.  Fasten and solder metal laps.

-	The second component shall be a metal, water tight umbrella, fabricated to be mechanically secured tightly around the roof penetration and extend beyond the roof jack opening by a minimum radius of 3 inches.  Caulk top edge of the watertight umbrella using an approved sealant.

PART 3 EXECUTION

3.01  FIELD QUALITY CONTROL

A.	Pre-Job Conference:  Conduct a pre-job conference to include the designer, Owner, roofing Contractor and manufacturer's representative prior to application of roofing.

B.	Foremen:  Provide the roofing foreman with a copy of these specifications to be available at the job site at all times.  The presence of specifications and an inspector shall not relieve the Contractor of strict compliance with the manufacturer's specifications, detail drawings, and/or approved material requirements.

C.	Deck Penetrations:  Verify that work penetrating the roof deck, or which may otherwise affect the roofing application, has been properly completed.

D.	Final Inspection – post installation meeting:  Arrange a meeting at the completion of the project to be attended by all parties that were present at the pre-job conference.  A punch list of items required for completion shall be compiled by the Contractor and the manufacturer's representative.  Complete, sign, and mail the punch list form to the manufacturer's headquarters.

3.02  PREPARATION

A.	General:  Sweep or vacuum all surfaces, removing all loose aggregate and foreign substances prior to commencement of roofing.

B.	Remove All Existing:

- Surface gravel

- Roof membrane

- Insulation

- Base flashings

- Edge metal

- Flanged metal flashings

- Cants

- Walkways

- Non functional penetrations/curbs

- Drain assemblies

- Vapor retarder

- Metal trim, counterflashing

C.	Damaged And/Or Deteriorated Deck:  Inspect decking; make necessary repairs or replace sections of deck that cannot be repaired.  Submit a unit price for replacement of sections of roof deck.

D.	Wall Preparation:  Repair minor cracks, surface irregularities, and open joints in masonry walls using a quick dry grout mix to ensure a smooth, even surface for application of the roofing/flashing membranes.

E.	Existing Curbs:  Raise all existing curbs to accommodate a new minimum height of 8 inches.

3.03  SUBSTRATE REQUIREMENTS

A.	Preparation of Wood/Plywood Substrates to Receive Flashing Coverage:  Mechanically attach the gypsum sheathing panels to all wood/plywood substrates that will be covered with the specified flashing membrane, using the specified screws/plates, at 12 inches o.c. staggered.  Cut the cant backing sheet into 12 inch widths and peel the release film from the back of the sheet.  Set the sheet into place extending 6 inches onto the field of the roof area and 6 inches up the gypsum sheathing panel surface utilizing minimum 3 inch side laps.  Set the cant into place prior to installation of the roof membrane base ply.

B.	Roof Decks:  Structural roof decks should properly provide sufficient strength to support anticipated dead and live loads and normal construction traffic without excessive deflection or movement.  All openings, walls or projections through the roof deck should be completed before application of the roof membrane is begun.  The deck should be constructed and necessary deck repairs made according to the deck manufacturer's specifications following best established practices.

1.	Wood:  Wood decks should be constructed of dry, well-seasoned lumber of minimum 1 inch thickness, tongue and groove, shiplap or splined together at side joints and matched at end joints.  Boards should have a bearing on rafters at each end and be securely nailed.  Cracks wider than 1/4 inch and knot holes larger than 1 inch in diameter should be covered with sheet metal.

3.04  SUBSTRATE PREPARATION

A.	Perimeter Wood Nailers:  Install perimeter wood nailers in accordance with the guidelines set forth in latest edition of FM Global Property Loss Prevention Data Sheet 1-49.

B.	Insulation:  Install insulation panels with end joints offset; edges of the panels shall be in moderate contact without forcing applied in strict accordance with the insulation manufacturer's requirements and the following instructions.  Where insulation is installed in two or more layers, stagger joints between layers.  Maintain a maximum panel size of 4 feet by 4 feet for insulation applied in hot asphalt or insulation adhesive.

1.	Insulation - single layer:  Mechanically attach the insulation panels, using the specified fasteners, at a rate of 1 fastener for every 2 square feet of panel area (16 per 4' x 8' panel).  Increase the fastening frequency by 50% at the perimeter of the roof and 100% in the corners.

2.	Crickets:  Construct crickets of tapered insulation panels in a layout as indicated on the roof plan.

3.	Tapered Edge at Transitions:  Field-cut, shape and install tapered edge strip at transitions of 1/4 inch or greater between substrate components to provide a smooth transition and proper support for the subsequent insulation layer or membrane/flashing system components.

3.05  ROOF MEMBRANE INSTALLATION - GENERAL

A.	Membrane Application:  Apply roofing in accordance with roofing system manufacturer's instructions and the following requirements.  Application of roofing membrane components shall immediately follow application of base sheet and/or insulation as a continuous operation.

B.	Aesthetic Considerations:  An aesthetically pleasing overall appearance of the finished roof application is a standard requirement for this project.  Make necessary preparations, utilize recommended application techniques, apply the specified materials including granules and metallic powder, and exercise care in ensuring that the finished application is acceptable to the Owner.

C.	Priming:  Prime metal and concrete and masonry surfaces with a uniform coating of the specified asphalt primer.

D.	Kettles And Tankers:  Kettles and tankers shall be equipped with accurate, fully readable thermometers.  Do not heat asphalt to or above its flash point.  Avoid heating at or above the FBT, should conditions make this impractical, heating must be no more than 25ºF  below the EVT and no more than 25ºF above EVT.

E.	Asphalt Temperatures:  If the EVT information is not provided, the following asphalt temperature shall be observed.  Maximum heating temperature shall be 525ºF (274ºC).  Minimum application temperature shall be 400ºF (204ºC).

F.	Asphalt Moppings:  Ensure that all moppings do not exceed a maximum of 25 lb/sq.  Mopping shall be total in coverage, leaving no breaks or voids.

G.	Bitumen Consistency:  Cutting or alterations of bitumen, primer, and sealants will not be permitted.

H.	Roofing Application:  Apply all layers of roofing free of wrinkles, creases or fishmouths.  Exert sufficient pressure on the roll during application to ensure prevention of air pockets.

1.	Apply all layers of roofing perpendicular to the slope of the deck.

2.	Fully bond the base ply to the prepared substrate, utilizing minimum 3 inch side and end laps.  Apply each sheet directly behind the asphalt applicator.  Cut a dog ear angle at the end laps on overlapping selvage edges.  Using a clean trowel, apply top pressure to top seal T-laps immediately following sheet application.  Stagger end laps a minimum of 3 feet.

3.	Fully bond the finish ply to the base ply, utilizing minimum 3 inch side and end laps.  Apply each sheet directly behind the torch applicator.  Stagger end laps of the finish ply a minimum 3 feet.  Cut a dog ear angle at the end laps on overlapping selvage edges.  Using a clean trowel, apply top pressure to top seal T-laps immediately following sheet application.  Stagger side laps of the finish ply a minimum 12 inches from side laps in the underlying base ply.  Stagger end laps of the finish ply a minimum 3 feet from end laps in the underlying base ply.

4.	Maximum sheet lengths and special fastening of the specified roof membrane system may be required at various slope increments where the roof deck slope exceeds 1/2 inch per foot. The manufacturer shall provide acceptable sheet lengths and the required fastening schedule for all roofing sheet applications to applicable roof slopes.

J.	Granule Embedment:  Broadcast mineral granules over all bitumen overruns on the finish ply surface, while the bitumen is still hot or the adhesive is soft, to ensure a monolithic surface color.

K.	Flashing Application - masonry surfaces:  Flash masonry parapet walls and curbs using the reinforcing sheet and the metal foil flashing membrane.  After the base ply has been applied to the top of the cant, fully adhere the reinforcing sheet, utilizing minimum 3 inch side laps and extend a minimum of 3 inches onto the base ply surface and 3 inches up the parapet wall above the cant.  After the final roofing ply has been applied to the top of the cant, prepare the surface area that is to receive flashing coverage by torch heating granular surfaces or by application of asphalt primer; allowing primer to dry thoroughly.  Torch apply the metal foil-faced flashing into place using three foot widths (cut off the end of roll) always lapping the factory selvage edge.  Stagger the laps of the metal foil flashing layer from lap seams in the reinforcing layer.  Extend the flashing sheet a minimum of 4 inches beyond the toe of the cant onto the prepared surface of the finished roof and up the wall to the desired flashing height.  Exert pressure on the flashing sheet during application to ensure complete contact with the wall/roof surfaces, preventing air pockets; this can be accomplished by using a damp sponge or shop rag.  Check and seal all loose laps and edges.  Nail the top edge of the flashing on 9 inch centers.  (See manufacturer's schematic for visual interpretation).

L.	Flashing Application – surfaces sheathed with gypsum sheathing panels:  After the gypsum sheathing panel and cant backing sheet have been installed, flash parapet walls and curbs with the specified reinforcing sheet and the metal foil flashing membrane.  The reinforcing sheet shall have minimum 3 inch side laps and extend a minimum of 3 inches onto the base ply surface and to the top of the parapet wall or curb.  Using the specified fasteners, mechanically attach the reinforcing sheet through the field of the sheet to the vertical flashing surface on 12 inch centers from the top of the cant to the top of the wall or curb.  Fully adhere the remainder of the flashing reinforcing sheet that extends over the cant and roof level.  Using a Leister Hand Welding Tool, seal the laps between flashing reinforcing sheets.  After the final roofing ply has been applied to the top of the cant, prepare the surface area that is to receive flashing coverage by torch heating granular surfaces or by application of asphalt primer; allowing primer to dry thoroughly.  Torch apply the metal foil-faced flashing into place using three foot widths (cut off the end of roll) always lapping the factory selvage edge.  Stagger the laps of the metal foil flashing layer from lap seams in the reinforcing layer.  Extend the flashing sheet a minimum of 4 inches beyond the toe of the cant onto the prepared surface of the finished roof and up the wall to the desired flashing height.  Exert pressure on the flashing sheet during application to ensure complete contact with the wall/roof surfaces, preventing air pockets; this can be accomplished by using a damp sponge or shop rag.  Check and seal all loose laps and edges.  Nail the top edge of the flashing on 9 inch centers.  (See manufacturer's schematic for visual interpretation).

M.	Catalyzed Acrylic Resin Flashing System:  Install the liquid-applied primer and flashing system in accordance with the membrane system manufacturer’s printed installer’s guidelines and other applicable written recommendations as provided by the manufacturer.

N.	Use of Metallic Powder:  Broadcast metallic powder over all bitumen overruns on the metal foil membrane surface while the bitumen is still hot to ensure a monolithic surface color.

O.	Water Cut-Off:  At end of day's work, or when precipitation is imminent, construct a water cut-off at all open edges.  Cut-offs can be built using asphalt or plastic cement and roofing felts, constructed to withstand protracted periods of service.  Cut-offs must be completely removed prior to the resumption of roofing.

3.06  RELATED COMPONENTS - INSTALLATION

A.	Edge Metal:  Completely prime metal flanges and allow to dry prior to installation.  Turn the base ply down 2 inches past the roof edge and over the nailer.  After the base ply and continuous cleat (if applicable) have been installed, set the flange in mastic and stagger nail every 3 inches on center.  Strip-in the flange using the stripping-ply material, extending a minimum of 4 inches beyond the edge of the flange.  Terminate the finish ply at the gravel-stop rise of the edge metal.  SEE ITEM: SEALANT, for finish of this detail.

B.	Lead Pipe Flashings:  Completely prime the lead flanges and allow to dry prior to installation.  After the base ply has been applied, set the flange in mastic and strip-in the flange using the stripping-ply material, extending a minimum of 4 inches beyond the edge of the flange.  Terminate the finish ply at the flange-sleeve juncture of the pipe flashing.  SEE ITEM: SEALANT for finish of this detail.

C.	Lead Drain Flashings:  Completely prime the lead drain flashing and allow to dry prior to installation.  After the base ply has been applied, set the lead flashing sheet in mastic and form to turn down inside of the drain bowl.  Ply-in the perimeter of the lead flashing using an additional layer of the base ply material, overlapping the perimeter of the lead a minimum of 4 inches.  Terminate the finish ply to extend beneath the clamping ring seal.  Install the clamping ring with all bolts in place.

D.	Light Air Unit Supports:  Separate light air handling units that are supported by wood sleepers (not supported by a roof curb) from the new roof assembly using the manufacturer's walktread-roof protection material.  Cut each walktread pad to a size which extends a minimum of 2 inches beyond the perimeter of each sleeper block.  Set the walktread pad dry over the new assembly.  Set each sleeper block dry over the walktread pad.

E.	Small Pipe Supports:  Support all gas lines and conduits which are a maximum of 1 inch diameter and run horizontally over the roof membrane surface using wood blocking and the manufacturer's walktread - roof protection material.  The blocking shall be 4 inches by 4 inches by 12 inches in size.  Cut each walktread pad to a size which extends a minimum of 2 inches beyond the perimeter of the blocking.  Loosely secure the pipe to allow movement over the 6 inch center of each block; the spacing for the blocks shall be of adequate distance to prevent sagging of the pipe and to prevent the pipe from coming into contact with the new roof assembly.  Set the walktread dry over the new roof assembly.  Set each pipe support block dry over the walktread pad.

F.	Metal Pipe Flashings:  Completely prime the metal pipe flanges and allow to dry prior to installation.  After the base ply has been applied, set the flanges in mastic and strip-in the flange using the stripping-ply material, extending a minimum of 4 inches beyond the edge of the flange.  Terminate the finish ply at the flange-sleeve juncture of the pipe flashing.  Install a watertight umbrella to the penetration, completely covering the opening of the pipe flashing.  SEE ITEM: SEALANT for finish of this detail.

G.	Walktread:  Cut the walktread into maximum 5 foot lengths and allow to relax until flat.  Adhere the sheet using the specified plastic cement.  Apply the specified cement in a 3/8 inch thickness to the back of the product in 5 inch by 5 inch spots in accordance with the pattern as supplied by the walktread manufacturer.  Walk-in each sheet after application to ensure proper adhesion.  Use a minimum spacing of 2 inches between sheets to allow for proper drainage.

H.	Sealant:  Caulk all exposed finish ply edges at the transition to metal flashings incorporated into the roof system with a smooth continuous bead of the specified sealant.

3.07 SPECIAL CONDITIONS

A.	Site Condition:  Leave all areas around job site free of debris, roofing materials, equipment and related items after completion of job.

B.	Notification Of Completion:  Notify the manufacturer by means of manufacturer's printed Notification of Completion form of job completion in order to schedule a final inspection date.

C.	Final Inspection

1.	Post-Installation Meeting:  Hold a meeting at the completion of the project, attended by all parties that were present at the pre-job conference.  A punch list of items required for completion shall be compiled by the Contractor and the manufacturer's representative.  Complete, sign, and mail the punch list form to the manufacturer's headquarters.

2.	Drain Verification:  At final inspection of all work, verify that all drains and scuppers, are functioning properly.  Ensure that roof drains have adequate strainers.

3.	Air Handling Units:  Reconnect all ductwork, electrical and supply connections.  At final inspection, verify that all connections are restored to a complete working, watertight, and safe condition, following SMACNA standards.

D.	Issuance Of The Guarantee:  Complete all post installation procedures and meet the manufacturer's final endorsement for issuance of the specified guarantee.