COMMENTS OF THE

WILLIAMS GAS PIPELINE

NOTICE OF PROPOSED RULEMAKING

Pipeline Safety: Standards for Increasing the

Maximum Allowable Operating Pressure

For Gas Transmission Pipelines

Docket ID PHMSA-2005-23447; Notice 2

Docket No. RIN 2137-AE25

Pursuant to the proposed rulemaking notice (“Proposed Rule”) issued by the U.S. Department of Transportation (“DOT”) Pipeline and Hazardous Materials Safety Administrations (“PHMSA”) on March 12, 200, Federal Register Vol. 73, No. 49, 13167, Williams Gas Pipeline (“WGP”), 2800 Post Oak Boulevard, Houston, Texas 77056 submits the following comments on PHMSA’s proposal to amend the pipeline safety regulations to prescribe safety requirements for the operation of certain gas transmission pipeline at pressure based on higher stress levels.

Industry has been working with PHMSA on these criteria for 3 years. In addition, individual companies, through the special permit process have been working with PHMSA to set reasonable requirements. Some of the requirements set by PHMSA are not supported by any technical data or information. WGP therefore will be providing comments on those items.

Also during the special permit process, companies are inclined to agree with PHMSA requirements in order to get the permit as expeditiously as possible; costs of delays are not tenable. Therefore, companies have agreed to non-technically based requirements in order to get the permit. These issues will be addressed by WGP in the response for individual items.

GENERAL COMMENTS

Several operators have sought and/or been granted Special Permits to operate at higher stress levels. WGP is concerned that these Special Permits will be revoked and the requirements of the proposed rule implemented. This may cause an undo hardship on the companies that have invested significant resources to meet the requirements of the Special Permits. All Special Permits should be grandfathered. A company should, however be allowed to suspend operations under the Special Permit and instead follow the proposed regulations.

Many of the proposed requirements seem to ignore the requirements and criteria set forth in Subpart O and the referenced ASME B31.8S standard. These proposed requirements do not have a technical basis and there need is not explained where as the requirements in Subpart O and in ASME B31.8S are based on science and technical research. Where the elements of integrity management are required, it is recommended that reference to Subpart O be made instead of stating new, unjustified and conflicting requirements.

comments on the preamble

The preamble has a few errors that WGP wishes to point out so that the final rule will be correct. In addition, comments on some questions posed in the preamble are provided These changes and comments are as follows:

B.1	The phrase “but not to exceed 80% of MSYS” at the end of paragraph one is not correct. There is no upper limit to the pressure under which a grandfathered pipeline can operate.

B.6	Paragraph one, the review of existing permits, may be an appropriate action for PHMSA to take. PHMSA should not use this review to impose additional requirements on those operators which Special Permits nor revoke any Special Permits already granted.

B.6	Paragraph two, PHMSA should continue to expeditiously process any Special Permits they receive regardless of the status of this proposed rulemaking. The operators who have submitted the Special Permits may need to increase pressure to meet customer demand before the rulemaking is complete. Additionally, operators may need relief from both existing regulations and the proposed regulations as drafted.

C.3	Paragraph two makes reference to “level 2 of API Specification 5L’. The new edition of this specification will likely be published before this rulemaking is complete. The reference, as stated will be outdated. PHMSA should review the proposed new edition of this specification and make appropriate references as part of the final rule.

C.3 	Paragraph eight requires certification of serviceability for fittings and other components. It is not known what this requirement means. PHMSA should clarify this requirement; does PHMSA mean that mill certificates are required for each component?

C.4	Paragraph four states that “industry practice has been to non-destructively test only a sample of girth welds”. WGP takes exception to this statement. Although this represents the regulatory requirement, industry practice, including WGP is to non-destructively test nearly all girth welds.

C.4 	Paragraph six states that “since the initial strength test is a destructive test, it only detects flaws relatively close to failure during operation. This could leave in place smaller flaws that could grow more rapidly at higher stress levels. WGP takes exception to this statement. The pressure test eliminates all flaws that may fail significantly above operating pressure and to the level of the strength test (1.25 times MAOP or greater). Any flaws left in place will not grow more rapidly at higher stress levels and there is nothing that will cause them to grow. PHSMA should review research on pressure testing to more accurately state the how flaws are manifested and grow and how pressure testing minimizes the material and construction threats.

C.7.7	Paragraph one implies that geometry tools are run for baseline purposes and during periodic assessments. This is not a correct statement based on the proposed regulations. Geometry tools are required for the baseline assessment but not for periodic assessments. The language in the proposed rule is correct.

C.7.8	Paragraph one states that “The higher stress levels of operation can allow more rapid growth of materials”. This statement is not correct. The growth of anomalies is not depended on operating stress level.

D.2	Paragraph 4 has a statement that is not correct. “In the case of new pipelines, the ability to use an alternative MAOP will make it possible to transport more product”. This statement may be true for existing pipelines but new pipelines are designed for the required capacity as certificated regardless of operating stress level.

cOMMENTS ON pROPOSED Changes to paragraph 192.7– INCORPORATION BY REFERENCE

In general, WGP supports the use of consensus standards to provide the technical foundation for any regulatory actions; particularly those developed under the provisions established by the American National Standards Institute (ANSI). Specifically, WGP supports the incorporation of the standard, ASTM A 578/A579M-96 (re-approved 2001) “Standard Specification for Straight-Beam Ultrasonic Examination of Plain and Clad Steel Plates for Special Applications” for use in inspecting plate manufactured for pipe orders to be used for operation using the alternative design basis and life cycle management proposed by PHMSA.

COMMENTS ON PROPOSED PARAGRAPH 192.112

This new paragraph sets the eligibility requirements for a new or existing pipeline to operate at the alternative maximum allowable MAOP. WGP’s comments to the new language are as follows:

Paragraph (a) – General Standards for Steel Pipe

PHMSA proposes the use of a ratio of the diameter over the nominal wall thickness, referred to as D/t to address the threat of damage during construction and atypical loads and mechanical damage during operation of the pipeline. WGP believes that while consideration of the relationship between wall thickness relative to pipe diameter is important, there is no hard and fast threshold that applies under all circumstances. D/t limitations are particularly inappropriate for higher yield strength pipe. For pipe grades X-80 and above, the D/t ratios may exceed 100 to 1. Ovality and denting issues can be managed for these higher D/t pipelines, and for that matter any pipe under this regulation through the construction practices proposed by PHMSA in 192.328(a)(1),  Quality Assurance (during construction), and by provisions in the existing ASME code that relate to analyses of instantaneous and sustained loads during operation (ASME B31.8, Paragraph 833.4).

With respect to carbon equivalents, the consensus standard API 5L establishes specifications for maximum carbon equivalents using the Ito-Bessyo formula (Pcm formula) for varying grades and wall thicknesses of steel pipe. PHMSA has proposed limitations that differ from those in API 5L, without technical justification. WGP supports use of the limits as expressed in API 5L, absent any other information to justify differing limits.

Paragraph (b)  – Fracture Control

In general, WGP agrees with the approach proposed by PHMSA with respect to fracture control. It is critical that an operator’s plan considers and addresses initiation, propagation and arrest under the range of operating pressures and temperatures anticipated on the pipeline. In addition, it is important that the fracture control plan addresses the potential under-conservatism of conventional Charpy toughness equations for higher strength steels (grades X70 and above) and enriched gases. A White Paper “Fracture Control” has been developed by the Joint Industry Project on Alternative Design Basis and Life Cycle Management, and it supports WGP’s comments.

WGP agrees that the basis for arrest proposed by PHMSA is appropriate for new pipeline design. The basis selected by PHMSA in effect requires that approximately 58 percent of the pipe be arrest pipe. This basis is also appropriate for existing pipelines as well except under one design scenario; that is a scenario under which a crack arrest design is used. WGP proposes that PHMSA amend the regulatory language to allow an operator to alternatively apply a crack arrest design based on an engineering analysis including an analysis of consequence.

WGP recommends that the language under 192.112(b)(3) be changed to read “If it is not physically possible to achieve the pipeline toughness properties of paragraphs’ (b)(1) and (2) of this section, a crack arrest design must be developed and implemented or mechanical crack arrestors of proper design and spacing must be used to insure fracture arrest as described in (b)(2)(iii) of this section”.

Paragraph (c) – Plate/Coil Quality Control

In general WGP believes that the consensus standard API 5L provides the foundation for the materials specification and manufacturing of line pipe. Operators (purchasers of pipe) build upon API 5L through use of materials specification and manufacturing quality management programs. The Joint Industry Project on Alternative Design Basis and Life Cycle Management has developed a White Paper “Material Specification and Manufacturing” that describes how line pipe metallurgical, chemical and dimensional properties are managed by a materials and manufacturing quality management program. Materials and manufacturing quality management programs draw upon international consensus-based standards in combination with mill and source-specific specifications, quality control measures used by the pipe mill and quality assurance used by the purchaser. The quality management program comprises four steps:

- Pipe manufacturing mill qualification

- Pipe standard, specifications and contracting agreements

- Pipe manufacturing procedure specification review and agreement

- Surveillance and auditing

The purchaser engages in a technical evaluation of the mill to ensure that the mill is qualified to produce pipe to the purchaser’s specifications. The purchaser will establish a pipe specification knowing the requirements of the project for which the pipe is being procured. The mill and purchaser engage in the development and agreement upon a manufacturing procedure specification (MPS) that establishes the materials specification to standards and the purchaser’s additional requirements and manufacturing procedures and quality control/quality assurance (QA/QC) practices.  The mill knows best how to source the steel, roll and weld pipe to meet the performance parameters required by the purchaser.  The MPS sets out the kinds of inspections and frequencies and how exceptions are to be dealt with.  The MPS is designed to locate issues before they become problems and minimize exceptions.

Steel properties are specified by the operator in the pipe specification and the mill selects the chemical formulations that are designed to ensure the slab mill producer, skelp mill and the pipe mill achieve the desired final properties in the finished pipes. Most alloying elements must fall within compositional limits that are known to lead to the appropriate mechanical properties.  Solidification control during continuous casting minimizes centerline segregation and lamination from refractory and slag entrapment.

Centerline segregation and lamination in the pipe body or pipe ends if it extends into the weld preparation generally reduces weld strength and may promote girth weld cracking.  In particular, carbon, oxygen, sulfur and phosphorous in the carbon equivalents formulation are minimized controlled to promote weldability, and the controlled rolling (and accelerated cooling/strip coiling where applicable) using advanced thermo-mechanical parameters, and micro-alloying elements are used to assure the fine grain size and precipitation hardening effects which compensates for the loss of strength, due to the reduced carbon.

It is important to recognize that API 5L provides performance-based requirements to address the outcomes of centerline segregation, or failure of the source material to meet the metallurgical and dimensional properties of the operator’s pipe specification and API 5L. The operator, the pipe mill and source mill must balance the use of quality control measures and the potential for out-of-spec pipe to be formed. This is not best achieved by the imposition of a single simple prescriptive approach unrelated to the negotiated MPS.  Delays always lead to increase cost, and these will occur by improperly imposing production constraints.

Even considering the performance-based requirements set forth in API 5L, WGP recommends that the purchaser require specific slab mill inspections, such as macro-etch testing. Macro-etch testing is a valuable quality control method to be applied by the mill. This approach aligns with the approach proposed by PHMSA. While WGP agrees with PHMSA in the value of the tests, the frequency and acceptance criteria are best left to be agreed upon between the purchaser and the mill, based on mill configuration, slab source materials among others.

WGP recommends that the language under 192.112(c)(2)(i)) be changed to read “A macro etch test or other equivalent method to identify inclusions that may form centerline segregation during the continuous casting process. The acceptance criteria must be agreed to between the purchase and the mill”.

With respect to ultrasonic inspection of plate/coil or pipe, WGP agrees that the pipe mill must include a comprehensive plate/coil and pipe mill inspection program to check for surface defects and inclusions that can be injurious to the integrity of the pipe.  This program can be conducted on plate or rolled pipe (body and all ends) ultrasonic testing (UT) inspection program using as a basis, guidelines in ASTM A578 to check for imperfections such as laminations. Alternatively, WGP believes that the pipe mill may conduct full-body UT of the pipe. Full-body UT entails the use of a single transducer oscillating back and forth across the internal pipe surface. The basis of either approach is to assure that the inspection finds defects that exceed a certain minimum size in the body of the plate or pipe, and provides coverage for 100 percent of the pipe ends back a specified length. The work group recommends that the performance criteria set forth in ASTM 578 be used for plate inspection and as a basis for establishing criteria for full-body UT.

Paragraph (d) – Seam Quality Control

As a starting point, WGP believes that API 5L provides the technical foundation for managing seam quality control. The pipe weld seam must meet the minimum requirements for tensile strength as specified in API 5L for the appropriate pipe grade properties. WGP is aware of the work being undertaken by the Joint Industry Project on Alternative Design Basis and Life Cycle Management. The JIP has developed a white paper on Materials Specification and Manufacturing and it supports WGP’s comments.

WGP agrees with PHMSA that pipe weld seam hardness test using the Vickers hardness testing of a cross-section from the weld seam confirms adequate ductility across the plate, HAZ, and weld material volumes and must be performed on one length of pipe from each heat. WGP does not agree with the use of a threshold value of 280 Vickers Hardness (Hv 10). While API 5L does provide such a threshold value for sour gas service, it does not provide a single, fixed value for the gas service addressed under 49 CFR 192; that is the transportation of non-corrosive gases. WGP believes that the pipe mill and the purchaser should establish a hardness maximum in the manufacturing procedure specification and quality assurance plan.

API 5L requires that the pipe weld seam must be 100 percent UT or x-ray inspected to ensure there are no defects or cracks. In addition, API 5L requires that pipe ends be non-destructively inspected by either UT or x-ray, to identify there are injurious laminations or inclusions interacting the weld volume.

WGP recommends that the language under 192.112(d)(2) be changed to read “There must be a hardness test method used to ensure hardness levels established between the purchaser and the mill of the following:…”

Paragraph (e) – Mill Hydrostatic Test

WGP understands that the mill hydrostatic test is really a quality control test conducted on each pipe manufactured in the mill. It is an important quality control test but none-the-less it is a quality control test. The ultimate test of the pipe’s integrity is the eight-hour pressure test, often referred to as the proof test, conducted on the pipe as constructed in the field.

WGP is aware of the work being undertaken by the Joint Industry Project on Alternative Design Basis and Life Cycle Management. The JIP has developed a White Paper “Materials Specification and Manufacturing” and it supports WGP’s comments. The JIP work group examined hydrostatic testing practices in modern mills around the world and found that most operators specify a hydrostatic test of 95 percent of the specified minimum yield strength (SMYS) for a duration of 15 seconds. API 5L in the forty-third edition and for a number of years has specified a test to 90 percent of SMYS for 10 seconds. The members of the JIP work group discussed test pressure and duration and reached the following conclusions. Testing to 95 percent of SMYS is appropriate as long as the current provisions that allow for end-loading compensation as per Appendix K are applicable. In addition, the work group considered the additional 10 seconds proposed by PHMSA beyond the 10 seconds stipulated in API 5L is are also prudent. The work group found that a duration in excess of 10 seconds did not add value to the test. Consequently, the work group recommends,

WGP recommends that the language under 192.112(e)(1) be changed to read “A hydrostatic test of all pipe will be conducted in the pipe mill at a pressure of at least 95% of SMYS, for a duration of 10 seconds including the allowance for end loading”

Paragraph (f) - Coating

Fusion bonded epoxy coatings (FBE) have proven performance in pipeline applications for over thirty years around the world. WGP believes that it is important to allow for alternatives to ensure improved technologies are not arbitrarily restricted.  Three layer coatings especially FBE-PE and other hybrids have provided good performance in other parts of the world.  Performance coatings that have been shown as semi-conductive and/or do not crack would be preferred over this “one size fits all” statement.  Abrasion resistant coatings and other high integrity specialty coatings need inclusion through performance language such as non-disbonding, non-shielding, or non-cracking.  Prescriptive language remains inappropriate because it risks stifling innovation. Regulations should allow the use of manufacturer’s coating performances on petition.

WGP recommends that performance language be used to describe the expected coating performance rather than specify only FBE coatings. This language should be “the pipeline must be protected against external corrosion by non-disbonding, non-shielding, non-cracking coating”.

WGP agrees with the quality assurance approach proposed by PHMSA at 192.112(f)(3).

Paragraph (g) – Fittings and Flanges.

WGP agrees with the provisions proposed by PHMSA. But to clarify, pipe fittings, valves and flanges, associated with line pipe and main line block valves, should be designed and purchased in accordance with applicable reference standards or their equivalent, already incorporated within 49 CFR 192. The referenced standards may be supplemented by the operator’s supplemental requirements to ensure the materials meet the minimum engineering design specifications. In all cases, the valves and flanges should be ANSI Class 600 for pressures up to and including 1,480 psig, and ANSI 900 for pressures up to 2,200 psig. Valves should be manufactured in accordance with API 6D. High-test flanges should be manufactured in accordance with MSS SP-44 and normal flanges in accordance with ASME B16.5. Small pipe fittings should be manufactured in accordance with ASME B16.9 and large fittings with MSS SP-7. All of these materials should be pressure tested in accordance with the applicable standards.

Paragraph (h) – Compressor Stations

PHMSA concerns with respect to compressor station discharge temperatures relate to the long-term durability and integrity of plant and field applied fusion bond epoxy (FBE) coating for operations greater than 120oF. The concern arises when considering operating scenarios for uncontrolled compressor discharge temperatures projected to heat the downstream pipe to a temperature that may reach 150oF.

All pipelines built under PHMSA regulations must have two corrosion protection systems.  The first line of defense against corrosion is the coating system and the second line of defense is the applied cathodic protection current.  PHMSA in 49CFR192 requires a minimum test point (or close interval survey) voltage to ensure the imposed current provides sufficient protection in the event the coating has deteriorated.

The FBE concern arises out of historical experience in the pipeline industry when some pipeline systems were operated at temperatures above 120oF, even as high as 160oF.  In many cases these early coatings were non conductive and prevented the cathodic current from completing the circuit. The pipe was “shielded” and the applied potential could not protect the surface. Corrosion is prevented by applying small voltage potential.  These earlier reports refer to tar and asphalt based coatings that predominated prior to the use of FBE.

Early FBE coatings did not appear in the US until about the mid 1970’s.  Over time there was evidence that some pre-FBE coatings had degraded and eventually became blistered or disbonded from the pipe.  FBE however, remains conductive even when disbonded and raised proud of the pipe.  FBE coatings do not block the cathodic protection current, meaning that disbondment of the coating does not interrupt the cathodic protection system, and the imposed CP continues to protect the pipe from external corrosion and SCC.

Never the less, there remain two major concerns:

- absent a coated surface, the underlying steel can be prone to external corrosion and

- stress corrosion cracking (SCC) can occur under disbonded and non-conductive coatings.

It is known that the pipe shielded by disbonded non-conductive coating is susceptible to SCC and more so for any pipe that has experienced temperature excursions in excess of 120ºF.  The TCPL study (3), which had experience temperature excursions to 150ºF (65ºC), concluded that the disbondment of FBE coatings did not present an integrity threat to a pipeline as long as cathodic protection was present on the line.

NACE RP0394-2002, Standard for Application, Performance, and Quality Control of

Plant-Applied, Fusion-Bonded Epoxy External Pipe Coating, states in section 6.1.5 that a minimum coating thickness of 12 mils is required to meet the acceptance criteria for tests in the RP, including cathodic disbondment, for temperatures up to 150oF. Pipeline operators interpret this standardized practice to mean that FBE coatings, applied with a thickness of at least 12 mils, are appropriate for operating temperatures up to 150oF.  Since the FBE has been used in pipeline construction, the normal practice is to verify the thickness, and the integrity of the pipeline coating using a high voltage Jeeping inspection, as the line is lowered into the ditch.  Holidays are immediately repaired before backfilling the ditch.

The Joint Industry Project on Alternative Design Basis and Life Cycle Management has developed a White Paper “A Review of the Performance of Fusion-Bonded Epoxy Coatings on Pipelines at Operating Temperatures Above 120º F” is a review that summarizes operating and performance case histories, as well as laboratory and field-testing of the long-term performance of FBE coatings. This paper documents that FBE coatings have demonstrated good adhesion and little disbondment in both laboratory-testing environments and after 30 years of operation at temperatures greater than 120oF on systems in the United States, Canada and the Middle East.  In addition, FBE remains conductive even when disbonded as a continuous barrier like film proud of the pipe.  However, FBE coatings do not block the cathodic protection current, meaning that disbondment of the coating does not interrupt the cathodic protection system, and the imposed CP current continues to protect the pipe from external corrosion and SCC.

The work summarized in the JIP white paper shows that even the first generation FBE coatings having seen as many as thirty years service have performed well at temperatures above 120oF.  Even so, blistering and disbondment has been observed on in-service lines in operation above 120oF. Laboratory tests conducted on FBE coatings in simulated environments at temperatures above 120oF do indicate a greater degree of disbondment as the temperature is increased towards 200o F however any corrosion is minimized by the CP system.

FBE coating is known to be conductive, meaning that even when disbonded, cathodic protection remains effective. In-service experience described in this white paper confirms this behavior.  FBE coatings do not shield the cathodic protection currents.

It is not apparent that additional laboratory testing on FBE coating at temperatures above 120oF will add any information not already known based on the studies described in this white paper. An operator may elect to conduct additional laboratory testing.

Recognizing that there is the potential for disbondment, an operator may elect to conduct above ground surveys using close interval surveys to confirm the effectiveness of the applied potential and use direct current voltage gradient (DCVG) surveys periodically to locate holidays, if any, in the FBE coating.  The conductivity of FBE coatings ensures the integrity of the second line of protection, the applied CP system, is not compromised.

WGP recommends that the language under 192.112(h)(2) be changed to read “If research or testing shows that the coating will withstand …”

COMMENTS ON PROPOSED PARAGRAPH 192.328

Paragraph (a) – Quality Assurance

WGP agrees with these proposed requirements.

Paragraph (b) – Girth welds

Item (2) in this paragraph refers to pipelines that were constructed prior to the effective date of this rule. This requirement is in the wrong area of the regulations. Paragraph 328 is a construction requirement and is not a retro-active requirement. Paragraph 620 is an Operations requirement and applies retro-actively to all pipelines.

WGP recommend removing item (b)(2) from paragraph 192.328 and putting it in paragraph 192.620, under (c)(3) in a manner that is similar to the requirement for pressure testing.

Paragraph (c) – Depth of Cover

WGP agrees with these proposed requirements.

Paragraph (d) – Initial strength testing

In a paper by John Kiefner, “Role of Hydrostatic Testing in Pipeline Integrity Assessment” the technical benefits for the test is stated as follows:

“The purpose of hydrostatic testing a pipeline is to either eliminate any defect that might threaten its ability to sustain its maximum operating pressure or to show that none exists. A key work here is pressure. Hydrostatic testing consists of raising the pressure level above the operating pressure to see whether or not any defects with failure pressures above the operating pressure exist. If defects fail and are eliminated or if no failure occurs because no such defect exists, a safe margin of pressure above the operating pressure is demonstrated.”

This statement is the underlying philosophy for all pressure tests including the post construction test addressed in this paragraph. In the case of post construction tests, the defects that the operator is trying to find or prove do not exist are material and construction defects.

This item deals specifically with “any failures indicative of fault in material”. Material is produced as specified in the pipeline safety regulations and the additional requirements of proposed 192.112. Even with the rigorous controls, there is a possibility that a piece of pipe will have a material defect. This unacceptable pipe will be found during the pressure test if the defect is large enough to grow to failure. If it does not grow to failure, the safety margin is sustained.

Special permits granted to date have addressed pressure test failures by requiring a root cause failure analysis. If a systemic issue was found during the test, discussions had to be held with the regional offices. The requirement stated in the special permits is:

“Assessment of Test Failures:  Any pipe failure occurring during the pre-in service hydrostatic test must undergo a root cause failure analysis to include a metallurgical examination of the failed pipe. The results of this examination must preclude a systemic pipeline material issue and the results must be reported to PHMSA headquarters and the appropriate PHMSA regional office.”

The requirement as stated in the NPRM, by stating that “the segment must not experience any failure indicative of fault in material” during the hydrotest is excessive. A root cause analysis of any test failure however is appropriate. If there is a systemic issue with the material more needs to be done to understand and address the issue.

WGP recommends that the language under 192.328(d) be changed to what was used in the special permits, namely “Any pipe failure occurring during the pre-in service hydrostatic test must undergo a root cause failure analysis to include a metallurgical examination of the failed pipe. The results of this examination must preclude a systemic pipeline material issue and the results must be reported to PHMSA headquarters and the appropriate PHMSA regional office.”

Paragraph (e) – Cathodic Protection

This paragraph is not necessary. Existing paragraph 192.455 requires that cathodic protection must be installed and placed in operation within one year after the completion of construction.

WGP recommends removal of this paragraph. If necessary, a reference to 192.455 can be added in stead of restating the requirement.

Paragraph (f) – Interference currents

WGP agrees with these proposed requirements.

COMMENTS ON PROPOSED PARAGRAPH 192.620

Paragraph (a)

Stated requirements in the NPRM are more restrictive than current regulations and granted special permits. This inconsistency must be addressed in the NPRM.

The design factors set in the NPRM do not recognize that the class location may change after the pipeline has been constructed. Special provisions are provided in the existing regulations to allow for the class location change without the need for pipe replacement. This provision is contingent on a pressure test to the next class location test factor.

Waivers have been granted to pipelines operating to 80% or more of SMYS that were grandfathered and have subsequently experienced a class change from Class 1 to Class 2. In order obtain this waiver, companies agreed to in-line inspection of the pipeline and to employ additional preventative and mitigative measures such as those that are mandated within a company’s Integrity Management Plan. Today, there are pipelines that have been granted waivers to operate at 80% or more of SMYS in Class 2 areas.

Waivers have been granted to pipelines operating at 60% or more of SMYS in Class 3 locations where the pressure test was not to the level required by the regulations (1.5 times MAOP). Waivers have been granted to pipelines operating at 72% or more of SMYS of design pressure in Class 3 locations, where neither the design nor the pressure test met the requirements of the regulations. The companies in these cases also agreed to in-line inspection of the pipeline and operations in accordance with the companies Integrity Management Plan. The granting of these waivers was part of the agreement reached between PHMSA and the industry in 2002 as part of the promulgation of the integrity management regulations in order to help justify the extreme cost of the regulations. Many of these pipelines contain HCA’s.

There are significant inconsistencies between current regulations, current waivers granted to existing pipelines, and the proposed regulations. While changes to existing regulations is not part of the scope of the NPRM, there is no reason to confuse the issue again with this rule, it should be made simpler and more in line with current waivers.

The proposed regulations do not have a provision for compressor station, meter station, road crossings or fabricated assemblies to operate at higher pressures. As written, a compressor station in a Class 1 area can be operated at 80% of SMYS.

WGP recommends the following changes to proposed Paragraph 192.620(a):

For the new pipelines that meet all of the special provisions in the NPRM, it is recommend that:

- Class 1 pipelines be limited to operation at 80% of SMYS and pressure tested to 1.25 times MAOP

- Class 2 pipelines be limited to operation at 67% of SMYS and pressure tested to 1.25 times MAOP

- Class 3 pipelines be limited to operation at 56% of SMYS and pressure tested to 1.5 times MAOP

- Station piping  be limited to operation at 56% of SMYS and  pressure tested to 1.5 times MAOP

- Fabricated assemblies would be limited to operation at 67% of SMY and pressure  tested to 1.25 times MAOP

- Uncased road and railroad crossing be limited to 67 % of SMYS in Class 1 locations and to 56% of SMYS in Class 2 locations.

For Class location changes, it is recommended that a new paragraph be added to 192.611 to provide the following:

- Pipe that  operates at 80% and in accordance with paragraph 192.620 and changes from Class 1 to Class 2,  can continue to operate up to 80% SMYS

- Pipe that operates at 80% and changes from Class 2 to Class 3 or from Class 1 to Class 3 would need to have the pressure lowered to 67% of SMYS or be replaced with pipe designed at 67% SMYS or less

- Pipe that operates at 67% and in accordance with paragraph 192.620 and changes from Class 2 to Class 3 can continue to operate at 67%

These class change provisions are necessary or operators will be asking for special permits in the very near future as population encroachment drives the class location to change from Class 1 to Class 2 or from Class 2 to Class 3. These criteria also provides for consistency with Special Permits previously granted and gives the operator flexibility in design for all pipeline facilities

It is important to note that the regulations require operations and maintenance activity frequency be based on the class location. The higher the class location, the more frequent the inspection or other activity is performed. These provisions address the slightly higher risk due to consequence by reducing the likelihood of an event through more frequent inspection.

A White Paper “Alternative Pipeline Design Pressures” has been developed on this topic. It discusses the current regulations, the special permits granted for performing Integrity Management in lieu of replacing pipe and the proposed regulations.

Paragraph (b)

Item (6)

The NPRM states that the segment must not experience any failures during normal operations indicative of fault in material. This requirement is excessive as the failure may be a single event. If there is a failure, a root cause analysis should be conducted in order to ascertain that the failure is not indicative of a systemic materials issue. If there is a systemic issue with the material more needs to be done to understand and address the issue.

WGP recommends that the language under 192.620(b)(6) be changed to read “Any pipe failure occurring during normal operations  must undergo a root cause failure analysis to include a metallurgical examination of the failed pipe. The results of this examination must preclude a systemic pipeline material issue and the results must be reported to PHMSA headquarters and the appropriate PHMSA regional office.”

Paragraph (c)

Item (3)

This item shows the criteria for pressure testing in Class 1 areas but does not say anything about Class 2 or 3 areas. For pipelines that are presently in operation and are being up-rated to the higher pressures, the pressure test requirements should not be the same as required in paragraph (a) of this section.

For existing pipelines, pressure test levels may not have been to the levels stated in paragraph (a) of this section; however the tests may have been very near those levels. Some relief from this requirement should be allowed. In 192.328(b)(2) the requirement for weld NDE is somewhat reduced recognizing that every weld may have not have experienced NDE. This rationale should apply to pressure tests as well in order to gain some relief from the pressure test requirements.

In a paper written for Alliance Pipeline, and contained in the docket for their waiver or special permit for increasing operating pressure, Kiefner and Associates concluded “there would be little additional benefit gained in terms of demonstrating that the pipeline is fit for the modest proposed increase in operating stress by repeating the hydrostatic test to the incrementally higher level necessary to meet the 1.25 factor”. The paper states the reason for these conclusions and included that more than ¾ of all joints were tested to 95% of SMYS, more than ½ of all joints were tested to 97% SMYS or greater and more than 1/3 of all the joints were tested to 99% of SMYS. In addition, the conclusions were justified by pipe manufacturing controls, resistance to mechanical damage, the decay of pressure with distance downstream of compression, and the minimal difference in safety factor as compared to current regulations.

WGP recommends that Item 3 of Paragraph C be changed to the following:

(i) Perform a strength test as described in 192.505 to at least the factor stated in (a) of this section times the maximum allowable operating pressure: or

(ii) For a segment in existence prior to the effective date of this regulations, and the pressure test levels do note meet the requirements of 192.620(a)(ii) of this paragraph, certify, under paragraph (c)(1) of this section, that a  strength test was conducted and provide an engineering critical analysis discussing the relationship of the pressure test to actual operating pressure and the affects of remaining defect size, pipe toughness, fracture control properties and fatigue on the pipeline ”.

Paragraph (d)

Item (1) – Assessing threats:

The way in which item 1 is written implies that operation at the higher stress levels increases the risk and that the procedures used will mitigate the risk. The slight increase in risk however is already mitigated through all of the additional design, materials, construction, and operations requirements of these proposed regulations. It is unclear what procedures are being talked about.

WGP recommends that this item be clarified to state that the operator must include in their design, construction, material, operations, and maintenance procedures and specifications, provisions to mitigate risk for operation at the higher design pressures.

Item (2) – Notifying the public:

This item appears to require a special notification to the public near pipelines that will be operating at higher pressures. The justification for this requirement has not been provided other than to state the information is necessary to people potentially impacted by a failure. Everyone along the pipeline could be affected by a failure. Notification about pipelines is already required by 192.616 “Public awareness”.

WGP recommends item (d)(2) be revised to change the title of the section to “Assessing potential impact area”. In addition, delete item (d)(2)(ii) in its entirety.

Item (3) – Responding to an emergency in an area defined as a high consequence area:

This item states the requirements for timing of valve closure in an HCA. WGP is not aware of any study or research that supports this requirement. The requirement seems arbitrary and is contrary to research and operational experience.

Especially onerous is the requirement for additional pressure monitoring upstream and downstream of the valve. WGP is not aware of any benefit in monitoring the pipeline pressure upstream and downstream of the valve. Pressure monitoring requires additional equipment and the resultant maintenance where the benefit is not known and has not been justified. Given a rupture of the pipeline, the pressure will read zero after the valves are closed upstream and downstream of the rupture site. Upstream of the first closed valve the pressure will equalize to the upstream compressor station discharge pressure. Downstream of the second closed valve the pressure will equalize to the downstream compressor station suction pressure. There is no need for pressure monitoring.

In addition, the requirement to be able to remotely open the valve is contrary to many companies operations policies. Many operators believe that if the situation is so serious that remote closure of the valve is required, on-site personnel should make the determination that the area is safe prior to re-pressurizing the segment and therefore do not allow remote opening of the valve.

WGP recommends that 192.620(d)(3)(iii) be changed to read “Remote valve control must include the ability to close the valve and monitor the position (open and close) of the valve”.

Item (4) - Patrolling

The patrolling frequency proposed in the NPRM is excessive. WGP is not aware of any technical justification for the proposed frequency however it does recognize that it follows the frequency mandated for hazardous liquid pipelines.

A review of the incident data for both gas and hazardous liquid transmission lines does not show any benefit from the increased patrolling frequency for hazardous liquid lines. In 2007 there were 466 hazardous liquid incidents reported for the approximately 160,000 miles of pipeline. Of these there were 26 due to third party damage. For gas pipelines there were 127 incident reports for the approximately 300,000 of pipeline. Of these 14 were due to third party damage. There were approximately 3.7 times more incidents reported for hazardous liquid pipelines for a population equal to 53% of the gas pipeline mileage. Taking these factors into account, the number of incidents for pipelines patrolled 26 times per year is the same as for those patrolled twice per year (twice per year is an average required number of patrols based on one per year for Class 1, two per year for Class 2 and four per year for Class 3). This comparison is arrived by taking 26 third party incidents for gas pipelines divided by (3.7 * .53) which equals 13, the expected number for gas incidents. This compares to the 14 actual incidents.

A report by CFER Technologies for PRCI shows that unless patrolling is done at least daily, there is not much chance of prevention for outside force damage. In addition, B31.8 only requires once per year in Class 1 and 2 even when Class 1 pipe can operate at 80%.

WGP recommends changing the patrolling requirements to four times per year Class 1, six times per year in Class 2 and twelve times per year in Class 3.

This increase in frequency is akin to the frequency for the next higher class location as are other of the additional requirements in the NPRM. For example, the requirement in the NPRM for NDE to 100% of all girth welds in Class 1 areas operating at 80% of SMYS is the same as required in Class 3 areas in the existing regulations.

Depth of Cover

The language used in the NPRM for maintaining depth of cover is confusing. The first sentence says to maintain depth of cover to the requirements stated in 192.327 or 192.328. The second sentence says that if observed conditions indicate the possible loss of cover, perform a depth of cover survey and replace cover as necessary. The first sentence statement requiring that cover be maintained is a requirement that can not be obtained in any practical sense. The second sentence statement is more in line with a performance requirement that can be obtained and is event driven.

Based on studies of incidents where depth of cover was recorded, it was found that there is no correlation between depth of cover and third party damage. There are situations where the removal of cover may pose a threat of damage to the pipeline due to third party activities such as in agricultural situations. In these cases the restoration of cover may be appropriate.

There may be situations where cover can not be permanently restored. In these situations there may be more appropriate measures that can be employed, such as the addition of a barrier or some other prevention or mitigation measure.

For existing pipelines that were installed in accordance with 192.327, the depth of cover requirements in a Class 1 area was 30 inches. Some removal of cover may have occurred during the life of the pipeline do to agriculture, normal soil erosion or other factors. This paragraph, as written would require the operator to maintain cover to 30 inches for existing pipelines which may result in significant environmental disturbance to replace cover over long segments of pipeline.

WGP recommends changing the language to eliminate the first sentence so that it reads “If observed conditions indicate the possible loss of cover in an area where damage to the pipeline may result due to the loss of cover, replace the cover or provide appropriate prevention and mitigation measures as necessary”.

Damage Prevention

The requirement to review the damage prevention program in light of consensus standards and practices and employ the appropriate practices into the damage prevention program seems appropriate. The language in this requirement may lead to many interpretations by the companies and by inspection personnel due to its ambiguity. The requirement, as stated, does not identify the standards or practices to be reviewed, however it may be assumed that the CGA best practices are what are being referred to in this requirement. An operator may chose to follow one standard or practice; however inspection personnel may believe the operator should follow another. Another issue during inspections may be the determination of which items in a standard or practice should be followed by the operator.

WGP recommend changing the requirement so it reads “Review of CGA best practices and incorporation of the applicable practices into the operator’s damage prevention program”

Right-of-Way Plan

The requirement to develop and implement a right-of-way plan is duplicative of an operator’s damage prevention program and other requirements in the regulations. This additional program is not necessary or justified. The intent as stated is to protect the segment from damage due to excavation damage and this requirement is the same as required in a operator’s damage prevention programs as stated in 192.614. Paragraph (a) of this section states “… each operator of a buried pipeline must carry out, in accordance with this section, a written program to prevent damage to that pipeline from excavation damage…”.

The other conditions required by the proposed plan are already covered in 192.613 “Continuing surveillance”, 192.705 “Transmission Lines: Patrolling”, 192.706 “Transmission Lines: Leakage surveys”. These items are addressed in an operator’s manual of operations and maintenance procedures as required by 192.605 “Procedural manual for operations, maintenance, and emergency response”.

WGP recommends removing 192.620(d)(4)(ii) and 192.620(d)(4)(vi) from the proposed regulations.

Item (5) – Controlling internal corrosion:

This proposed regulation is somewhat duplicative yet in conflict with the new regulation at 192.476 “Internal corrosion control: Design and construction of transmission line”. The new regulation provides specific requirements for new pipelines for the control of internal corrosion. The new regulation also has a provision for “change to existing transmission line” which would apply to any pipeline that is presently in operation and would be up-rated based on the NPRM. With conflicting regulations, the operator may not be able to meet both requirements.

This proposed regulation also sets limits on gas quality. These limits may be in conflict with gas quality requirements set by FERC in an operator’s tariff. In addition, there is no justification in the NPRM for the limits set.

The proposed regulation requires the use of cleaning pigs and inhibitors and sampling of accumulated liquids. This requirement is required regardless of the gas quality, whether or not there is liquid water and whether or not there are other prevention and mitigation options available to the operator. The language used in 192.476 is better stated and covers all the same issues without the need to mandate work that may not be needed.

In response to the new regulations at 192.476, INGAA companies, including WGP developed guidelines in order to assist pipeline operators in determining the requirements of this regulation. These guidelines “Internal Corrosion Control: Design and Construction of Transmission Line” should be used in developing regulations for internal corrosion control measures. In addition, a White Paper, “Management of Time Dependent Threats” has been developed which discusses the concerns and remediation of gas quality issues.

WGP recommends revising 192.620(d(5) to read “develop and implement a program to monitor gas quality to prevent internal corrosion and to remediate any gas quality excursions where internal corrosion may result”

Item (6) – Controlling interference that can impact external corrosion:

WGP agrees with the proposed requirements.

Item (7) – Confirming external corrosion control through direct assessment:

The requirements in the NPRM and existing regulations provide several layers of protection for corrosion control. There are specific and comprehensive requirements for coating application at both the mill and in the field. There are coating continuity checks after the coating is applied and again before the pipe is lowered into the ditch and backfilled. Cathodic protection test stations are installed during construction. A geometry tool is run after construction which checks for pipe and ultimately coating damage that may have been caused during construction. Interference surveys are conducted within 6 months of placing the pipeline in operation. Cathodic protection is added within one year of placing the pipeline in operation. A close interval survey is conducted within six months of placing the cathodic protection in service. An in-line inspection with an MFL tools is performed within three years of placing the pipeline in service.

The proposed rule requires operators to “assess the integrity of the coating and adequacy of the cathodic protection through an indirect method such as close-interval survey, direct current voltage gradient or alternating current voltage gradient”. Close-interval surveys are used to confirm the adequacy of cathodic protection. Voltage gradient surveys are used to determine coating defects. Neither tool can meet both requirements. This implies that two separate surveys are required.

This proposed requirement also states that remediation of the coating must be performed based on NACE RP-0502 for any indication that is severe or moderate. This requirement is in conflict with the NACE standard which determines severe or moderate based on two or more above ground methods, not one.

The proposed regulation therefore implies that Direct Assessment must be conducted on the pipeline after construction and installation of the cathodic protection systems. These requirements together are excessive and not necessary. These requirements are in addition to a pressure test and in-line inspection with an MFL tool. This means that the pipeline must be assessed using all three tools identified in Subpart O of the pipeline safety regulations.

The close interval survey may be appropriate in order to confirm that the cathodic protection system is operating as designed. The coating survey is not necessary; any coating anomaly is protected from corrosion by the cathodic protection system. In addition the requirement to base and respond to results based on the NACE ECDA standard is not necessary.

The requirement to perform the close interval survey within 6 months is excessive and in many cases not possible. CIS is not performed in winter months in cold climates and the time between completion of construction in the fall and CIS in the summer will exceed six months.

A White Paper “Management of Time Dependent Threats” has been developed and discusses the requirements and needs for corrosion control activities.

WGP recommends revising 192.620(d)(7)(i) to read “ Within one year of placing the cathodic protection of a new segment in operations or within one year after recalculating the maximum allowable operating pressure of an existing segment under this section, perform a close-interval survey to determine the adequacy of the cathodic protection system”

WGP recommends revising 192.620(d)(7)(ii) to read “Remediate the coating or insure cathodic protection levels are appropriate to mitigate corrosion”

This new requirement states that results of the above ground assessment results must be integrated with the ILI results within 6 months for performing the ILI. This timing is burdensome and not necessary. The value of this data integration is not explained or justified.

WGP recommend revising 192.620(d)(7)(iii) to read “Within one year…”.

This new requirement states that test stations be installed at half-mile intervals in HCA’s and that at least one station is in each HCA (see item B). In addition, this item does not seem to fit under the topic of periodic assessments. This item may better fit under 192.328(e) as a construction requirement. In addition location of a test station within the HCA may not be practical. For example a pipeline that is physically 600 feet from a church and in a farm field, but the church makes it an HCA; it is not practical to place the test station in the HCA which is in the farm field. The need for the ½ mile spacing is not justified and is contrary to consensus standards.

WGP recommends that this item should be moved to 192.328(e) and that it could be clearer if it states that “no location in an HCA can be further than one mile from a cathodic protection test station”.

This new requirement states that there must be periodic close interval surveys of the pipelines in HCA’s and that they are performed in association with subpart O. This statement is not clear. Subpart O addresses integrity management and allows the use of one of three assessment techniques. Item 10 of this paragraph requires periodic in-line inspections at a frequency determined by the operator. This item implies that CIS is required at different intervals that the ILI interval. The need for close interval surveys is not justified or explained in the NPRM.

WGP recommends deletion of 192.620(d)(7)(iv) in its entirety once item (d)(7)(iv)(B) is moved to paragraph 192.328(e).

Item (8) – Controlling external corrosion through cathodic protection:

This item states requirements for what is required if a test point reading falls below criteria. Since the test stations are required in or near HCA’s and are rather closely spaced, and with specific requirements on what do if the readings fall below criteria, the need for CIS is not justified.

This proposed requirement states that remediation must be completed within 6-months. This requirement is excessive and not justified. Based on the seasons and associated land use issues as well as the time it takes to obtain permits, a one-year timeframe is more appropriate.

WGP recommends changing 192.620(d)(8)(i) to read “… within one year…”.

This item requires a CIS after remediation for a CP issue. This requirement is excessive and not justified. The reason for a failed reading may not require CIS to confirm restoration of CP. Example include loss of power, a cable cut, a short, etc. all of which can be fixed and have no baring on the effectiveness of the CP on the segment. The operator does need to confirm that the remedial action was appropriate and effective, however CIS in not always necessary or may be inappropriate.

WGP recommends changing 192.620(d)(8)(ii) to read “After remedial action to address the loss of CP, the operator must confirm that the remedial action did restore the CP system to criteria as identified in 192 subpart I”.

Item (9) – Conducting a baseline assessment of integrity:

This item requires the use of DA for segments that are not piggable. These segments may be designed per 192.111 and therefore would not be required to follow the requirements of 192.620. In addition, DA may not be appropriate for periodic assessments at these locations. Previous waivers have allowed operators to develop a corrosion control plan that does not require DA but is entirely appropriate for the subject segments.

Pressure testing is also an alternative to DA where ILI can not be performed and should be considered as an option as well

WGP recommends changing 192.620(d)(9)(iii) to read “…use either DA or pressure testing  to assess that segment or develop and implement a corrosion control plan to address corrosion of  the segment”.

Item 10 – Conducting periodic assessments of integrity:

WGP agrees with the proposed requirements.

Item (11) – Making repairs:

Item 11(i) requires the use of the most conservative calculation for determing remaining strength. This statement seems to imply that more than one calculation must be performed. Each calculation method results in slightly different answers with none being more accurate than the other. This requirement is excessive and has not been justified.

The idea of tool tolerance is addressed in the Protocols used by PHMSA for expectations of an operator’s integrity management program. If Subpart O is referenced in lieu of this proposed requirement, there is no need for this requirement.

Item 11(ii) in general, proposes that immediate repair conditions must be replaced based on the criteria set forth. These proposed requirements are extremely conservative and in many cases are not achievable. These criteria are not consistent with Subpart O requirements and have not been technically justified. These issues have been addressed in a White Paper “Safety Factors for Assessing Pipeline Anomalies” (attached) which states that the requirements outlined in ASME B31.8S and incorporated into Subpart O of part 192 are appropriate for pipelines operating up to 80% of SMYS.

Item 11(ii)(A) sets dent criteria to that required for new pipelines even if the pipeline is already in operation. For existing pipelines, this is not a readily achievable requirement and is not technically justified. The requirements under 192.933(d) are the appropriate criteria to apply to existing pipelines

Item 11(iii) in general proposes that one year repair conditions must be replaced based on the criteria set forth. These proposed requirements are extremely conservative and in many cases are not achievable. These criteria are not consistent with Subpart O requirements and have not been technically justified. Again, these issues have been addressed in the White Paper “Safety Factors for Assessing Pipeline Anomalies”.

Early Special Permits required that any anomaly with a predicted failure pressure to MAOP ratio of 1.1 or less was an immediate repair condition. A one year condition was an anomaly with a predicted failure pressure to MAOP ratio of 1.25 or less. Later Special Permits tightened these already conservative requirements by adding wall loss factors so that an immediate repair condition also included any wall loss of 60% or more and a one year condition included any wall loss of 40% or more. These additional factors are not technically justified and add much more conservatism than is necessary.

Item 11(iv) is not clear. The terminology is not consistent with Subpart O requirements in the regulations or ASME b31.8S. If an indication from an ILI or DA assessment does not require an examination or evaluation, it is not determined to be a defect. Based on the assessment information, the indications not remediated are classified and used to determine the next integrity assessment. This paragraph seems to repeat the requirements of 10(i) of this paragraph yet they terminology or intent seems to conflict. Paragraph 10(i) is the appropriate language to use to require subsequent inspections and references Subpart O where the requirements are more clearly stated.

WGP would prefer that paragraph 192.620(d)(11) as written be deleted in its entirety and replacing it with the statement “examination, evaluation and remediation of any indication or anomaly must be in accordance with Subpart O of this part”. However some recognition for more conservative repair criteria may be justified for pipelines operating at the higher pressure levels.

WGP recommends modification of 192.620(d)11) to read as follows:

(i) Do the following when evaluating an anomaly:

(A) Use a method for determining remaining strength of a corroded pipeline that is appropriate for the pipe being evaluated

(B) Take into account the tolerance of the tools used for the assessment

(ii) Repair a defect immediately if any of the following apply:

(A) For new pipelines, a dent discovered during the baseline assessment under (d)(9) of this section and the defect meets the criteria in 192.309(b). For existing pipelines, a dent discovered during the baseline assessment under (d)(9) of this section and the defect meets the criteria in 192.933(d).

(B) The defect meets the criteria for immediate repair condition in 192.933(d)(1)(iii)

(C) A corrosion defect with a predicted failure pressure to MAOP ratio of 1.1 or less; or with pitting depths of 80% or more.

(iii) If paragraph (d)(ii) of this section does not require an immediate repair, repair a defect within one year of any of the following:

(A) The defect meets the criteria for a one-year condition in 192.933(d)(2)

(B) A corrosion defect with a predicted failure pressure to MAOP ratio of 1.25 or less; or with pitting depths of 70% of more.

The criteria as it relates to the predicted failure pressure to MAOP ratio will address any issues of remaining strength of the pipeline. The pit depth criteria will address any issue with the potential for a corrosion leak. The 80% value for immediate repair conditions is consistent with the various methodologies for determining remaining strength of pipelines. Any corrosion with depths of 80% or more is outside the parameters of the methodologies and provides conservativeness. The 70% value for one-year repair conditions allows for extreme pitting corrosion over the one year period without exceeding the 80% methodology parameters.

Paragraph (e)

WGP agrees with the proposed requirements.

# Footnotes

Even the Forty-Fourth edition of API 5L, effective October 1, 2008 retains the 90% SMYS for at least 10 seconds for large diameter pipe.