# 7. Conventional Construction and Facilities Stages 1 & 2

## 7.1	Geology of the Fermilab Region

The many geologic studies for the Illinois proposal for the SSC [SSC-Illinois] demonstrated that the region around Fermilab provided an almost ideal medium, Galena-Platteville dolomite,  for constructing the main tunnel (87 km circumference) and experimental facilities.  The only less-than-ideal feature was the depth of construction (approximately 400 feet below the surface) to reach this dolomite layer.  A subsequent geotechnical study for the Next Linear Collider Project [NLC-NS] and generic site studies for future accelerator facilities at Fermilab[FCSS01-2] also reached the same conclusion.  However, due to its longer circumference (232 km), a VLHC might extend beyond the region of favorable geology.  There has been substantial experience in the Chicago area [TARP, NUMI] in tunneling and underground caverns in hard rock strata, such as Silurian dolomite, Maquoketa shale, and Galena-Platteville dolomite.  There is a lack of corresponding local similar experience, or even knowledge of the mechanical/structural engineering properties of the softer strata such as Glacial drift, the Ancell layer,  the Middle Confining unit, or the Franconia formation.  These may be respectively characterized as clay, sandstone, and two strata of dolomitic sandstones.  At Fermilab, the Ancell, Middle Confining, and Franconia layers lie below the Galena-Platteville dolomite.

There is a  general sloping of the till, Silurian, Maquoketa, Galena-Platteville, Ancell, … sequence of layers from the West (higher elevation above mean sea level) to the East (lower elevation) to Lake Michigan.  However, to the Northwest and West of Fermilab are located the Troy and Rock Bedrock Valleys, where the hard rock Silurian, Maquoketa, and Galena-Platteville layers have been completely cut away by glaciers and filled to the underlying sandstones with Glacial drift.  The Sandwich Fault Zone lies to the Southwest of Fermilab, passing through Sandwich, Illinois, and running roughly NW to SE.  This fault zone does end approximately SSE of Fermilab.  To the Southwest of the Sandwich Fault Zone, the underlying Ancell and Middle Confining layers are upthrust to meet the Glacial drift at the bedrock surface, and even the Franconia layer can impact tunnels traversing the fault zone.

If we restrict consideration to rings that would be contiguous to the existing Tevatron, only a VLHC ring with its center oriented to the North of Fermilab (North Ring) could be completely contained within the Galena-Platteville dolomite.  This ring would have a North-South strike axis passing through Fermilab with a tilt of approximately 0.2 % grade to stay within the dolomite.  This ring would be bounded by Lake Michigan and the Wisconsin border.  Any ring with its center oriented farther to the West (even NNW) would be impacted by the bedrock valleys  Possible rings oriented to the South or West would traverse the Sandwich fault into softer strata, less ideal for tunneling.

In order to undertake a tunnel costing and feasibility study for various orientations of a VLHC ring, two layouts and vertical strata lampshades were prepared.  The simplest configuration is a  tilted (0.2%) North Ring which stays completely (100%) in Galena-Platteville dolomite.  The second is  a flat North Ring which transitions between the following hard rock media:  Maquoketa shale (13%), Silurian dolomite (31%), Maquoketa shale (15%), Galena-Platteville dolomite (41%), and back into Maquoketa shale.  The third is a tilted South Ring, which crosses the Sandwich Fault (only once) into the sandstone Ancell aquifer and the dolomitic sandstone Middle Confining unit and possibly the Franconia formation.  The surface plans and the vertical strata lampshades for these rings are illustrated in Figures 7.1 – 7.5.

Another design constraint of this costing exercise deals with the positioning and depth of the caverns for the two experimental halls.  It is desirable to have these located at the Fermilab site to be able to cluster the long straight sections (for injection/abort and interaction regions) and to utilize the Fermilab campus for the related experiment fabrication and staging buildings,  support utilities, and equipment shaft facilities.  This also helps to minimize off-site surface land requirements.

Structural features and thickness of the strata supporting the spans of the experimental halls or caverns [SSC-Illinois-2] will determine the elevations at which the caverns can feasibly be sited.  This, of course, implies the elevation of the accelerator tunnel at the site of the cavern.  A general rule of thumb is that there should be a depth of hard rock (dolomite) strata above the cavern at least equal to the span of the cavern.  The previous study has concluded that for 75 foot high chambers, roof spans up to 125 feet are feasible using standard methods of  roof arching and rock supports.  This assumed that the orientation axis of the cavern bisects the major joint sets.  The joints run approximately NE-SW x NW-SE so this criteria would be satisfied by VLHC ring orientations to the North, South, or West.  Possible options in elevation for the experimental caverns are depicted in Figure 7.6.

As a working hypothesis for this study, a time scale of 5 years is assumed for completion of the underground construction, including main tunnel, special tunnels, and all caverns and enclosures.

Analogously to the 1997 study of  a 34 km VLHC booster tunnel with the Kenny Construction Company [TM-2048], we have entered into a tunnel costing exercise with (to be named) Company, to study the expected cost ranges and cost drivers of these three tunnel configurations listed above. By studying the three different tunnels,  we hope to learn the unit costs (per mile, per shaft, lined/unlined, etc.)  of a tunnel in an excellent media, that of a tunnel transitioning between three different hard rock media, and that of a tunnel which combines hard rock media, traversing the Sandwich Fault, and the softer sandstone and dolomitic sandstones beyond. This data will allow optimizations and tradeoffs with respect to siting costs.  It is anticipated that the final (to be named) report will be available in mid-May, 2001.

## 7.2	Collider tunnel and enclosures

Since the largest volume of the underground construction is the main collider tunnel, we will first concentrate on that component.  The tunnel is envisioned to be race-track shaped with circumference of  232 km as in Figure 7.7.   It consists of arcs of radius 35 km and 10 straight sections (total length 12 km) for injection, abort, RF cavities, Interaction Regions for experiments, and beam transfers between the Phase 1 and Phase 2 rings.  The ring will be adjacent to the Fermilab Tevatron which will serve as the injector to the Phase 1 (low field) ring.  The major straight sections will be clustered (5 each cluster) at Fermilab and at the side opposite.  Keeping many of these special tunnels, the abort/beam stops, and the experimental areas at Fermilab will optimize utilization of the existing infrastructure and minimize offsite underground construction and shafts.  The cluster opposite will contain only the Phase 1 to Phase 2 beam transfer (and possibly beam scrapers).  Much of these opposite side straight sections can be reserved for future needs.  The cluster of straight sections near Fermilab is illustrated in Figure 7.8.  Although one configuration for Tevatron injection is shown in this figure, the next section will discuss other possible options.

The main tunnel will have a finished inner clear diameter of 12 feet with 10 foot wide invert surface(Figure 7.9).  The four utility straights (injection and abort) will likely require additional transverse dimensions, possibly up to 20 feet x 20 feet square.  These can be finished by drill and blasting techniques after initial tunnel construction by tunnel boring machine technology.  Similarly, the short straight sections for RF-cavities may need widening (the SSC design had a 25 foot horseshoe shape).   Similarly, at the cryogenics utility turn-around points, mid-way between the cryogenic plant sites, an extra 5 foot wide x 100 foot long section would be required for cryogenics specialty devices.  These special tunnel configurations are illustrated in Figure 7.10.

It is anticipated that there be 6 major equipment access shafts distributed around the ring at the sites of the 6 cryogenics plants.  These will have 30 foot diameter bores, with a clear aperture of

6 foot x 30 foot for lowering high field dipoles for Phase 2.  Low field dipoles for Phase 1 will access the tunnel through the ramps to the surface.  The rest of the aperture of these shafts will be filled with equipment elevator, cryogenic, power, communications, and sump discharge utilities, plus an isolated emergency egress staircase.  In addition, there will be a 15 foot diameter clear access shaft (TR500 PS has 6 foot diagonal) for larger equipment such as magnet power supplies.  See Figure 7.10.   For emergency egress and tunnel ventilation, there will be approximately 60 shafts of 15 foot diameter separated by 2.7 miles maximum (the SSCL standard, see Sec. 7.8.).  Does this egress shaft have elevator?

Is the 30 foot x 6 foot  and 15 foot diameter adequate?  Do we need more eq access shafts?

In addition, at each of the 1710 half-cells, separated by 135.5 meters, there will be a 4 foot diameter x 6 foot deep cubby- hole for instrumentation and power supplies for the correction elements. The cubby-hole will be humidity controlled and isolated from the tunnel by a fire door.  A thermal conductor through the fire door will be convection cooled by the tunnel air flow.  The equipment contained in this cubby hole will be on rolling racks allowing access when extracted into the tunnel aisle.    Is this an egress/rescue hazard?  This is illustrated in Figure 7.11.

What about VACUUM?  TR500 PS?  Are they fire/smoke hazards? Protection?

Table 7.1  Five straight sections and intervening arcs at Fermilab (top to bottom in Fig.7.8)

Major arc		174 degrees bend – to/from far side cluster of straight sections

Utility Straight 		CW Phase 1 injection, CW-1 beam scraping, CCW-1 abort,

1.38 km		CCW-2  abort, with parallel kicker power supply cavern

20 foot x 20 foot square cross section

Bend Section		28.491 mrad bend @ 35 km radius

- km

IR Straight		experimental hall/cavern (100 meters)

1.64 km		     with equipment bypass tunnel (0.55 km @ 25 m bypass)

Bend Section		20.668 mrad bend @ 35 km radius

0.72 km

RF Straight		with parallel Klystron gallery

0.27 km		25 foot horseshoe cross section

Bend Section		20.668 mrad bend @ 35 km radius

0.72 km

IR Straight		experimental hall/cavern (100 meters)

1.64 km		     with equipment bypass tunnel (0.55 km @ 25 m bypass)

Bend Section		28.491 mrad bend @ 35 km radius

1.0 km

Utility Straight 		CCW Phase 1 injection, CCW-1 beam scraping, CW-1 abort,

1.38 km		CW-2  abort, with parallel kicker power supply cavern

20 foot x 20 foot square cross section

Major arc		174 degree bend – to/from far side cluster of straight sections

## 7.3	Injection line tunnels (various scenarios), beam abort lines, equipment access ramps, and Phase 2 low-field ring bypass.

Options for injecting from the Tevatron to the VLHC are discussed in Chapter 4.  The Tevatron Complex and Injector, and specifically in Chapter 4.3.  Tevatron Transfer Lines.  For whatever option is chosen, the Tevatron tunnel will have a new line(s) tangential which will then pitch downward to the elevation of the VLHC as in Figure 7.12.  The major slope of this injection tunnel is approximately 3.5 % grade which will be sufficiently flat to serve as part of the equipment access ramp(s).  There will be an incentive to cross the boundary between glacial drift and bedrock surface as steeply as possible to reduce both complexity of construction and ground water influx at the interface.  The less steeply sloped equipment access tunnel would continue to the surface.  The required tunnel lengths for the three options for injection from the Tevatron considered in Chapter 4 are listed in Table 7.2.

There also will be straight tunnels connected to the two near-Fermilab Utility Straight Sections.  These will be for the injection lines from the Tevatron to the Phase 1 low field ring, for the abort beam lines of both the Phase 1 and Phase 2 high field ring, and equipment access ramps to the surface.  Figure 7.11 illustrates the bi-polar operation and extraction from the Tevatron.  Table 7.2 also includes the length of arcs for uni-polar operation and extraction from the Tevatron.  Some of  lines for injection, abort, and equipment ramps could likely share some common tunnel sections.  However, the lines are now listed independently.  The interfaces between these tunnels have not yet been designed.  To facilitate construction and installation of a VLHC, it will be important to configure the equipment ramps to allow access while the Tevatron program is in operation.

It is planned to operate the Phase 1 VLHC with the low field, super-ferric magnet ring.  For Phase 2, a high field superconducting ring will be added.   The low field ring will serve as injector to the high field ring.  This beam transfer is anticipated to occur in the straight sections opposite Fermilab.  In order to reduce crowding and (possibly) to allow access to the experimental halls/caverns while the low field ring operates, the low-field ring will move to the inside of the main tunnel ring between, with extra and stronger bends to match its beam arc length to that of the high field ring through the main tunnel.  In the current model, stubs will be provided at the 28.4 mrad bend enclosures to allow later construction of this bypass tunnel for the low field ring in Phase 2.  A larger RF straight section (and another RF Klystron gallery) will be needed for this bypass, but not new experimental halls.  No such bypass is planned for the far-side cluster of straight sections

All of these special tunnel sections are anticipated to be of the same inner finished diameter as that of the main tunnel.

Table 7.2   Special Tunnel Sections (same finished diameter as main tunnel)

Function		Number	Length each	Comments

Access Ramps	2		3.5+ km		3.5 % grade to surface (741’ msl)

at Fermilab, (possibly 1 opposite)

Abort Lines	2		3.7 km		at tunnel level

to common abort/beam stop cavern

Injection Lines	2		3.5 km  		 bi-polar  to inboard end of Util. Str. Sec.

or	5.7 km   		uni-polar    @3.5 km radius of curvature

or 	3.7 km   		69 config

from Tevatron (722.3’ msl) to VLHC

Exp. Hall Bypass	2		0.55 km		radius = 2.0 km, offset = 25 meters

Low Field Ring Bypass	1		7.0 km		Phase 2 construction only

with enlarged RF straight section

and RF Klystron gallery

## 7.4	Accelerator utility caverns (includes special requirements for abort system) – shafts – Figure #

### 7.4.1	Beam Stop Enclosure (1)

A single beam stop enclosure will be located on the Fermilab site at the elevation of the main tunnel.  It will house the water cooled (need cooling specs and mechanical systems, where?) beam stop which will simultaneously service the four rings:  low-field CW, low-field CCW, high-field CW, and high-field CCW.  The beam stop enclosure is fed by standard diameter tunnels from the inboard ends of the two Utility Straight Sections at the Fermilab site.  By putting all four beam stops at the same location, this plan minimizes the number of places where high energy densities and high radiation fields are encountered, and does this on the existing Fermilab site.  The size of the beam stop enclosure will be 16 m x 16 m x 40 m (WxHxL).  It will have the necessary shielding and water impervious retention linings to prevent radioactive contamination of the bedrock or groundwater either by prompt or residual radiation or by coolant leakage.  A reservoir cavern (size) below the cavern elevation will prevent contamination of the tunnels due to leakage of beam stop coolant.  This reservoir cavern will allow monitoring of the radioactivity and other contamination levels before proper discharge.  There will be a 30 foot diameter equipment access shaft and a 15 foot diameter personnel access shaft at this enclosure site.

### 7.4.2	Klystron Tube Enclosure (1 + 1 in Phase 2) (SSC specs)

The Klystron Tube Gallery houses the RF driver tubes and power supplies for the RF cavities.  These RF cavities are located in the 274 meter long RF straight section on the Fermilab site.  For Phase 2, an additional similar RF straight section and Klystron Tube Enclosure will be required for the Low-Field Ring Bypass.  The Klystron galleries intended to be accessible by personnel for servicing systems during operation of the VLHC.  The gallery is illustrated in Figure 7.x. The Klystron Gallery is 25 feet x 25 feet x 120 feet long, serviced by a 30 foot diameter equipment and personnel shaft.  It is a minimum of 30 feet from the accelerator tunnel and is joined to the RF Cavern by four 30” diameter feed throughs, and a 12 foot diameter labyrinth corridor.

### 7.4.3	Kicker Magnet Power Supply Enclosures (4) (SSC specs)

The Kicker Magnet Power Supply Enclosures house the power supplies for injection and abort (at the Fermilab site) and for beam transfer from Low-Field to High-Field Rings (opposite side). These enclosures are adjacent to the four Utility Straight Sections.  For Phase 2, an additional RF straight will be required for the Low-Field Ring Bypass.  The enclosure is illustrated in Figure 7.x. The Kicker Power Supply Enclosure is 25 feet x 25 feet x 100 feet long, serviced by a 15 foot diameter equipment and personnel shaft.  It is a minimum of 30 feet from the accelerator tunnel and is joined to the Utility Straight Section by four 12” diameter feed throughs, and a 12 foot diameter labyrinth corridor.

### 7.4.4	Groundwater Collection Caverns and Pumping Stations (6)

The handling of groundwater seepage during the lifetime of the VLHC project will be a major concern.  The tunnel design specifies a maximum average of 50 gallons per minute per mile, or a total of 7,200 gallons per minute.  This flow will be directed through conduits through the invert floor to six collection and pumping stations at the sites of the cryogenics plants.  It is necessary to be able to collect at least 1 day’s flow of groundwater seepage (1.728 Million gallons = 231,000 cu. ft. per day for each of 6 pumping sites), in the event of failure of power or water systems.   At each of the 6 pumping sites, there will be groundwater collection reservoir caverns of dimensions (equivalent to) 62 ft x 62 ft x 62 ft plus volume for pumps (submersible or maintainable?)  How big pipes up shaft are needed?  Problems with depth?  If required, any monitoring of  groundwater influx for contamination, either conventional or radioactive, can be sampled at the collection caverns before discharge.   But what if it is contaminated?  Or even suspected to be contaminated?  We can’t stop discharging without risk of flooding the tunnel.  This task remains over the 40 year operational life of the project.  Do we need greater buffer volumes?  Maybe we need to do everything to exclude water from tunnel.

Need slope to drive the drainage!

### 7.4.5	Power Supply Caverns

The Phase 2 collider magnet systems will require 6 power supply stations to be distributed around the ring at the sites of the 6 cryogenics plants.  These will consist of an underground enclosure of dimensions 5 m x 4 m x 20 m (WxHxL) serviced by a 15 foot diameter personnel access shaft, a 15 foot (TR500 is 6 foot diagonal) clear equipment access shaft, and a nominal tunnel diameter corridor to the main tunnel.  This underground cavern will be serviced by LCW cooling water and AC electrical power (how much?) from the surface.  An alternative approach could be to feed only DC power, possibly through superconducting transmission lines, from the surface to the main tunnel directly.

## 7.5	Experimental caverns and bypasses (SSC model)

### 7.5.1	In Stage 1

### 7.5.2	In Stage 2 – no only one set of Experimental Caverns!

There is intended to be provision for two experimental caverns and installations in the IR straight sections at the Fermilab site.  These caverns, major access shafts, and associated surface structures for experimental apparatus fabrication, staging, and operations, will be located on the Fermilab site to minimize land procurement.  The model chosen is that of the designs for the caverns for the GEM and SDC experiments at the SSC [SSCL94].  It is understood that these caverns were optimized for a 20 TeV x  20 TeV collider, analogous to the VLHC Phase 1 Collider, and specifically not for the 85 TeV x 85 TeV VLHC Phase 2 Collider.  At this stage of this exercise, it is not fully appreciated how the cavern needs scale with collider energy.   The current model assumes that there is only one pair of experiment caverns, placed along the tunnel of the Phase 2 ring.  During Phase 1, the low field ring will also follow the Phase 2 tunnel.  For Phase 2, the low field ring will be displaced through its low-field ring bypass tunnel, away from the Experimental Caverns.  There will not be interaction regions or experimental caverns in the Phase 2 low field bypass.  Before Phase 2, the experiments will have to upgrade to the increased energy range (> 4 X), including a vertical change in the position of the interaction point, due to the difference in elevations of the low-field and high-field rings.

Cost optimization of the combination of geology, structural strength of strata, height of dolomite in spans, strength of walls, requirements of radiation shielding, and equipment access all determine the siting in elevation of the experimental caverns, and, thus, also the tunnel elevation at the Fermilab site.

Structural features and thickness of the strata supporting the spans of the experimental halls or caverns [SSC-Illinois-2] will determine the elevations at which the caverns can feasibly be sited.  This, of course, implies the elevation of the accelerator tunnel at the site of the cavern.  A general rule of thumb is that there should be a depth of hard rock (dolomite) strata above the cavern at least equal to the span of the cavern.  The previous study has concluded that for 75 foot high chambers, roof spans up to 125 feet are feasible using standard methods of  roof arching and rock supports.  This assumed that the orientation axis of the cavern bisects the major joint sets.  The joints run approximately NE-SW x NW-SE so this criteria would be satisfied by VLHC ring orientations to the North, South, or West.  Possible options in elevation for the experimental caverns are depicted in Figure 7.6.

The experimental caverns are envisioned to be 30 m x 40 m x 100 m (WxHxL) as in the SSC model depicted in Figure 7.13.

7.5.2.1	Cryogenics facilities, and safety

A tunnel bypass, to allow free access and transport of accelerator personnel, utilities, and equipment without entering the experimental caverns will be included.  A 25 meter maximum offset can be accommodated with  2 km radius bends over a total bypass length of 550 meters (including the 100 meters).  This would be of the same diameter as the main tunnel, likely constructed by backing up the tunnel boring machine.  (do we need larger tunnel here? – don’t tell them how to build it, boring machine, then widen for experiment caverns, or use experiment access shafts to tunnel height to drop boring machine).

7.5.2.2	Special surface buildings for Experimental Facilities

## 7.6	Survey and alignment (Global, for tunnel) – nothing yet

## 7.7	Surface buildings, footprints, and utilities

### 7.7.1	Stage 1

### 7.7.2	Stage 2

## 7.8	ES&H issues during construction, installation, and operations (worker health & safety, wetlands restoration, muck disposal, egress, etc.)  - given to Don Cossairt for review, 13feb01

For this exercise, ES&H issues have been merely identified without detailed study or specification of proposed solutions. Most of the ES&H issues both during construction and during operations of a VLHC are discussed for generic new accelerator facilities by the Fermilab Committee on Site Studies [FCSS01].  Although it is anticipated that much further ES&H work will be needed to optimize the costs and operations of a VLHC and satisfy standards to be applicable at the relevant time scales, for the purposes of this study, many of the ES&H requirements of the Superconducting Super Collider Laboratory [SSCL94] were assumed for the specifications and costing exercises.

VLHC design/specification issues with ES&H impact start with the finished diameter of the main tunnel.  A larger diameter will optimize installation, operations, and maintenance of the accelerator systems, and improve emergency egress and response.  However, increasing the tunnel diameter increases the overall project cost.   Personnel access and egress are issues with the number and placement of minor shafts.  After much negotiation, the Department of Energy accepted a minimum egress/ventilation shaft spacing of 2.7 miles for the final operating configuration for the SSC.  The Chicago area deep reservoir project (TARP) construction required a temporary personnel access/egress shaft (serviced by a crane with man-cage, at a maximum of 5000 feet from the dead-headed boring face.  Such temporary egress shafts are filled-in upon completion and final finishing of that nearby tunnel section.

In this study, it is anticipated that there will be minimum fire and smoke hazards in the tunnel.  Power supplies and electronics will be in special isolated cubby-holes, and interconnecting cables will be non-flammable, smokeless, and halogen-free.   The envisioned VLHC cryogenics systems will not use Liquid Nitrogen.  The quench reliefs of the Liquid Helium systems will be through high pressure piping within the cryogenic transfer lines.  What if that proves to be a problem?  There is the possibility of leaks and ruptures at every interconnect.  With reduced fire, smoke, and oxygen deficiency hazards, it is anticipated that during and after installation of the accelerator components, personnel entering the tunnel will carry sufficient oxygen supplies (2 hours?) nearby on their motorized access vehicles, removing the need for safety refuges (SSCL-90:  the SSCL had refuges, each with two hour fire door and two hour emergency air supply for up to 7 people located not greater than 2500 feet apart, between the emergency egress shafts).

The handling of groundwater issues will be a major environmental concern throughout the VLHC project.  Much of the tunnel, although below the piezometric surface (water table), will be in the Galena-Platteville dolomite, which is classified as an aquitard.  Still, grouting of cracks will be required to reduce the post-construction groundwater influx to workable pumping limits.  Other strata such as the sandstone and dolomitic sandstone, below the water table, of the South Ring configuration will be problematic from structural and water influx rate viewpoints and likely will require fully lined tunnel sections.

During tunnel construction, there will be additional water influx rates before tunnel grouting and lining, especially at the injection/equipment access ramps where the long and shallow-angle traversal of the glacial till-bedrock surface interface may be problematic before tunnel lining.  There will be the issues of dewatering the aquifer both during construction and operations, and aquifer contamination during construction, and radiological contamination of the soil and aquifer during accelerator operations.  Channeling, storage, pumping, and disposal of groundwater influx will require an engineered solution.  Are existing creeks nearby capable of accepting the water discharge?  The VLHC specification for groundwater seepage average discharge of 50 gallons per minute per mile of tunnel corresponds to a total of  7,200 gpm total, do be distributed over 6 pumping sites, each at 1,200 gpm.  Optimization studies will have to be undertaken to balance additional construction costs for water exclusion versus operating costs for dewatering costs over the 40 year (?) lifetime of the VLHC, including environmental impacts.

For the Phase 2 – high field ring VLHC, each of the six remote cryogenics sites will be consuming approximately 30 MW electrical power, mainly to run the Helium compressors.  This power will have to be dissipated to the environment, either by air-cooling towers, cooling ponds (approximately 30 acres each), or combinations of towers and ponds, depending on the particular environmental needs at each cryogenics site.

The disposal of spoils or muck from the underground construction will be an issue.  The spoils will have various fractions of clay, dolomite, shale, sandstone, etc. The Illinois SSC Proposal [SSC-Illinois-3] evaluated four scenarios, three of which were to refill nearby previous mining operations and the fourth was in landscaping around the shafts and remote sites.  Sale of the dolomite for use as construction material may, or may not, be feasible, depending on market conditions.

Constructing a tunnel will have major surface impact for personnel and equipment access and muck removal.  Some of these surface sites will not be needed , or with reduced footprint, after construction.  It will be important to have a plan to return these lands back to the citizens of Illinois in a useable and environmentally acceptable condition.

References:

SSC-Illinois:

-1	Geological- Geotechnical Studies for Siting the Superconducting Super Collider

in Illinois:  Preliminary Geological Feasibility Report, J.P. Kempton et al., ISGS

Environmental Geology Notes, EGN-111 (1985).

-2	Geotechnical Summary to the Proposal to Site the Superconducting Super Collider in Illinois, Harza Engineering Company and ISGS, (1987).

-3	Disposal of Material to be Excavated from the Illinois SSC,  L.M. Curran, S. B. Bhadwat, ISGS, (1987).

FCSS01-2:  Siting Considerations for Future Accelerator Facilities at Fermilab, FSCC,

DRAFT 2, dated XX-XX-XX, Chapter 2.  Geology and Underground Construction Methodologies.

NLC-NS:  Next Linear Collider (NLC) Project, North-South Alignment, Geotechnical Study, Harza Engineering Company (2000).

TARP:  Chicago Tunnel and Reservoir Plan.

NUMI:  Summary of the NuMI Project, the Fermilab NuMI Project Staff and the MINOS 		Collaboration, NuMI-678, Version 5.1 (2000).

TM-2048:  Cost Model for a 3 TeV VLHC Booster Tunnel, J. Lach et al.,

FERMILAB-TM-2048 (1998).

FCSS01-4:  Siting Considerations for Future Accelerator Facilities at Fermilab, FSCC,

DRAFT 2, dated XX-XX-XX, Chapter 4.  Potential Environmental, Safety, and Health Issues.

SSCL94:  Superconducting Super Collider, A Retrospective Summary, 1989-1993,

SSCL-SR-1235, April, 1994, Chapter 28, Environment, Safety, and Health, and

Quality Assurance.

SSCL90:  SSC Egress Provisions and Features for Evaluation of Equivalency as per

Chapter 7 of NFPA 101 M, L. Coulson and T. Toohig, 5/29/90.

Figures:

  - North Ring Surface Plan

  - Tilted North Ring Lampshade 				(same as 7.3)

  - Flat North Ring Lampshade					(same as 7.2)

  - South Ring Surface Plan

  - Tilted South Ring Lampshade

  - Elevation Options for Experimental Halls/Caverns		need

  - VLHC main tunnel plan

  - Straight Section Cluster at Fermilab

  - Main Tunnel Cross Section					modify to 12’ dia

  - Tunnel Shafts							need

  - Special Tunnel Configurations				need

  - Injection from Tevatron to VLHC (elevation view)		need modification

  - SSC Model of Experimental Caverns				needs modification

Tables:

  - Straight Sections at Fermilab

  - Special Tunnel Sections

# Footnotes

original source file: \\tdserver1\project\VLHC\TDDoc\DesignStudyReport\07_Conventional_construction\Draft1\7_conventional_construction_v1.doc