## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 777
EPA ID No. | GAD981237118
Facility Name | Monsanto (Nutrasweet Kelco Co.)
Facility Location
City | Augusta
State | GA
Unit ID Name/No. | Boiler 2 - WHRU 2
Other Sister Facilities | None
Number of Sister Facilities | 0
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics | Firetube boiler. John Zink 2-stage combustion firetube boiler, forced draft, with 2 burner guns; 26 MM Btu/hr, 19,500 lb/hr steam with fire-tube heat recovery boiler; part of cooled boiler exhaust is returned to 2nd stage combustor inlet
Capacity (MMBtu/hr) | 26
Soot Blowing | None
APCS Detailed Acronym | QC/WS
APCS General Class | WQ,LEWS
APCS Characteristics | (Cooler/caustic scrubber)
Hazardous Wastes | Liq
Haz Waste Description | Liquid, primarily ester #1 and methanol, classed as D001 and D002; 42-51% ester #1, 10-17% methanol, 11-18% water, 9-22% acetic acid, and <1% hydrochloric acid; 8.1 lb/gal and 7,100 Btu/lb
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft)
Height (ft) | 100
Gas Velocity (ft/sec)
Gas Temperature (°F) | 155
Permitting Status | Tier IA for all metals, except Cr; Tier III for Cr/HCL/Cl2
HWC Burn Status (Date if Terminated)

## cond
Cond Description
777C10
Report Name/Date | BIF Recertification of Compliance Test Report - Boilers 1 and 2; dated August 20, 1997
Report Prepar | B3 Systems, Inc
Testing Firm | METCO
Testing Dates | June 17-25, 1997
Cond Dates | 1997-06-01
Cond Description | CoC; max feedrate
Content | PM, CO, HCl/Cl2, Cr emissions; metals/ash/Cl feed analysis
777C11
Report Name/Date | BIF Recertification of Compliance Test Report - Boilers 1 and 2; dated August 20, 1997
Report Prepar | B3 Systems, Inc
Testing Firm | METCO
Testing Dates | June 17-25, 1997
Cond Dates | 1997-06-01
Cond Description | CoC; min combustion temp
Content | CO

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
10 | 777C10 |  |  |  | R1 | R2 | R3 | Cond Avg
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  | 5850 | 5695 | 5639 | 5728
| O2 |  | % |  | 3 | 2.3 | 2.6 | 2.6333
| Moisture |  | % |  | 27.29 | 26.68 | 27.97 | 27.3133
| Temperature |  | °F |  | 155 | 154 | 156 | 155
| PM |  | gr/dscf | n | 0.0556 | 0.0567 | 0.0557
| HCl |  | ppmv | n | 5.63 | 5.4 | 5.56
| Cl2 |  | ppmv | n | 0.01 | 0.01 | 0.01
| PM | E1 | gr/dscf | y | 0.043244 | 0.042449 | 0.04238 | 0.042691
| CO (RA) | E1 | ppmv | y | 12 | 7.2 | 7.1 | 8.7667
| CO (MHRA) | E1 | ppmv | y | 12 | 7 | 7 | 8.6667
| HCl | E1 | ppmv | y | 4.3789 | 4.0428 | 4.2304 | 4.2174
| Cl2 | E1 | ppmv | y | 0.0077778 | 0.0074866 | 0.0076087 | 0.0076244
| Total Chlorine | E1 | ppmv | y | 4.3944 | 4.0578 | 4.2457 | 4.2326
| Sampling Train | Cr | E2
| Stack Gas Flowrate |  | dscfm |  | 6011 | 5735 | 5691 | 5812.3333
| O2 |  | % |  | 3 | 2.3 | 2.6 | 2.6333
| Moisture |  | % |  | 27.78 | 26.86 | 27.88 | 27.5067
| Temperature |  | °F |  | 153 | 154 | 155 | 154
| Chromium |  | µg/dscm | n | 9.4155 | 16.7438 | 15.4747 | 13.878
| Chromium | E2 | µg/dscm | y | 7.3232 | 12.5354 | 11.7742 | 10.5443
| LVM | E2 | µg/dscm | y | 7.3232 | 12.5354 | 11.7742 | 10.5443
11 | 777C11 |  |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) | E1 | ppmv | y | 16.8 | 17.7 | 19 | 17.8333
| CO (MHRA) | E1 | ppmv | y | 17 | 17 | 19 | 17.6667
| Sampling Train | CO | E1
| Stack Gas Flowrate |  | dscfm
| O2 |  | % |  | 11 | 11 | 11.2 | 11.0667
| Moisture |  | %
| Temperature |  | °F

## feed
Feedstreams
* | 777C10 |  | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg
| Feedstream Number |  | F1 | F1 | F1 | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3
| Feed Class |  | Liq HW | Liq HW | Liq HW | Liq HW | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feed Class 2 |  | HW | HW | HW | HW | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feedstream Description |  | Liquid waste | Liquid waste | Liquid waste | Liq waste | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feed Rate | g/hr | 1960000 | 1950000 | 1910000 | 1940000 | 127000 | 127000 | 127000 | 127000
| Density | g/ml | 0.94 | 0.95 | 0.92 | 0.93667
| Ash | g/hr | 1960 | 1950 | 1910 | 1940 | 15100 | 15200 | 15200 | 15200
| Chlorine | g/hr | 2150 | 1950 | 2490 | 2196.6667 | 15200 | 15200 | 15200 | 15200
| Mercury | g/hr | 0.00391 | 0.00389 | 0.00383 | 0.0038767
| Lead | g/hr | 0.0489 | 0.0486 | 0.0478 | 0.048433
| Cadmium | g/hr | 0.0489 | 0.0486 | 0.0478 | 0.048433
| Arsenic | g/hr | 0.215 | 0.272 | 0.142 | 0.20967
| Beryllium | g/hr | 0.0489 | 0.0486 | 0.0478 | 0.048433
| Chromium | g/hr | 0.235 | 0.253 | 0.249 | 0.24567 | 2.42 | 2.42 | 2.42 | 2.4
| Antimony | g/hr | 0.09 | 0.125 | 0.0478 | 0.0876
| Stack Gas Flowrate | dscfm | 5850 | 5695 | 5639 | 5728 | 5850 | 5695 | 5639 | 5728
| O2 | % | 3 | 2.3 | 2.6 | 2.6333 | 3 | 2.3 | 2.6 | 2.6333
| Thermal Feedrate | MMBtu/hr | 26.3 | 22.3 | 24.9 | 24.5 |  |  |  |  | 26.3 | 22.3 | 24.9 | 24.5
| Estimated Firing Rate | MMBtu/hr | [8 empty] | 33.4286 | 33.8084 | 32.9389 | 33.3982
Feedrate MTEC Calculations
| Ash | mg/dscm | 153.4681 | 150.9696 | 151.7762 | 152.0713 | 1182.3306 | 1176.789 | 1207.8528 | 1191.2436 | 1335.7987 | 1327.7586 | 1359.6291 | 1343.3149
| Chlorine | µg/dscm | 168345.0839 | 150969.6423 | 197865.3644 | 172393.3636 | 1190160.5934 | 1176789.007 | 1207852.827 | 1191243.6107 | 1358505.6773 | 1327758.6493 | 1405718.1914 | 1363636.9742
| Mercury | µg/dscm | 0.30615 | 0.30117 | 0.30435 | 0.30389 |  |  |  |  | 0.30615 | 0.30117 | 0.30435 | 0.30389
| Lead | µg/dscm | 3.8289 | 3.7626 | 3.7984 | 3.7966 |  |  |  |  | 3.8289 | 3.7626 | 3.7984 | 3.7966
| Cadmium | µg/dscm | 3.8289 | 3.7626 | 3.7984 | 3.7966 |  |  |  |  | 3.8289 | 3.7626 | 3.7984 | 3.7966
| Arsenic | µg/dscm | 16.8345 | 21.0583 | 11.2839 | 16.3922 |  |  |  |  | 16.8345 | 21.0583 | 11.2839 | 16.3922
| Beryllium | µg/dscm | 3.8289 | 3.7626 | 3.7984 | 3.7966 |  |  |  |  | 3.8289 | 3.7626 | 3.7984 | 3.7966
| Chromium | µg/dscm | 18.4005 | 19.5873 | 19.7865 | 19.2581 | 189.4861 | 187.3572 | 192.3029 | 188.0911 | 207.8866 | 206.9445 | 212.0894 | 207.3492
| Antimony | µg/dscm | 7.047 | 9.6775 | 3.7984 | 6.841 |  |  |  |  | 7.047 | 9.6775 | 3.7984 | 6.841
| SVM | µg/dscm | 7.6577 | 7.5253 | 7.5968 | 7.5933 |  |  |  |  | 7.6577 | 7.5253 | 7.5968 | 7.5933
| LVM | µg/dscm | 39.0639 | 44.4083 | 34.8688 | 39.447 | 189.4861 | 187.3572 | 192.3029 | 188.0911 | 228.55 | 231.7655 | 227.1717 | 229.1624
* | 777C11 |  | R1 | R2 | R3 | Cond Avg
| Feedstream Number |  | F1 | F1 | F1 | F1
| Feed Class |  | Liq HW | Liq HW | Liq HW | Liq HW
| Feed Class 2 |  | HW | HW | HW | HW
| Feedstream Description |  | Liquid waste | Liquid waste | Liquid waste | Liquid waste
| Feed Rate | g/hr | 1140000 | 1100000 | 1140000 | 1126666.6667
| Thermal Feedrate | MMBtu/hr | 16.6 | 15.5 | 15.8 | 15.9667
| Ash | g/hr | 1140 | 1100 | 1140 | 1126.6667
| Chlorine | g/hr | 1830 | 1430 | 1590 | 1616.6667
| Mercury | g/hr | 0.0229 | 0.022 | 0.0227 | 0.022533
| Lead | g/hr | 0.0286 | 0.0275 | 0.0284 | 0.028167
| Cadmium | g/hr | 0.0286 | 0.0275 | 0.0284 | 0.028167
| Arsenic | g/hr | 0.106 | 0.291 | 0.0847 | 0.16057
| Beryllium | g/hr | 0.0418 | 0.0868 | 0.136 | 0.0882
| Chromium | g/hr | 0.137 | 0.103 | 0.0682 | 0.10273
| Antimony | g/hr | 0.0492 | 0.0275 | 0.0738 | 0.050167
| Stack Gas Flowrate | dscfm |  |  |  | NA
| O2 | % | 3 | 2.3 | 2.6 | 2.6333
need stack gas flowrate to make MTEC calculations
| Estimated Firing Rate | MMBtu/hr
| Ash | mg/dscm
| Chlorine | µg/dscm
| Mercury | µg/dscm
| Lead | µg/dscm
| Cadmium | µg/dscm
| Arsenic | µg/dscm
| Beryllium | µg/dscm
| Chromium | µg/dscm
| Antimony | µg/dscm
| SVM | µg/dscm
| LVM | µg/dscm

## process
Process Information
| Units | Cond Avg
777C10
Steam Production Rate | klb/hr | 51.16
Comb Chamber Temperature | F | 1993
Scrubber Operation
Scrubber L/G Ratio | gpm | 9.79
Scrubber Liquid Blowdown | gpm/kacfm | 5.3
Scrubber pH |  | 6.3
777C11
Comb Chamber Temperature | F | 1105