November 21, 1997

Contract # TW-0928

SPECIAL SPECIFICATION

SECTION 16425-S

LOW VOLTAGE SWITCHBOARD

PART 1 - GENERAL

1.01	Description Of Work 	  1

1.02	References	  1					2

1.03	Submittals and Substitutions	  3					4

1.04	Quality Assurance	  4				5

1.05	Delivery, Storage, And Handling	  6

1.06	Warranty	  6					5

PART 2 - PRODUCTS

2.01	Switchboard, General	  6				6

2.02	Fabrication And Features	  7			7

2.03	Overcurrent Protective Devices	  10			9

2.04	Circuit Breaker Accessories	15

2.05	Circuit Breaker Trip Devices	15

2.06	Control Power And Wiring	17

2.07	Test And Inspection Equipment	17

2.08	Identification	18

2.09	Extra Material	18

PART 3 - EXECUTION

3.01	Examination	18

3.02	Installation	18

3.03	Cleaning	19

3.04	Inspection And Testing	19

Appendix A and B

SPECIAL SPECIFICATION

SECTION 16425-S

LOW VOLTAGE SWITCHBOARD

PART 1 - GENERAL

1.01	DESCRIPTION OF WORK

A.	This section includes furnishing and installing power distribution switchboard and associated auxiliary equipment rated 600 Volt or less.

B.	Switchboard protective devices covered by this specification are:

1.	Molded case circuit breakers

2.	Insulated case circuit breakers

3.	Power circuit breakers (used as incoming main or tie breaker only)

C.	Related Sections:  Refer to the following sections for related work:

1.	Section 01300 -  Submittals

2.	Section 16001 - Electrical Work

1.02	REFERENCES

Comply with the following applicable standards and codes:

A.	National Fire Protection Association (NFPA):

1.	NFPA 70	National Electrical Code

B.	Underwriters Laboratories, Inc. (UL):

1.	UL 486A	Wire Connectors and Wiring Lugs for Use With Copper Conductors

2.	UL 489	Circuit Breakers, Molded-Case, and Circuit-Breaker Enclosures

3.	UL 891	Deadfront Electrical Switchboards

4.	UL 1066	Low-Voltage AC and DC Power Circuit Breakers Used in Enclosures

C.	National Electrical Manufacturers Association (NEMA):

1.	NEMA AB 1	Molded Case Circuit Breakers

2.	NEMA EI 21.1	Instrument Transformers for Revenue Metering 110 kV BIL and less

3.	NEMA PB 2	Deadfront Distribution Switchboards

4.	NEMA PB 2.1	General Instructions for Proper Handling, Installation and Maintenance of Deadfront Distribution Switchboards Rated 600 Volts or Less

5.	NEMA PB 2.2	Application Guide for Ground Fault Protective Devices for Equipment

6.	NEMA SG3	Low-Voltage Power Circuit Breakers

7.	NEMA 250	Enclosures for Electrical Equipment (1,000 volts, maximum)

D.	American National Standards Institute, Inc. (ANSI):

1.	ANSI-C12.1	Electricity Metering

E.	American National Standards Institute, Inc./Institute of Electrical and Electronics Engineers (ANSI/IEEE):

1.	ANSI/IEEE-C37.16	Low-voltage Power Circuit Breaker and AC Power Circuit Breaker Protectors - Preferred Ratings, Related Requirements and Application Recommendations

2.	ANSI/IEEE-C37.17	Trip Devices for AC and General Purpose DC Low-Voltage Power Circuit Breaker

3.	ANSI/IEEE-C37.20.1	Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear

4.	ANSI/IEEE-C39.1	Requirements for Electrical Analog Indicating Instruments

5.	ANSI/IEEE-C57.13	Requirements for Instrument Transformers

F.	InterNational Electrical Testing Association (INETA):

1.	 Acceptance Testing Specifications, ATS, for Electrical Power Distribution Equipment and Systems

1.03	SUBMITTALS and SUBSTITUTIONS:

A.	General:  Submit the following in accordance with provisions of Section 1300-S, "Descriptive Submittals".

B.	For approval before equipment is ordered.

1.	Manufacturer's published data for each product and component furnished.

2.	Schedule of features, characteristics (including time-current curves), ratings, and factory settings of individual protective devices.

3.	Shop drawings for proposed switchboard including, but not limited to, dimensioned plans and elevations, component and device lists, conduit entrance locations and requirements, and a single-line diagram showing main and branch bus current ratings, main and branch protective device ratings, ground connection current rating, and short-time and short-circuit ratings of switchboard.

4.	Manufacturer's Schematic Wiring Diagram Point-to-Point Control Wiring Diagram.  Differentiate between manufacturer-installed and field-installed wiring.

5.	Shop drawings or other descriptive documentation of barriers specified for electrical insulation and isolation.

6.	Shop drawings detailing the installation, when required of metering test switches and potential and current transformers.

7.	Shop drawings detailing the installation, when required, of Square D PowerLogic Circuit Monitor(s).

8.	When it is proposed to provide protective devices manufactured by other than those designated in schedules of overcurrent protective devices or show on the drawings, comply with the provisions of Section 16001-S (Electrical Work), part 1.03.E and submit results.

9.	When a mimic bus is required, submit diagram.

10.	If the proposed switchboard incorporates overcurrent protective devices or components not listed in Appendix A to this specification, a complete list of all special tools and test equipment to be supplied to Sandia National Laboratories as required by part 2.07 of this specification.

C.	Following installation of the switchboard

1.	As built drawings showing all changes made during installation.

2.	Final settings of all circuit breaker tripping devices.

3.	When a mimic bus is supplied, submit updated version of diagram reflecting field changes after final switchboard load connections have been made.

4.	Documentation of manufacturer's warranty

5.	Original copies of all manufacturer furnished installation, operating and maintenance instructions.

D.	Substitutions: only under provisions of Section 1600-S.

1.04	QUALITY ASSURANCE

A.	Manufacturer's Qualifications:  The manufacturer shall be regularly engaged in the manufacture of switchboard of the types and sizes required and shall have had similar products in satisfactory use in similar service for not less than ten (10) years.

B.	Listing and Labeling:  The switchboard and all devices mounted thereon shall be listed and labeled for their intended use by a nationally recognized testing laboratory as defined in OSHA Regulation 1910.7.  The terms "listed" and "labeled" are defined in the National Electrical Code, Article 100.

C.	Electrical Component Standard:  Components and installation shall comply with NFPA 70, National Electrical Code.

D.	Product Selection for Restricted Space:  Where the drawings indicate maximum dimensions for equipment, including clearances between equipment and adjacent surfaces and items, only switchgear meeting specified performance characteristics and complying with indicated maximum dimensions will be accepted.

1.05	DELIVERY, STORAGE, AND HANDLING

A.	Deliver in shipping splits of lengths that can be moved past obstructions in delivery path.  Provide weather tight protection during shipment.

B.	Store so condensation will not occur on or in switchboard. Provide temporary heaters as required to assure avoiding condensation.  Store NEMA Class 1 equipment indoors.

C.	Handle equipment in accordance with manufacturer's instructions and NEMA PB2.1.

D.	Use factory-installed lifting provisions.

E.	Do not remove shipping blocks or braces until equipment is mounted in final location.

1.06	WARRANTY

A.	Included:  Design, material, and workmanship for switchgear and all associated protective devices, control systems, and metering systems.

B.	Period:  Standard for manufacturer, but not less than 12 months following acceptance by owner from contractor.

PART 2 - PRODUCTS

2.01	SWITCHBOARD, GENERAL

A.	Refer to the drawings or schedules for required circuit breaker types, circuit breaker ratings, circuit breaker mounting requirements, short circuit current rating(s) in RMS symmetrical amperes, general configuration of switchgear and whether or not the switchboard is service entrance equipment.

B.	Description - Provide equipment with deadfront construction. Furnish front connected, front accessible or front and rear accessible as shown on the drawings or schedules.

C.	Barriers:  Provide insulated barriers between adjacent switchgear sections to minimize probability of arc propagation.

D.	Service Conditions:

1.	Except as noted otherwise on the construction drawings, switchboard classified NEMA 1 shall be designed for indoor installation at an altitude of 6,000 feet (2,000 meters) or less.

2.	Except as noted otherwise on the construction drawings, switchboard classified NEMA 3R shall be designed for the following conditions.

a.	Ambient temperature:  -18 to 45 degrees C.

b.	Altitude:  6,000 feet (2,000 meters) or less above sea level.

c.	Service location:  Non-hazardous location.

d.	Seismic zone:  2.

e.	Environment:  Outdoors in direct sunlight with full exposure to the weather. Occasional wind-blown rain, snow, sand, and dust.

2.02	FABRICATION AND FEATURES

A.	Provide steel enclosure constructed to NEMA classification as required by the drawings or schedules.  Required NEMA classifications include.

1.	NEMA 1

2.	NEMA 1 with drip shield

3.	NEMA 3R, rain proof

4.	NEMA 3R, rain proof, with lighted walk-in interior aisle and convenience outlet

B.	Designed and constructed to prevent the entry of rodents into the interior of the switchboard.  For NEMA 3R - Design to prevent entry of dust into switchboard by using gasketing on all doors.

C.	Design NEMA 3R rated equipment to prevent entry of dust into switchboard by using gasketing on all doors and filters on all ventilation registers.

D.	Top and bottom shall have removable bolted steel plates and shall be suitable for conduit entry.  All internal devices, line connections, and load connections shall be readily accessible and removable.

E.	Overcurrent protective devices shall not be attached to the front panel.  Sufficient space shall be provided to accommodate specified accessories, separately mounted current transformers, etc.  Where meters, switches, relays, etc., are mounted to front panels, those panels shall be side hinged for access with bolt closures.

F.	Finish:

1.	Enclosure Finish for Outdoor Units:  UL 891, Paragraph 9.22 C.2, manufacturer's standard color.  Undersurfaces shall additionally receive a corrosion-resistant undercoating treatment.  The finish system shall meet the requirements of tests in accordance with ANSI/IEEE C37.20.1, "Standard for Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear," paragraph 5.2.8.

2.	Enclosure Finish for Indoor Units:  Manufacturer's standard gray finish over a rust inhibiting primer on phosphatizing treated metal surface.  Provide painted surfaces that conform to ANSI/IEEE C37.20.1, "Standard for Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear," paragraph 5.2.8.

G.	Space Heaters:

1.	Application: Provide outdoor switchboard with factory-installed, electric space heaters in each vertical section.

2.	Description: Space heaters shall be rated 230 Vac and operated at 120 Vac.  Mount space heaters away from painted surfaces and provide a suitable mechanical guard for each space heater.

3.	Space Heater Control:  Thermostat, adjustable over a minimum range of 0 degree C. to 25 degree C.  Factory-set to maintain switchgear above 10 degree C.

4.	Space Heater Power Source:  Control power transformer factory-mounted in switchgear with all ungrounded leads fused.

H.	Provide bus transition and incoming line pull sections when specified on the drawings or schedules.  Match and align the sections with the basic switchboard.  When bottom feed, provide cable support so weight of cable does not hang on cable lugs.

I.	When rear access is required, provide hinged rear doors for access to rear interior of switchboard.  Secure by captive thumb screws.

J.	Removable Hinged Front Panels:  Provide to allow access to breaker, metering, accessory, and blank compartments.

K.	Buses and Connections:  Three-phase, four-wire except as otherwise

1.	Phase and Neutral Bus Material:  Hard-drawn copper of minimum 98 percent conductivity.

2.	Use copper for feeder and branch circuit-breaker line connections.

3.	Cable connections to bus shall be by lug with crimp (compression) connection between the barrel of the lug and the conductor and two hole NEMA pattern bolted connection of the lug to the bus.  Use compression dies recommended by lug manufacturer only.

L.	Ground Bus:  1/4-inch by 2-inch (7mm X 50mm) minimum size, hard-drawn copper of minimum 98 percent conductivity, and equipped with crimp (compression) connector terminations for feeder- and branch-circuit ground conductors.  For busway feeders extend insulated equipment grounding cable to busway ground connection and support cable in vertical run.

M.	Supports and Bracing for Buses:  Adequate strength for specified short-circuit currents.

N.	Contact Surfaces of Buses:  Silver plated.

O.	Main Phase Buses, Neutral Bus, and Equipment Ground Bus:  Uniform capacity the entire length of the switchgear main and distribution sections.  Provide for future extensions from either end by means of bolt holes or other approved method and connecting links.

P.	Provide access to permit field torquing of all bus bolts.

Q.	Neutral Buses:  100 percent of the ampacity of the phase buses and equipped with approved terminations for all neutral cables.  Provide braced neutral bus extension for busway feeders with neutral conductors.

R.	Surge Arresters

1.	General:  Furnish with factory-installed arresters as shown on drawings or schedules.

S.	Instrumentation and metering

1.	General:  Furnish with factory-installed metering and associated instrument transformers and test switches as shown on drawings or schedules.

2.	Include relay and meter test plugs suitable to permit testing switchgear meters.

3.	All instrumentation and metering wiring connected to threaded posts shall be terminated with ring tongue connectors.

4.	Powerlogic monitor

a.	Furnish and install Square D PowerLogic circuit monitor(s), as required by drawings or schedules.  Supply model shown on drawings or schedules.

b.	Mount monitor(s) flush or semi-flush on a separate instrument compartment hinged door when switchgear is furnished with drawout-type main circuit breaker(s).

c.	When switchgear is rated 480Y/277 volts, monitor(s) shall be furnished with the Square D potential transformers unit intended to permit the monitors to be directly  operated at 480 volts.

2.03	OVERCURRENT PROTECTIVE DEVICES

A.	General:  Provide circuit breakers as integral components of switchboard with indicated features, ratings, characteristics, and settings.

B.	Future Devices:  Where provision for future circuit breakers or spaces is indicated, equip compartments with mounting brackets, supports, bus connections and necessary appurtenances, of ampere ratings indicated for future installation of circuit breakers.

C.	Ground fault protection shall be provided for all main service circuit breakers when shown on the drawings or schedules or as required by the NEC, Article 230-95.  Ground fault protection for feeder circuit breakers shall only be provided when shown on the drawings or schedules.

D.	Molded-Case Circuit Breakers

1.	General:  UL 489, "Molded Case Circuit Breakers and Circuit Breaker Enclosures," and NEMA AB 1, "Molded Case Circuit Breakers."

2.	Characteristics:  Frame size, trip rating, number of poles, and short-circuit interrupting capacity rating as shown on drawings or schedules.  Interrupting capacity not less than 14,000 amperes symmetrical.  Voltage and frequency ratings same as switchboard.

3.	Tripping Device:  Quick-make, quick-break toggle mechanism with inverse-time delay and instantaneous overcurrent trip protection for each pole.

4.	Adjustable Instantaneous Trip Devices:  On units where available shall be front adjustable.  When furnished shall be factory adjusted to low-trip-setting current values.

5.	Current-Limiting Circuit Breakers:  Where required by drawings or schedules, Arranged to limit let-through ampere-squared-seconds during fault conditions to a value less than the ampere-squared-seconds of one-half-cycle wave of the prospective symmetrical fault current.  The circuit breaker shall use no fusible devices in its operation.  The current-limiting characteristic shall be in addition to normal time-delay and instantaneous-trip characteristics and other features as indicated.

6.	Circuit Breakers With Solid-State Trip Devices:  Except as noted otherwise on the drawings or schedules, all molded case circuit breakers with solid-state trip devices shall be 100% rated.  Provide indicated circuit breakers with solid-state trip devices having the following features:

a.	Ambient Compensation:  Trip device insensitive to temperature changes between minus 20 deg C and plus 55 deg C.

b.	Adjustability:  Breaker ratings and trip settings shall be changeable by operation of controls on front panel of breaker, by change of plug-in element without removing breaker from mounting, or by a combination of the two methods.

c.	Ground-Fault Tripping:

(1)	Furnish when required on drawings or schedules, adjustable for pick-up and time-delay values.

(2)	Suitable for incorporation in zone selective ground-fault tripping schemes.

7.	Terminal Lugs:  Furnish load side of circuit breaker with front-connected UL listed lugs for copper cable at full frame rating.

E.	Insulated-Case Circuit Breakers

1.	General:  UL 489, "Molded-Case Circuit Breakers and Circuit Breaker Enclosures," and NEMA AB 1, "Molded-Case Circuit Breakers."

2.	Characteristics:  Frame size, number of poles, and short-circuit interrupting capacity rating as shown on drawings or schedules.  Voltage and frequency ratings compatible with switchboard.  Circuit breakers UL listed to continuously carry 100 percent of the frame rated current in their intended enclosure.

3.	Operating Mechanism:  Mechanically or electrically operable, trip-free, stored-energy operating mechanism with the following features:

a.	Moving Contacts Closing Speed:  Independent of both control and operator.

b.	Stored-Energy Mechanism:  True two-step stored energy mechanism that shall provide a five cycle maximum closing time.  Either manually or electrically operated as indicated on the drawings and/or schedules.  Electrically operated breakers shall have provisions for optional manual charging.  Furnish both manual and electrical operated breakers with multiply charge/close provisions capable of the following sequence: charge-close-recharge-open-close-open.  Provide capability to manually discharge the stored energy without closing the breaker.

c.	Anti-pump provisions shall be provided for electrically operated breakers.

d.	Operation Counter:  Include except as otherwise indicated.

4.	Auxiliary Contacts for Remote Indication:  Where remote indication of breaker position is indicated, provide a spare auxiliary switch in addition to other auxiliary switches required for the normal breaker operation.  The spare auxiliary switch shall consist of 2 Type "a" and 2 Type "b" stages (contacts) wired through secondary disconnecting devices to a terminal block in the stationary housing.

5.	Mounting:  Provide draw-out circuit breaker mounting assembly equipped with a heavy duty racking mechanism that properly positions the circuit breaker and holds it rigidly in connected, test/disconnected, and fully withdrawn positions and includes the following features:

a.	Interlock arrangement, preventing movement of the circuit breaker to or from the connected position when it is in the closed position and closure of the circuit breaker unless it is in the connected, test/disconnected or withdrawn position.

b.	Construction permitting racking an open circuit breaker to or from the connected, test, and disconnected positions with the associated compartment door closed or equivalent dead-front barrier protection, and manual withdrawal to a position for removal from the structure with the door open.

c.	Primary disconnecting devices disengaged and secondary disconnecting devices engaged when breaker is in test position.

d.	Primary and secondary devices disengaged when circuit breaker is in the disconnected position.

e.	Ground contact engaged when the circuit-breaker element is in the connected and test positions.

f.	Rotatable breaker moveable element when the breaker is in the withdrawn position for ease of inspection.

6.	Circuit-Breaker Features:  Include the following:

a.	Charging Handle:  Provide one for each breaker.  Interlock manual close button and charging handle.

b.	Manual trip button.

F.	Power Circuit Breakers

1.	Standards:  Conform to UL 1066, "Low-Voltage AC and DC Power Circuit Breakers Used in Enclosures," and to IEEE C37.13, "Standard for Low-Voltage AC Power Circuit Breakers Used in Enclosures."

2.	Characteristics:  Frame size, number of poles, and short-circuit interrupting capacity rating as shown on drawings or schedules.  Voltage and frequency ratings compatible with switchboard.  Circuit breakers listed to continuously carry 100 percent of the frame rated current in their intended enclosure.

3.	Operating Mechanism:  Mechanically and electrically operable, trip-free, stored energy operating mechanism with the following features:

a.	control and operator.

b.	Provide for manual charging of the mechanism and for slow  closing of the contacts for inspection and adjustment.

c.	Stored Energy Mechanism:  Manually or electrically charged as indicated on the drawings or schedules.  Furnish electrically operated only if indicated on drawings and/or schedules.

d.	Operation Counter:  Include except as otherwise indicated.

4.	Auxiliary Contacts for Remote Indication:  Where remote indication of breaker position is indicated, provide a spare auxiliary switch in addition to other auxiliary switches required for the normal breaker operation.  The spare auxiliary switch shall consist of 2 Type "a" and 2 Type "b" stages (contacts) wired through secondary disconnecting devices to a terminal block in the stationary housing.

5.	Mounting:  Provide draw-out circuit breaker mounting assembly equipped with a heavy duty racking mechanism that properly positions the power circuit breaker and holds it rigidly in connected, test/disconnected, and fully withdrawn positions and includes the following features:

a.	Interlock arrangement preventing movement of the circuit breaker to or from the connected position when it is in the closed position and closure of the circuit breaker unless it is in the connected, test/disconnected or disconnected position.

b.	Construction permitting racking an open circuit breaker to or from the connected, test, and disconnected positions with the associated compartment door closed (unless live parts are covered by a full dead-front shield), and manual withdrawal to a position for removal from the structure with the door open.

c.	Primary disconnecting devices disengaged and secondary disconnecting devices engaged when breaker is in test position.

d.	Primary and secondary devices disengaged when circuit breaker is in the disconnected position.

e.	Ground contact engaged when the circuit breaker element is in the connected and test positions.

6.	Circuit Breaker Features:  Include the following:

a.	Arc Chutes:  Readily removable when the circuit breaker is in the disconnected position.  Arranged to permit inspection of the contacts without removing the circuit breaker from the switchboard.

b.	Charging Handle:  One for each manually operated breaker.

c.	Manual Trip Button:  One for each manually operated breaker.

2.04	CIRCUIT BREAKER ACCESSORIES

A.	Circuit-Breaker Removal Apparatus:  When drawout breakers are furnished, provide overhead breaker lifting device, track mounted at top front of switchgear and complete with hoist and lifting yokes matching each drawout breaker.

B.	Key Interlocks:  When required by the drawings or schedules, arrange interlocking so keys are held captive at devices indicated.  Where future key interlocking provisions are indicated, provide necessary mountings and hardware as required for the future installation.

C.	Shunt-Trip Devices for Circuit Breakers:  When required by drawings or schedules, arrange to trip breaker from an external source of power through a control switch or relay contacts.

D.	Padlocking Provisions:  Provide padlocking provisions as follows:

1.	Equip all circuit breakers for padlocking in the open position.

2.	Equip all draw out mechanisms for the installation of a padlock to prevent circuit breaker insertion.

3.	Padlocking assembly shall not prevent doors from being opened while energized or closed.

2.05	CIRCUIT BREAKER TRIP DEVICES FOR INSULATED-CASE AND POWER CIRCUIT BREAKERS:

A.	Multi-function devices:  True RMS sensing, microprocessor based, solid-state overcurrent trip device system that includes one or more integrally mounted current transformer or sensor per phase, a release mechanism, and the following features:

1.	Functions:  Long-time-delay, short-time-delay, and instantaneous-trip functions, which are independent of each other in both action and adjustment or other combination of functions if shown on the drawings or schedules.

2.	Temperature compensation to assure accuracy and calibration stability from minus 20 deg C to plus 55 deg C.

3.	Field-adjustable time-current characteristics while breaker is energized and closed.

4.	Current Adjustability:  Effected by operating controls on front panel or by changing plug-in elements or current transformers or sensors or a combination of these methods.

5.	Three bands for long-time- and short-time-delay functions marked "minimum," "intermediate," and "maximum."

6.	Pickup points for long-time, short-time and instantaneous-trip functions as shown on drawings or schedules.  If shown on drawings or schedules, furnish short-time-trip function with switchable ampere-squared-seconds capability.

7.	Ground fault protection:  Where indicated on drawing or schedules, provide ground fault protection incorporating:

a	Minimum of three short-time-delay settings and three trip-time-delay bands.

b.	Adjustable current pickup.

c.	When required, suitable for incorporation in zone selective ground-fault tripping schemes.

d.	Provide with both fixed time delay and tampere-squared-seconds settings.

8.	Trip Indication:  Labeled lights or mechanical indicators on trip device indicating type of fault or overload causing breaker trip.  If lights are used, integral power source shall maintain indication for 60 hours, minimum.

9.	Adjustable-Time-Delay Undervoltage Trip Devices:  Provide when indicated on drawings or schedules.

10.	Arranged to permit testing of all functions of solid-state rip devices without removal from switchgear.

11.	Arrange to permit viewing and adjustment of all adjustable trip settings and all trip indications without having to open circuit breaker compartment doors.

12.	Provide clear, sealable cover over adjustments.

B.	Single-function:  Solid-state or electro-mechanical.

1.	Furnish device(s) as required by drawings or schedules.

2.	Arranged to permit testing of all functions without removal from switchgear.

2.06	CONTROL POWER AND WIRING

A.	General:  When required, provide control power transformer(s) as shown on the drawings or schedules.

B.	Control Power Transformers:  Dry type.  Separate compartments for units larger than 3 kVA and their primary and secondary fuses.

C.	Control Power Fuses:  Include primary and secondary fuses for fault and overload protection of transformer and control circuits.  Interrupting capability of primary fuses not less than interrupting capability of main circuit breaker.  Provide nameplate with fuse type and rating located at each fuse block.  Fuses NEMA RK-5.

D.	Electrically Interlocked Main and Tie Circuit Breakers:  When required by the drawings, provide two control power transformers in separate compartments with necessary interlocking relays.  Connect the primary of each control power transformer at the line side of the associated main current breaker.  Connect the 120 volt secondaries through a relay or relays as a control bus to effect a fail-safe automatic transfer scheme.

E.	Control Wiring:  Factory-installed, complete with bundling, lacing, and protection.  Switchboard type SIS, stranded copper, with minimum size of #14 AWG (2.5 mm2).

F.	Terminal Blocks:   Number terminal blocks and wires as shown on construction drawings or schedules or as shown on approved shop drawings.  Include at least 20% spare terminals.

G.	Where control wiring is connected to threaded posts, terminate conductors with ring tongue connectors.

2.07	TEST AND INSPECTION EQUIPMENT

If the proposed switchboard incorporates overcurrent protective devices or components not listed in Appendix A to this specification, furnish Sandia National Laboratories with all special tools and test equipment necessary for device test, inspection, maintenance, and operation.

2.08	IDENTIFICATION

A.	General:  Identify units, devices, controls, and wiring with factory-applied labels and signs.

B.	Compartment Nameplates:  Furnish and install nameplates as shown on the drawings or schedules.

2.09	EXTRA MATERIALS

A.	Spare Fuses:  Where the following fuses are furnished with switchboard, include six spares of each type and rating of fuse used.

1.	Potential transformer fuses.

2.	Control Power transformer fuses.

B.	Spare Indicating Lights:  When furnished with switchgear, provide six of each type installed.  Spares are not required for light emitting diodes (LEDs).

C.	Touch-up Paint:  One half-pint net content minimum aerosol can of paint for touch-up

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Thoroughly inspect switchgear to ensure conformance with specifications and approved shop drawings.

B.	Fully document all shipping damage.  Arrange for any necessary repairs as approved by the Sandia Designated Representative.

3.02	INSTALLATION

A.	General:  Install switchboard and accessory items in accordance with the drawings, manufacturers' written installation instructions, NEC required clearances and this section.

B.	Temporary Lifting Provisions:  Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from switchboard units and components.

C.	Operating Instructions:  Frame and mount printed, basic operating instructions for switchboards, including control and key interlocking sequences, and emergency procedures.  Fabricate frame of finished wood or metal and cover instructions with clear acrylic plastic.  For NEMA 1 switchboard, mount on the front of the switchboard.  For NEMA 3R switchboard, mount within the weather doors.

3.03	CLEANING

Upon completion of installation, inspect interior and exterior of switchboards.  Remove paint splatters and other spots, dirt, and debris.  Touch up scratches and mars of finish to match original finish.

3.04	INSPECTION AND TESTING

Sandia National Laboratories, or an independent party hired by Sandia National Laboratories may conduct a complete inspection and test of the switchboard to ensure the equipment and installation conforms to this specification.  Contractor will correct all deficiencies found and a re-test will be performed to verify corrections are acceptable.  Testing will be in accordance with NETA ATS.  A copy of this test check list is attached as Appendix B.

APPENDIX A

APPENDIX B