November 21, 1997

Contract # TW-0928

SPECIAL  SPECIFICATION

SECTION 15462-S

FUEL-FIRED WATER HEATERS

Page

PART 1 - GENERAL

1.01 	Description..	2

1.02	Related Work...	2

1.03	Quality Assurance...	2

1.04	References..	3

1.05	Submittals..	3

1.06 	Delivery, Storage, and Handling..	3

1.07	Warranty..	3

PART 2 - PRODUCTS

2.01	Acceptable Manufacturers..	5

2.02 	Water Heaters, General..	6

2.03 	Commercial, Horizontal-Grid, Finned-Tube, Gas Water Heaters..	6

2.04	Commercial, Storage, Powered, Gas Water Heaters  (Boilers)..	8

2.05	Storage Tanks..	10

PART 3 - EXECUTION

3.01 	Inspection	11

3.02 	Concrete Bases...	11

3.03 	Water Heater Installation..	11

3.04 	Connections..	12

3.05 	Commissioning...	13

3.06 	Demonstration.....	14

MASTERSPEC text, Copyright 1995, AIA, The American Institute of Architects

Paragraph number formatting method, Copyright 1988, ARCOM, Architectural Computer Services, Inc.

SPECIAL SPECIFICATION

SECTION 15462-S

FUEL-FIRED WATER HEATERS

PART 1 - GENERAL

1.01	DESCRIPTION

A.	This Section includes the following:

RETAIN ONLY WATER HEATER CATEGORIES BELOW THAT ARE SPECIFIED.

Gas fired water heaters with integral circulation pumps.

2.	Water heater accessories.

1.02	RELATED WORK

Section 01300-S

Section 15010-S

Section 15051-S

Section 15401-S

1.03	QUALITY ASSURANCE

Comply with provisions of the following:

AGA standards and bear AGA certification label.

NFPA 70, “National Electrical Code,” for electrical components.

Product Options:  Drawings indicate size, profiles, connections, dimensional requirements, and characteristics of water heaters and accessories and are based on specific types and models indicated.  Other manufacturers’ water heaters and accessories with equal performance characteristics may be considered based on Section 15010.

Equipment and system shall perform as specified and noted on drawings for site elevation of 5500 feet elevation above sea level.

1.04	REFERENCES

AGA Standards

NFPA 70

NFPA 54

D.		UL 486A and B

1.05	SUBMITTALS

Make submittals according to this Section, Section 15010-S, and Section 1300-S.

Submit product data including rated capacities of selected models, weights (shipping, installed, and operating), furnished specialties, and accessories.  Indicate dimensions, finishes and coatings, required clearances, methods of assembly of components, and piping and wiring connections.

C.	Maintenance data for water heaters to include in operation and maintenance manuals specified in Division 1.  Include startup instructions.

1.06	DELIVERY, STORAGE, AND HANDLING

DELETE PARA BELOW IF NOT APPLICABLE.

See Section 15010-S.

Store water heaters in a clean, dry location.

Retain shipping protective covers and protective coatings during storage.

RETAIN 1 OF 2 PARAS BELOW IF REQUIRED BY AUTHORITIES HAVING JURISDICTION.  PARAS COMPLY WITH ENERGY POLICY ACT (EPACT).

1.07	WARRANTY

WHEN WARRANTIES ARE REQUIRED, VERIFY WITH THE OWNER'S COUNSEL THAT SPECIAL WARRANTIES STATED IN THIS ARTICLE ARE NOT LESS THAN REMEDIES AVAILABLE TO THE OWNER UNDER PREVAILING LOCAL LAWS.  COORDINATE WITH DIVISION 1 SECTION "WARRANTIES."

A.	General Warranty:  The special warranty specified in this Article shall not deprive SNL of other rights SNL may have under other provisions of Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of Contract Documents.

REFER TO MFR'S PUBLISHED WARRANTIES FOR AVAILABILITY.  EXAMPLE BELOW IS AN EXTENSION FOR COILS, HEAT EXCHANGERS, AND BURNERS.  EDIT AS REQUIRED OR DELETE.

B.	Special Warranty:  Submit a written warranty executed by manufacturer agreeing to repair or replace water heaters and accessories that fail in materials or workmanship within specified warranty period.  Failures include, but are not limited to, tanks, coils, heat exchangers, and burners.  This warranty is in addition to, and not a limitation of, other rights SNL may have against Contractor under Contract Documents.

PARA BELOW IS AN EXAMPLE ONLY.  REVISE WARRANTY TO PERIOD REQUIRED AND VERIFY AVAILABILITY.

C.	Warranty Period:   Minimum 5 years after date of Substantial Completion.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

SEE EDITING INSTRUCTION NO. 1 IN THE EVALUATIONS FOR CAUTIONS ABOUT NAMING PRODUCTS AND MFRS.

A. 	Commercial, Horizontal-Grid, Finned-Tube, Gas Water Heaters:

1.	Lochinvar Corp.

2.	Precision Parts Corp.

3.	Raypak, Inc.

4.	Rheem Mfg. Co.; Rheem Water Heater Div.

5.	Rheem Mfg. Co.; Ruud Water Heater Div.

6.	Smith:  A.O. Smith Water Products Co.

Teledyne Laars.

AERCO

B. 	Commercial, Storage, Powered, Gas Water Heaters / Boilers:

AERCO

Burnham

3.	Precision Parts Corp.

4.	PVI Industries, Inc.

5.	Smith:  A.O. Smith Water Products Co.

C. 	Compression Tanks:

Amtrol, Inc.

Armstrong Pumps, Inc.

Bell & Gossett

Expanflex, Inc.

Smith:  A.O. Smith; Aqua-Air Div.

State Industries, Inc.

D.	Substitutions: only under provisions of Section 1600-S.

2.02	WATER HEATERS  (BOILERS) GENERAL

RETAIN AND EDIT THIS ARTICLE AS REQUIRED TO CORRESPOND TO SPECIFIC WATER HEATER ARTICLES RETAINED BELOW.

SEE EDITING INSTRUCTION NO. 3 IN THE EVALUATIONS FOR CAUTIONS ABOUT SELECTING AND NAMING EQUIVALENT PRODUCTS AND MFRS.  SCHEDULES ON DRAWINGS ARE REQUIRED TO INDICATE CAPACITIES, RECOVERIES, AND SOME CHARACTERISTICS OF WATER HEATERS.

A.	Specified manufacturer's standard components and features are acceptable where specific product requirements are not indicated.  Units shall meet the minimum efficiency requirements of ASHRAE 90.1.

B.	Temperature Control:  Adjustable thermostat, except for units where other 	arrangement is indicated or temperature is regulated by flow-control fitting.

C.	Safety Control:  Automatic, high-temperature-limit cutoff device or system on 	commercial units and where indicated.  Include automatic low-water cutoff device 	or system on commercial units where indicated.

D.	Interior Finish:  Materials that comply with requirements of applicable NSF, 	AWWA, or FDA and EPA regulatory standards for tasteless and odorless, 	potable-water-tank linings.

E.	Tappings:  Factory fabricated of materials compatible with tank.  Include tappings 	for piping connections, relief valves, pressure gage, thermometer, blow down, 	vent, and controls as required and others as indicated.  Attach tappings to tank 	before testing and labeling.  Include tappings and connections as follows:

1.	2-Inch NPS (DN50) and Smaller:  Threaded ends.

2.	  2-1/2-Inch NPS (DN65) and Larger:  Flanged ends.

F.	Insulation:  Fiberglass, polyurethane foam, or manufacturer's standard that is 	suitable for operating temperature and required insulating value.  Include 	insulation material that surrounds entire tank except connections and controls.

G.	Jacket:  Steel, with baked-on enamel finish, except where otherwise specified.

H.	Anode Rods:  Factory installed, magnesium.

I.	Circulation Pump:  Integrally mounted on the water heater package.

2.03	COMMERCIAL, HORIZONTAL-GRID, FINNED-TUBE, GAS WATER HEATERS (WH-2)

SEE EDITING INSTRUCTION NO. 3 IN THE EVALUATIONS FOR CAUTIONS ABOUT SELECTING AND NAMING EQUIVALENT PRODUCTS AND MFRS.

A.	Description:  UL 795, packaged, horizontal-grid, finned-tube, gas water heater 	complying with ANSI Z21.13 and for natural-gas fuel.  Include heater, storage 	tank, circulator, piping, and controls.

B.	Water Heater:  Enclosed, insulated unit with controls.

Construction:  ASME labeled with 160-psig working-pressure rating.

RETAIN 1 OF 3 BELOW.

2.	Heat Exchanger:  Copper, finned tube with bronze or glass-lined, cast-iron 	headers.

3.	Burner:  Manufacturer's standard, for use with grid, finned-tube water heaters 	and natural-gas fuel.

4.	Automatic Ignition:  Intermittent electronic ignition complying with ANSI Z21.20.

5.	Gas Shutoff Valve:  ANSI Z21.15, manually operated.  Furnish for installation 	in piping.

DELETE BELOW IF NOT REQUIRED.

6.	Pressure Regulator:  ANSI Z21.18, factory or field installed, for gas appliances.  Provide regulators with pressure rating, capacity, and pressure differential required for water heater and gas supply.

EDIT OR DELETE FIRST 2 SUBPARAS BELOW AS REQUIRED.  VERIFY AVAILABILITY FOR SELECTED WATER HEATER MODEL.  THESE FEATURES MAY BE INCLUDED IN MFR'S STANDARD MODEL.

7.	Automatic Valve:  ANSI Z21.21, appliance, automatic gas valve.

Automatic Damper:  ANSI Z21.66, gas-fired-appliance, automatic-vent-damper device.

Draft Hood:  Manufacturer's standard draft diverter; comply with ANSI Z21.12.

Pressure Relief Valve:  ASME rated and stamped and complying with ASME PTC 25.3 and ANSI Z21.22.  Include pressure setting less than water heater working-pressure rating.  Furnish for installation in piping.

11.		Combination Temperature and Pressure Relief Valve:  ASME rated and stamped and complying with ASME PTC 25.3 and ANSI Z21.22.  Include relieving capacity at least as great as heat input and pressure setting less than water heater working-pressure rating.

a.	Option:  Separate temperature and pressure relief valves are acceptable 	instead of combination relief valve.

Flow Switch.

Spark Ignition.

C.	Storage Tank:  Insulated; provide anode rods and relief valve.

RETAIN 1 OF 2 BELOW.  NON-ASME-CODE CONSTRUCTION TANKS ARE AVAILABLE.

1.	Construction:  ASME labeled, steel with 160-psig (1100-kPa) working-pressure rating.

2.	Construction:  ASME labeled, steel with 150-psig- (1035-kPa-) minimum 	working-pressure rating.

3.	Combination Temperature and Pressure Relief Valve:  ASME rated and 	stamped and complying with ASME PTC 25.3 and ANSI Z21.22.  Include 	relieving capacity at least as great as heat input and pressure setting less than 	water heater working-pressure rating.  Select relief valve with sensing element 	that extends into tank.

a.		Option:  Separate temperature and pressure relief valves are acceptable 	instead of combination relief valve.

RETAIN RELIEF VALVE BELOW TO PREVENT SIPHONING OF WATER FROM STORAGE TANK AND TO PREVENT COLLAPSE OF COPPER LINING.  DELETE IF NOT REQUIRED.

4.	Vacuum Relief Valve:  Comply with ASME PTC 25.3.  Furnish for 	installation in piping.

D.	Mounting:  Water heater, tank, and accessories factory mounted on skids.

E.	Circulator:  UL 778, all bronze, inline, centrifugal, single-stage, radially split case 	design, with mechanical seals; with 125-psig- minimum working-pressure rating 	and 225 deg F continuous water temperature.

F.	Piping:  Manufacturer's standard copper tubing.

G.	Temperature Control:  Adjustable, storage tank temperature-control fitting and 	flow switch, interlocked with circulator and burner.

H.	Safety Control:  Automatic, high-temperature-limit cutoff; low-water cut-off.

INSERT ADDITIONAL REQUIREMENTS HERE.

2.04	COMMERCIAL, STORAGE, POWERED, GAS WATER HEATERS  (BOILERS)

(B-1 THROUGH  -7, WH-1)

SEE EDITING INSTRUCTION NO. 3 IN THE EVALUATIONS FOR CAUTIONS ABOUT SELECTING AND NAMING EQUIVALENT PRODUCTS AND MFRS.

A.	Description:  UL 795, commercial, storage, powered, gas water heater; with 	capacity more than 40 gal. and natural-gas input more than 75,000 Btuh.

RETAIN 1 OF 2 PARAS BELOW.  NON-ASME-CODE CONSTRUCTION TANKS ARE AVAILABLE.

Storage Tank Construction:  ASME labeled, steel with 150-psig working-pressure 			rating.

C.	Burner:  Powered gas burner for natural-gas fuel, and complying with appropriate 			requirements of UL 795.

D.	Gas Shutoff Valve:  ANSI Z21.15, manually operated.  Furnish for installation in 	piping.

DELETE BELOW IF NOT REQUIRED.

E.	Pressure Regulator:  ANSI Z21.18, factory or field installed, for gas appliances.  	Provide regulators with pressure rating, capacity, and pressure differential 	required for water heater and gas supply.

EDIT OR DELETE FIRST 3 PARAS BELOW AS REQUIRED.  VERIFY AVAILABILITY FOR SELECTED WATER HEATER MODEL.  THESE FEATURES MAY BE INCLUDED IN MFR'S STANDARD MODEL.

F.	Automatic Ignition:  ANSI Z21.20, automatic gas-ignition system and 		components;  spark ignition.

G.	Automatic Valve:  ANSI Z21.21, appliance, automatic gas valve.

H.	Automatic Damper:  ANSI Z21.66, gas-fired-appliance, automatic-vent-damper 	device.

I.	Combination Temperature and Pressure Relief Valve:  ASME rated and stamped 	and complying with ASME PTC 25.3 and ANSI Z21.22.  Include relieving 	capacity at least as great as heat input and pressure setting less than water heater 	working-pressure rating.  Select relief valve with sensing element that extends 	into tank.

1.	Option:  Separate temperature and pressure relief valves are acceptable instead 	of combination relief valve.

RETAIN RELIEF VALVE BELOW TO PREVENT SIPHONING OF WATER FROM WATER HEATER AND TO PREVENT COLLAPSE OF COPPER LINING.  DELETE IF NOT REQUIRED.

J.	Vacuum  Relief Valve:  Comply with ASME PTC 25.3.  Furnish for installation in 	piping.

Exception:  Omit where water heater has integral vacuum relieving device.

K.	Safety:  Automatic hi-temp cut-off; low water cut-off.

Alternate Boiler/Water Heater Package:

Provide a skid-mounted boiler (minimum two boilers to a maximum four boilers per skid)  package with all appurtances integrally mounted including applicable pump.

Each skid-mounted  boiler  package to be independent and pre-tested.

A central controller shall be provided to control all or any combination of boiler packages.  The controller shall be capable of integrating with the Building Energy Management System.

All packages shall be manufactured and provided by the same manufacturer of identical components.

Each boiler package shall have single points of connection for entering water, leaving water, power, and controls.

If individual boiler circulation pumps are not used the contractor shall have the hot water main circulation pump design reviewed by a professional engineer to ensure proper sizing to account for head pressure difrences.

INSERT ADDITIONAL REQUIREMENTS HERE.

2.05	STORAGE TANKS (T-3, -4)

DELETE THIS ARTICLE EXCEPT WHEN SEPARATE COMPRESSION TANKS, NOT SPECIFIED AS PART OF A PACKAGED UNIT, ARE REQUIRED.

A.	Description:  Steel, pressured-rated tanks constructed with welded joints and 	factory-installed, butyl-rubber diaphragm.  Include air precharge to minimum 	system-operating pressure at tank.

RETAIN 1 OF 3 CONSTRUCTION PARAS BELOW.

B.	Construction:  ASME labeled with 150-psig (860-kPa) working-pressure rating.

C.	Interior Finish:  Materials that comply with requirements of applicable NSF, 	AWWA, or FDA and EPA regulatory standards for tasteless and odorless, 	potable-water-tank linings.

INDICATE AIR-PRECHARGE PRESSURE IN SCHEDULE OR ON DRAWINGS.

D.	Accessories:  Include air-charging valve and pressure gage.

PART 3 - EXECUTION

3.01	INSPECTION

Inspect areas and conditions, with Installer present, for compliance with requirements for installation tolerances, housekeeping pads, and other conditions affecting performance of the water heaters.

Inspect rough-in for hydronic, drainage piping, and electrical to verify actual locations of connections prior to installation.

Do not proceed until unsatisfactory conditions have been corrected.

3.02	CONCRETE BASES

COORDINATE SIZES AND LOCATIONS OF CONCRETE BASES.  VERIFY STRUCTURAL REQUIREMENTS WITH STRUCTURAL ENGINEER.

A.	Install concrete bases of dimensions indicated for water heaters and accessories.  Refer to Division 3 Section "Cast-in-Place Concrete" and Division 15 Section "Basic Mechanical Materials and Methods."

3.03	WATER HEATER (BOILER)  INSTALLATION

DELETE "CONCRETE BASES" IN FIRST SENTENCE BELOW WHERE BASES ARE NOT REQUIRED AND INSERT "FLOOR."  EDIT AS REQUIRED FOR WALL- OR SHELF-MOUNTING, POINT-OF-USE WATER HEATERS.

Install concrete bases of dimensions indicated for water heaters and accessories.  Refer to Division 3 and Section 15051 for concrete.

Water Heater Installation

1.	General:  Install water heaters on concrete bases.  Set and connect units according to manufacturer's written instructions.  Install units plumb, level, and firmly anchored in locations indicated.  Maintain manufacturer's recommended clearances.  Install so controls and devices are accessible for service.General:

2.	Anchor water heaters and storage tanks to substrate.

3.	Install seismic restraints as indicated and recommended by manufacturer, and as required in Section 15201.

INSERT SPECIAL REQUIREMENTS FOR SEISMIC RESTRAINTS HERE OR DETAIL ON DRAWINGS.

DELETE BELOW WHEN GAS WATER HEATERS ARE NOT SPECIFIED.

C.		Install and connect gas water heaters according to NFPA 54.

1.	Install gas pressure regulators on gas-burner inlets.

2.	Install vent piping from gas-train pressure regulators and valves to outside of building where required.  Terminate vent piping with brass-screened vent cap fitting.  Do not combine vents except with approval of authorities having jurisdiction.

DELETE BELOW IF OIL-FIRED WATER HEATERS ARE NOT SPECIFIED.

D.	Install temperature and pressure relief valves in top portion of storage water heater 	tanks and hot-water storage tanks.  Use relief valves with sensing elements that 	extend into tanks.  Extend relief valve outlet with water piping in continuous 	downward pitch and discharge to closest floor drain.

DELETE BELOW IF NOT REQUIRED.

E.	Install pressure relief valves in hot-water-outlet piping for water heaters without 	storage.  Extend relief valve outlet with water piping in continuous downward 	pitch and discharge to closest floor drain.

DELETE PARA BELOW IF NOT REQUIRED.

F.	Install vacuum relief valves in cold-water-inlet piping.

G.	Install vacuum relief valves in water heaters and hot-water storage tanks that have 	copper lining.

H.	Install water heater drain piping as indirect waste to spill into open drains or over 	floor drains.  Install hose-end drain valves at low points in water piping for water 	heaters that do not have tank drains.  Refer to Section 15401 for drain valves.

J.	Install thermometers on water heater inlet and outlet piping.  Thermometers are 	specified in Section 15135.

K.	Install pressure gages on water heater piping when and as indicated.  Pressure 	gages are specified in Section 15135.

L.	Install inlet and outlet piping manifolds for multiple water heaters.  Fabricate, 	modify, or arrange manifolds for balanced water flow through water heaters.  	Include throttling valves in outlet manifolds and thermometers in inlet and outlet 	manifolds.

M.	Install piping adjacent to water heaters to allow service and maintenance.

N.	Arrange for field-applied insulation on equipment and piping not furnished with 	factory-applied insulation.

3.04	CONNECTIONS

COORDINATE PIPING AND COMPONENTS WITH SCHEMATICS ON DRAWINGS AND REQUIREMENTS SPECIFIED.

A.	Piping installation requirements are specified in other Division 15 Sections.  	Drawings indicate general arrangement of piping, fittings, and specialties.  The 	following are specific connection requirements:

1.	Connect hot- and cold-water piping to units with shutoff valves and unions.  	Connect hot-water circulating piping to unit with shutoff valve, check valve, 	and union.

2.	Connect gas piping to gas burner with drip leg, tee, shutoff valve, and union; 	minimum size same as inlet connection.  Gas piping is specified in 	Section 	15051-S.

3.	Make connections with dielectric fittings where piping is made of dissimilar 	metals.  Dielectric fittings are specified in Section 15050-S.

B.	Electrical Connections:  Power wiring and disconnect switches are specified in 	Division 16 Sections.  Arrange wiring to allow unit servicing.

C.	Grounding:  Ground equipment.  Tighten electrical connectors and terminals, 	including grounding connections, according to manufacturer's published torque-	tightening values.  Where manufacturer's torque values are not indicated, use 	those specified in UL 486A and UL 486B.

EDIT BELOW AS REQUIRED.  SOME CONDENSING WATER HEATERS MAY REQUIRE SMALLER VENT CONNECTIONS.

D.	Gas, Water Heater Vent Connections:  Connect to vent system.  Include draft 	hoods and diverters where required.  Use vents same size as or larger than water 	heater outlets, but not smaller than indicated, except when smaller vent size has 	been calculated according to National Fuel Gas Code.  Comply with gas utility 	requirements for sizing.  Gas vents are specified in Division 15 Section 	"Breechings, Chimneys, and Stacks."

3.05	COMMISSIONING

DELETE REQUIREMENT FOR "FACTORY-AUTHORIZED SERVICE REPRESENTATIVE" EXCEPT FOR LARGE WATER HEATERS, COMPLEX INSTALLATIONS, OR IF REQUIRED.

Provide labor, material, equipment, etc., required to facilitate the commissioning 	process.  Perform tests and verification procedures required by the 	commissioning process when requested by SNL’s Commissioning Authority and 	directed by the General Contractor’s Test Engineer.

B.	Startup Services:  Engage a factory-authorized service representative to provide 	startup service and to demonstrate and train SNL’s maintenance personnel as 	specified below.

1.	Test and adjust operating and safety controls.  Replace damaged and 	malfunctioning controls and equipment.

2.	Train SNL’s maintenance personnel on procedures and schedules related to 	startup and shutdown, troubleshooting, servicing, and preventive maintenance.

3.	Review data in the operation and maintenance manuals.  Refer to Division 1 	Section "Contract Closeout."

RETAIN SUBPARA ABOVE OR BELOW.

4.	Review data in the operation and maintenance manuals.  Refer to Division 1 	Section "Operation and Maintenance Data."

Schedule training with SDR at least 7 days' advance notice.

Ref. Section 01700 “ Commissioning “.

C.	Perform the following final checks before startup:

DELETE ITEMS BELOW IF NOT REQUIRED.

1.	Fill water heaters with water.

2.	Charge compression tanks with air.

3.	Check that piping system tests are complete.

4.	Check for piping connection leaks.

5.	Check for adequate combustion air.

6.	Check for clear vents and devices.

7.	Check for clear relief valve inlets, outlets, and drain piping.

8.	Check operation of pumps and circulators.

9.	Test operation of safety controls, relief valves, and devices.

D.	Perform the following startup procedures:

1.	Energize electric circuits.

2.	Adjust operating controls.

3.	Adjust hot-water-outlet temperature settings.

3.06	DEMONSTRATION

Provide a factory-authorized service representative supervise start-up of equipment, to demonstrate operation, and to provide a minimum of 4 hours of owner training to train personnel.

END OF SECTION 15462

# Comments

Page: 1

Page: 1