Company Log

Name of Facility

Address of facility

Data Center Energy Efficiency Assessment

Assessor and affiliation

Disclaimer

This report was prepared by Qualified Assessor in the course of performing and energy assessment contracted for and sponsored by Sponsor.  Reproduction or distribution of the whole, or any part, of the contents of this document without written permission of Sponsor is prohibited.  Neither the assessor, Sponsor nor any of its employees make any warranty or representations, expressed or implied, or assume any legal liability or responsibility for the accuracy, completeness, or usefulness of any data, information, method product or process disclosed in this document, or represents that its use will not infringe any privately-owned rights, including, but not limited to, patents, trademarks, or copyrights.

This report uses preliminary information from vendor data and technical references.  The report, by itself, is not intended as a basis for the engineering required to adopt any of the recommendations.  Its intent is to inform the site of potential energy saving opportunities and very rough cost savings.  The purpose of the recommendations and calculations is to determine whether measures warrant further investigation.

Acknowledgments

Authors

Joe Green Engineer  - qualified assessor

The Authors Would Like to Acknowledge the Contributions and 
Assistance of the Following People:

Site staff or others who helped

TABLE OF CONTENTS

1.	Facility Overview	4

2.	Facility Energy Use	4

IT Equipment Loads	4

Data Center Energy End Use	5

3.	Mechanical System Description	5

4.	Electrical System Description	6

5.	Benchmarking	6

Data Center Infrastructure Efficiency (DCiE)	6

6.	OBSERVATIONS	6

7.	rECOMMENDED ENERGY EFFICIENCY MEASURES	6

IT equipment	6

HVAC	7

AppendiCES	8

Executive Summary

Summarize the following:  sponsor, site, contractor, brief description of site, use of DC Pro tools, etc.

A number of energy efficiency opportunities with varying payback periods were identified during the assessment.  Based on an estimated energy cost of $xxxx/kWh, energy cost savings of approximately $xx,xxx/yr are possible through measures that have an average payback period of x.x years and represent approximately x% energy savings.  The table below summarizes the projected economics for the recommended measures:

| Grouped Efficiency Measures | Estimated Installed Cost | Estimated Yearly Energy Savings | Estimated Simple Payback - Years |
| --- | --- | --- | --- |
| Totals | $ | $ | weighted ave. |

Table 1 - Summary of Estimated Savings and Payback Times

Additional high level findings

# Facility Overview

High level description of facility

# Facility Energy Use

The total electrical demand was on average approximately XXX kW with a yearly energy use of approximately X.X GWh/yr.  Approximately XX% of the energy use is related to the servers.  The data center is [stand alone; located in an office building; etc.], it was [not] separately submetered, and the team had to develop the energy usage through a combination of temporary submetering, spot measurements and/or spreadsheet calculations.

## IT Equipment Loads

Summarized in Table 2 below is the average power (kW) for IT equipment

| Data Center Areas | Area (sf) | IT equipment load (kW) | Power Density (W/sf) |
| --- | --- | --- | --- |
| Totals |  |  |  |

Table 2  IT equipment load

## Data Center Energy End Use

The electrical end use breakdown associated with the data center space was determined and is shown in Table 3.

| Data Center End Use | Approximate Area (SF) | Average IT Load (kW) | Power Density (W/SF) |
| --- | --- | --- | --- |
| XXX | x,xxx | xxx | xx |
| XXX | x,xxx | xx | xx |
| TOTALS: | x,xxx | xxx | xx |

Table 3 - Summary of Data Center Electrical End Use

Example Figure 2 –Electrical Breakout by End Use

Replace with actual breakdown

# Mechanical System Description

Figure 3 – HVAC System Schematic

# Electrical System Description

UPS System:

Example Table 4. UPS Electrical Measurements

|  | Units | UPS-A | UPS-B | Combined |
| --- | --- | --- | --- | --- |
| UPS Input | kW | xxx | xxx | xxx |
| UPS Output | kW | xxx | xxx | xxx |
| Losses | kW | xx | xx | xx |
| Efficiency | % | xx | xx | xx |
| Load Factor | % | xx | xx | xx |

Distribution transformers/PDUs:

Lighting:

# Benchmarking

The purpose of this section is to summarize the metrics that were gathered as part of the assessment process and compare them to data from other facilities, where available.

## 5.1	Overall energy Efficiency metrics

The table below indicates the metrics that were collected and the interpretation of their values.

| Metric ID | Metric Name | Unit | Value | Interpretation |
| --- | --- | --- | --- | --- |
| EM.M.1 | DCiE (site energy) (IT energy use / total energy use) | - |  |  |
| EM.M.2 | PUE (Total Power/IT Power) | - |  |  |
| EM.M.3 | HVAC Effectiveness (IT Power /HVAC Power) | - |  |  |
| EM.M.4 | Site Energy Use Intensity | Site BTU/sf-yr |  |  |
| EM.M.5 | Source Energy Use Intensity | Source BTU/sf-yr |  |  |
| EM.M.6 | Purchased Energy Cost Intensity | Energy $/sf-yr |  |  |
| EM.M.7 | Peak Electrical Demand Intensity | Peak W/sf |  |  |

Charts for selected metrics are provided below

Figure 4 - Data Center Infrastructure Efficiency (DCiE)

Figure 4 - Data Center Power Utilization Effectiveness (PUE)

Figure 6 - IT equipment power/HVAC power

## 5.2	Air Management and Air Distribution Metrics

Several server intake and exhaust temperatures were collected from a representative sample of servers in the data center.  In addition, measurements of return and supply air temperatures were taken from all of the CRAC or CRAH units as well as from the perforated tiles.  The goal is to establish an understanding of the air management performance, identify any issues such as potential hot spots.  From these temperature  measurements, the following indices were calculated:

Rack Cooling Index (RCI):

RCI is a dimensionless measure of how effectively the equipment is cooled within a given intake temperature specification (e.g., ASHRAE, NEBS). It provides a measure of the conditions at the high (HI) end and at the low (LO) end of the specified temperature range. RCIHI=100% means that no intake temperature is above the maximum recommended, and RCILO=100% means that no intake temperature is below the minimum recommended. Using ASHRAE Class 1 temperature specification, “poor” conditions are ≤90% whereas “good” conditions are ≥96%. The RCI is assuming the ASHRAE Class 1 recommended intake temperature

Return Temperature Index (RTI):

The Return Temperature Index (RTI) is a dimensionless measure of the actual utilization of the available temperature differential in the equipment room as well as a measure of the level of by-pass air or recirculation air in the data center. 100% is generally the target; >100% ( recirculation air; <100% ( by-pass air.

Supply Heat Index (SHI):

The Supply Heat Index (SHI) is a dimensionless measure of recirculation of hot air into the cold aisles. SHI is a number between 0 and 1, the lower the better. SHI is typically < 0.40. An SHI = 0 means that all inlet temperatures are equal to the supply temperature.

The table below summarizes the metrics.

| Metric ID | Metric Name | Unit | Value | Interpretation |
| --- | --- | --- | --- | --- |
| AM.M.1 | CRAC/CRAH/AHU Temperature Differential | F |  |  |
| AM.M.2 | Average Rack Temperature Rise | F |  |  |
| AM.M.3 | Return Temperature Index (RTI), measure of by-pass air and recirculation air. | % |  |  |
| AM.M.4 | Rack Intake Temperatures | F |  |  |
| AM.M.5 | Rack Cooling Index (RCI), measure of conformance with an intake temperature specification (e.g., ASHRAE, NEBS). | % |  |  |
| AM.M.6 | Supply Heat Index (SHI) | - |  |  |
| AM.M.7 | CRAC/CRAH/AHU Moisture Differential | lbs |  |  |
| AM.M.8 | Airflow Efficiency | W/cfm |  |  |
| AM.M.9 | Ratio of Total System Flow to Total Rack Flow | None |  |  |
| AM.M.10 | System Pressure Drop | in. w.g. |  |  |
| AM.M.11 | Fan motor efficiency | % |  |  |
| AM.M.12 | Econ Utilization Factor | % |  |  |

## 5.3	Cooling Plant Metrics

This section is relevant only if the data center is served by a cooling plant.

The table below summarizes the metrics.

| Metric ID | Metric Name | Unit | Value | Interpretation |
| --- | --- | --- | --- | --- |
| CS.M.1 | Chiller Plant Wire to Water Efficiency | kW/ton |  |  |
| CS.M.2 | Chiller Rated Efficiency at Design | kW/ton NPLV |  |  |
| CS.M.3 | Cooling Tower Design Efficiency | gpm/HP |  |  |
| CS.M.4 | Cooling Tower Design Approach | F |  |  |
| CS.M.5 | Condenser Approach Temperature | F |  |  |
| CS.M.6 | Chilled Water Pumping Efficiency | W/gpm |  |  |
| CS.M.7 | Condenser Water Pumping Efficiency | W/gpm |  |  |
| CS.M.8 | Pump and fan motor efficiency | % |  |  |
| CS.M.9 | Chiller Water-Side Econ Utilization Factor | % |  |  |

Figure 7 – Chilled Water plant and Chiller rated efficiency

## 5.4	Electrical Power Chain Metrics

The UPS system typically represents an efficiency opportunity in most data centers.  In this data center, the UPS was on an average loaded to approximately XX% of its rated capacity.  Since UPS efficiency is higher at higher load factors, loading to 50% total for 2N system or 40% for each module is good from an efficiency point of view.  The efficiency at this load factor was observed to be approximately XX%.  This means that the UPS efficiency is about average for all systems benchmarked at this load factor.

The table below summarizes the metrics that were collected.

| Metric ID | Metric Name | Unit | Value | Interpretation |
| --- | --- | --- | --- | --- |
| ED.M.1 | UPS Load Factor | - |  |  |
| ED.M.2 | UPS System Efficiency | % |  |  |
| ED.M.3 | Transformer Efficiency (upstream UPS system) Efficiency | % |  |  |
| ED.M.4 | PDU (with built-in transformer) System Efficiency | % |  |  |
| ED.M.5 | IT Peak Power Density | W/sf |  |  |
| ED.M.6 | IT Ave Power Density | W/sf |  |  |
| ED.M.7 | IT Peak Power Density (design) | W/sf |  |  |
| ED.M.8 | IT Rack Power Density | kW/rack |  |  |
| ED.M.9 | IT Rack Power Density (design) | kW/rack |  |  |
| ED.M.10 | UPS output voltage | V dc |  |  |
| ED.M.11 | Stand-by Gen Block heater power | W |  |  |

Figure 8 - Measured UPS Efficiency Curves

Figure 9 - UPS Load Factor

Figure 10 - Measured IT Load Density

# Observations

# Recommended Energy Efficiency Measures

The following measures are recommended for further evaluation:

| Recommendations | Cost | Simple payback (years) |
| --- | --- | --- |
| 1. | $XX k | ~Y.Y |
| 2. |  |  |
| 3. |  |  |
| 4. |  |  |
| 5. | $XX k | ~Y.Y |
| 6. | $XX k | ~Y.Y |
| 7. | $XX k | ~Y.Y |
| 8. | $XX k | ~Y.Y |
| 9. | $XXk | ~Y.Y |
| 10. | $XX k | ~Y.Y |
| Total | $XXXk | ~Y.Y “weighted” |

Air Management Measures

HVAC Measures

Electrical Measures

IT Equipment Measures

Commissioning Measures

Additional Measures

In addition to these recommendations, the following strategies are recommended:

- It is recommended that the company management investigate and adopt a "total cost of ownership" approach to their data centers.  Energy costs are already eclipsing the cost of the IT equipment over its life and this will only get worse as energy prices rise.  If actions requiring capital were not taken in the past without regard to the ongoing energy savings, this practice should be reviewed.

- An energy manager should be established with responsibility for monitoring energy performance and tracking improvements over time.    Specific goals (targets) for energy reduction should be implemented along with the commitment for capital expenditures where return on investment warrants.

- If the company operates multiple centers, a mechanism to share best practices should be established.

The pie charts below show the current data center energy breakdown along with the projected energy breakdown after implementation of recommendations (DCiE~0.XX).

Example Figure 8 – Current Facility Performance

Replace with actual chart

Example Figure 9 – Projected Facility Performance replace with actual projections

APPENDICES

APPENDIX - A –Best Practices

APPENDIX – B - DC-Pro Assessment Tool – Inputs & Outputs

APPENDIX - C – Electrical Single Lines

APPENDIX - D – Electrical Power Measurements / Readings

APPENDIX - E – Mechanical Flow Diagram / P&ID’s

APPENDIX - F – Mechanical System Measurements / Readings

APPENDIX - G - Assessment instrumentation

# Text boxes

DRAFT

date

Your center is here

Your center is here

Your center is here

Your Chiller plant efficiency is here

Your Chiller rated efficiency is here

Example your center

Your data center is here

Your data center is here