Project Number: AW-2225

Contract Number:  TW-0839

December 1996

SPECIAL SPECIFICATION

SECTION 05990

STAINLESS STEEL POOL LINER

PART	1 - GENERAL                                                                                                           Page

1.01	Description of Work

1.02	References

1.03	System Description

1.04	Submittals

1.05	Quality Assurance

1.06	Delivery, Storage and Handling

PART 2 - PRODUCTS

2.01	Materials

2.02	Fabrication

PART 3 - EXECUTION

3.01	Examination

3.02	Field Assembly and Installation

SPECIAL SPECIFICATION

SECTION 05990

STAINLESS STEEL POOL LINER

# PART 1 - GENERAL

## 1.01	DESCRIPTION OF WORK

A.	This section includes all material, labor, equipment, temporary protection and finishing for the fabrication and erection of the stainless steel pool liner assembly as indicated on the Drawings, including liner plates, angles, anchors, attachments and bracing connections.

B.	Related Sections:  Refer to the following sections for related work:

- Division 1, Section “Environmental, Safety, and Health Requirements”

- Division 3, Sections “Cast-In-Place Concrete” and “Cast-In-Place Concrete Supplement” for concrete placement and special concrete grout requirements.

- Division 5, Section “Metal Fabrications” for general fabrication requirements.

## 1.02	REFERENCES

A.	American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code Section VIII Rules for Construction of Pressure Vessels, Division 1.

B.	American Society of Testing and Materials (ASTM)

A 167 	Standard Specification for Stainless and Heat-Resisting Chromium-Nickel Steel Plate, Sheet and Strip.

A 276 	Standard Specification for Stainless and Heat-Resisting Steel Bars and Shapes

A 380 	Standard Practice for Cleaning and Descaling Stainless Steel Parts, Equipment, and Systems

E 165 	Standard Recommended Practice for Liquid Penetrant Inspection

C.	American Welding Society (AWS)

C 5.4	Recommended Practices for Stud Welding

D 1.1 	Structural Welding Code-Steel

D 1.3 	Structural Welding Code-Sheet Steel

## 1.03	SYSTEM DESCRIPTION

A.	General:  Provide a corrosion-resistant, watertight stainless steel liner for the pool that accommodates the related plumbing, casket manipulation and grating.

## 1.04	SUBMITTALS

- General:  Submit the following in accordance with Conditions of Contract and Division 1, Section “Descriptive Submittals.”

- Product Data:  Submit product data and manufacturer’s specifications and installation instructions for the following products.  Include laboratory test reports and mill certificates to show compliance with specifications and standards.

- Stainless steel plate

- Stainless steel shapes

- Welding electrodes and studs

- Preweld and postweld cleaning equipment and supplies

- Silica sand for sandblasting operations

- Shop Drawings:  Submit shop drawings, including complete details and schedules for shop fabrication of subassemblies of the pool liner, and details, schedules, procedures and diagrams showing the methods and sequence of field assembly.

- The Contractor must submit any proposed alternate layout for the pool liner assembly that uses plates of different dimensions and/or joint locations that vary from those shown on the drawings to the Sandia Delegated Representative (SDR) for review and approval.

- Submit complete drawings showing the sizes, locations and connections for the internal formwork, shoring and bracing to be used for the pool liner.  Submit calculations supporting the design of the formwork and shoring system, signed and stamped by a Professional Engineer registered in the state of jurisdiction.

- Quality Control:

- Submit qualification documents for each welding procedure.  Documents shall conform to the requirements of AWS  D1.3, Structural Welding Code-Sheet Steel and shall include Procedure Qualification Test Record and Welding Procedure Specification for each welding procedure and Welder and Welding Operator Qualification Test Record for each welder and welding procedure.  These documents shall be signed by an AWS certified inspector.

- Provide certification that all welders to be employed in the work have satisfactorily passed qualification tests for the material and welding procedures used for the pool liner.  The qualification tests shall be administered by an AWS certified welding inspector in accordance with the  applicable provisions of AWS D1.1, Structural Welding Code-Steel, and AWS D1.3, Structural Welding Code-Sheet Steel, within a period of time not to exceed 12 months prior to the welding work.

2. 	Submit test reports conducted on all welded connections of linear joints and of liner attachments.  Include data on the type(s) of test conducted and test results.  Reports must document the locations of every test and retest in such a manner that the location can be readily verified by others.

3. 	Provide certification that the pool liner assembly is watertight and leak free.

- Provide certification that all materials are asbestos-free and lead paint-free.

- Provide certification of liner manufacturer’s experience.

- Provide certification that the completed liner is watertight and leak free.

## 1.05	QUALITY ASSURANCE

- Manufacturer Qualifications:  The manufacturer of the liner shall have a minimum of five years experience in the construction of watertight tanks and/or pressure vessels in accordance with ASME rules end of the use of stainless steel.

- Regulatory Requirements:  Comply with the provisions of the following unless otherwise noted:

- AWS C5.4, Recommended Practices for Stud Welding

- AWS D1.1, Structural Welding Code-Steel

- AWS D1.3, Structural Welding Code-Sheet Steel

- Certification:  Employ an independent testing laboratory acceptable to the SDR to perform inspection of all welded connections, to perform tests, to prepare test reports and to certify that the finished pool liner assembly is watertight and leak free.  Welding inspected shall be certified by AWS.  Nondestructive testing of welds shall be performed by an ASNT level 2 technician.

## 1.06	DELIVERY, STORAGE AND HANDLING

A.	Packing and Shipping:  Deliver materials and assemblies to ensure uninterrupted progress of work.  Pack, brace and handle assemblies in such a manner to prevent distortion of each assembly or it’s parts or contamination by ferrous materials.

B.	Storage and Protection:  Store materials and assemblies to permit easy access for inspection and identification.  Protect liner assemblies and packaged materials from corrosion, contamination and deterioration.

# PART 2 - PRODUCTS

## 2.01	MATERIALS

- Stainless Steel Plates, Sheets and Strips:  AISI Type 304 and conforming to ASTM A167.

- Stainless Steel Bars and Shapes:  AISI Type 304 and conforming to ASTM A276.

- Welding Rods for Stainless Steel:  AWS E308L-15, E308L-16, ER308-15 or ER308-16.

## 2.02	FABRICATION

- General:

1.  The actual methods and procedures selected for the fabrication of the stainless steel pool liner is the contractor’s responsibility provided the result meets this specification.  However, the following is offered as a general guide:

- The pool liner is fabricated as two or more sub-assemblies in the shop including all internal bracing.  The overall size of the sub-assemblies is a function of the shop’s capabilities and transportation and handling considerations.

- The sub-assemblies are then shipped to the site.  At the site, the various sub-assemblies are welded together to form the completed pool liner assembly.

- Following the completion of the pool liner, the field welds are tested for watertightness.

- Notify the SDR prior to the start of any shop fabrication and develop a schedule for in-shop inspections.

- Fabricate the stainless steel pool liner assembly in accordance with ASME Code and as indicated on the final shop drawings.  Provide bracing to prevent deformation of the liner during assembly, transportation and handling.

- Properly mark and match-mark sub-assemblies of the pool liner for field assembly.  Fabricate for a delivery sequence which will expedite field welding and minimize field handling of the sub-assemblies.

- Welded Construction:  Comply with AWS Code for procedures, appearance and quality of welds and of methods used in correcting welding work.  Avoid overheating by limiting electrode size and welding current and/or by welding on a chilled base.

- Pre-weld Cleaning:  Clean the surfaces to be welded and the adjacent surfaces for at least ½ inch (12.7mm) on each side.  These surfaces must be completely cleansed of all hydrocarbon and other contaminants, such as cutting fluids, grease, oil, waxes and primers, by suitable solvents.  Acceptable pre-weld cleaning techniques include the following:

- Stainless steel wire brushes that have not been used for any other purpose;

- Blasting with non-ferrous sand or grit;

- Machining and grinding  using  a suitable tool and chloride-free cutting field; and

- Pickling with 10 to 20 percent nitric acid solution.

- Postweld Cleaning:  Thoroughly remove all welding slag and surface discoloration by stainless steel chipping and wire brushing or mechanical polishing with non-ferrous tools.

- Joint Testing:  Test all welded joints with the liner in its final position, prior to concrete placement, using the dye penetrant (ASTM E 165) or other non-destructive method(s) approved by the SDR.  Certify that the pool liner assembly is completely watertight and leak free.

# PART 3 - EXECUTION

## 3.01	EXAMINATION

- Erector must examine the area and conditions under which the pool liner is to be installed and notify the Contractor in writing of conditions detrimental to the proper and timely completion of the work.  Do not proceed with the work until unsatisfactory conditions have been corrected in a manner acceptable to the Erector.

## 3.02	FIELD ASSEMBLY AND INSTALLATION

- Temporary Shoring and Bracing:  Provide temporary shoring and bracing members as required with connections of sufficient strength to bear imposed loads.  Provide temporary guy lines, shoring and bracing to achieve proper alignment of the liner sub-assemblies as the field welding proceeds.

- Temporary Planking:  Provide temporary planking and working platforms as required by codes, OSHA regulations Section “Environmental, Safety and Health Requirements” and as necessary to effectively complete the work.

- Protect the area around the liner from flooding.  Do not allow surface waters to flow into the site and pump out any accumulations of rainwater promptly.

- Field Installation:

- The methods and procedures used for installing the pool liner and constructing the walls for the pool is the contractor’s responsibility, and the requirements in Sections “Cast-In-Place Concrete” and “Cast-In-Place Concrete Supplement” shall apply.  However, the following procedures are provided as a general guide for installing the liner and placing the concrete for the pool walls.  This procedure assumes the following condition:

- The concrete foundation for the pool is complete, with the dowels projecting upward from the top surface.

- An adequate number of the concrete pads used to support the pool liner assembly have been placed on top of the concrete foundation.

- The pool liner assembly is complete at the site, and has been tested and certified that it is watertight and leak free.

- Assemble the complete pool liner assembly on top of the concrete support pads.  Verify that the liner is in the correct position and elevation, and is adequately supported.  Level and plumb the liner assembly to within the tolerances noted on the drawings.

- Install the reinforcing bars for the pool wall for the first pour.  See Sections “Cast-In-Place Concrete” and “Cast-In-Place Concrete Supplement.”

- Install the external formwork for the first pour.

- Internal formwork:

- The internal bracing for the pool liner shown on the drawings is NOT intended to support the pressures from the concrete during the placement of concrete in the pool wall.  The contractor is responsible for providing adequate forming, shoring, and bracing to ensure the pool liner is NOT deformed during the concrete placement of the pool wall.

- Install the internal formwork, shoring and bracing inside the pool.

- Fill the pool liner with water to a depth of approximately 3 feet from the bottom of the pool.  Verify that there are no leaks through the liner.  Repair as necessary to ensure that there are NO leaks.

- Place the 4 inches of special concrete grout between the top of the concrete foundation and the bottom of the pool liner.  (Refer to Section “Cast-In-Place Concrete Supplement.”)  Place the special concrete grout slowly from one side of the pool only until it has flowed under and completely filled the space between the top of the concrete foundation and the bottom of the pool liner.

- Immediately after placing the special concrete grout under the bottom liner, place a layer of normal weight concrete in the pool wall to a height of 18 inches above the top of the pool foundation.

- Heavily rake all around the top of this pour using the detail shown on the drawings.  Allow the concrete to cure for at least 24 hours.

- At the contractor’s option, the water in the pool may be pumped out at this time.

- Install additional reinforcing bars and external formwork as required, and place the remaining concrete for the pool walls.  Placement rates of about 6 feet per day are typical.

- Remove the formwork and bracing in accordance with Section “Cast-In-Place Concrete.”

- Remove the internal stainless steel bracing and lifting lugs from inside the pool, and grind the welds smooth.

- Pump out the water in the pool if not already done so earlier.

E.	Backfilling:  Do not commence backfilling operations against the pool wall until the strength of the concrete in the pool wall and beams has reached 100% of its specified 28 day strength.

F.	Safety:  Appropriate safety devices and equipment, which meet all OSHA and Section “Environmental, Safety, and Health Requirements,” shall be installed and maintained over and around the pool.  Note that work within the pool may qualify as a confined space.

G.	Cleaning and Passivating:

- All internal bracing and lifting lugs shall be removed and the welds ground smooth.

- Prior to the installation of the elevator equipment, the entire pool liner and welds shall be cleaned and passivated using the sandblasting method in accordance with ASTM A380.

- Either dry or wet sandblasting may be used.

- Provide methods to keep the dust from the sandblasting operations from accumulating on the inside surfaces of the shields.

- Use only silica sand that has been chemically analyzed and found to be iron-free.

- Sandblasting shall remove all contaminates and provide a white metal blast finish with a profile of 1 to 2 mils.

- Protect the cleaned and sandblasted liner from contaminates such as nails, mild steel, or unprotected steel scaffolding.

END OF SECTION