## HRR-Calculations
CHAPTER 3. ESTIMATING BURNING CHARACTERISTICS OF LIQUID POOL FIRE,
HEAT RELEASE RATE, BURNING DURATION, AND FLAME HEIGHT
Version 1805.0
The following calculations estimate the heat release rate, burning duration, and flame height for liquid pool fire.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Fuel Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input
parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cell(s).
The chapter in the NUREG should be read before an analysis is made.
INPUT PARAMETERS
| Fuel Spill Volume (V) |  |  |  | 5 | gallons | 0.018927 | m3
| Fuel Spill Area or Dike Area (Adike) |  |  |  | 9 | ft2 | 0.83613 | m2
| Mass Burning Rate of Fuel (m") |  |  |  | 0.051 | kg/m2-sec
| Effective Heat of Combustion of Fuel (DHc,eff) |  |  |  | 43500 | kJ/kg
| Fuel Density (r) |  |  |  | 760 | kg/m3
| Empirical Constant (kb) |  |  |  | 3.6 | m-1
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F | 25 | °C
[7 empty] | 298 | K
| Gravitational Acceleration (g) |  |  |  | 9.81 | m/sec2
| Ambient Air Density (ra) |  |  |  | 1.1846 | kg/m3
Calculate
Note: Air density will automatically correct with Ambient Air Temperature (Ta) Input
THERMAL PROPERTIES DATA
BURNING RATE DATA FOR LIQUID HYDROCARBON FUELS
Fuel |  | Mass Burning Rate |  | Heat of Combustion |  | Density | Empirical Constant | Select Fuel Type
|  | m" (kg/m2-sec) |  | DHc,eff (kJ/kg) |  | r (kg/m3) | kb (m-1)
Methanol |  | 0.017 |  | 20000 |  | 796 | 100 | Scroll to desired fuel type
Ethanol |  | 0.015 |  | 26800 |  | 794 | 100 | Click on selection
Butane |  | 0.078 |  | 45700 |  | 573 | 2.7
Benzene |  | 0.085 |  | 40100 |  | 874 | 2.7
Hexane |  | 0.074 |  | 44700 |  | 650 | 1.9
Heptane |  | 0.101 |  | 44600 |  | 675 | 1.1
Xylene |  | 0.09 |  | 40800 |  | 870 | 1.4
Acetone |  | 0.041 |  | 25800 |  | 791 | 1.9
Dioxane |  | 0.018 |  | 26200 |  | 1035 | 5.4
Diethy Ether |  | 0.085 |  | 34200 |  | 714 | 0.7
Benzine |  | 0.048 |  | 44700 |  | 740 | 3.6
Gasoline |  | 0.055 |  | 43700 |  | 740 | 2.1
Kerosine |  | 0.039 |  | 43200 |  | 820 | 3.5
Diesel |  | 0.045 |  | 44400 |  | 918 | 2.1
JP-4 |  | 0.051 |  | 43500 |  | 760 | 3.6
JP-5 |  | 0.054 |  | 43000 |  | 810 | 1.6
Transformer Oil, Hydrocarbon |  | 0.039 |  | 46000 |  | 760 | 0.7
561 Silicon Transformer Fluid |  | 0.005 |  | 28100 |  | 960 | 100
Fuel Oil, Heavy |  | 0.035 |  | 39700 |  | 970 | 1.7
Crude Oil |  | 0.0335 |  | 42600 |  | 855 | 2.8
Lube Oil |  | 0.039 |  | 46000 |  | 760 | 0.7
User Specified Value |  | Enter Value |  | Enter Value |  | Enter Value | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-26.
ESTIMATING POOL FIRE HEAT RELEASE RATE
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-25.
Q = m"DHc,eff (1 - e-kb D) Adike
| Where | Q = pool fire heat release rate (kW)
m" = mass burning rate of fuel per unit surface area (kg/m2-sec)
DHc,eff = effective heat of combustion of fuel (kJ/kg)
Af = Adike = surface area of pool fire (area involved in vaporization) (m2)
kb = empirical constant (m-1)
D = diameter of pool fire (diameter involved in vaporization, circular pool is assumed) (m)
Pool Fire Diameter Calculation
| Adike = | pD2/4
| Where | Adike = surface area of pool fire (m2)
D = pool fire diamter (m)
D = √(4Adike/p)
| D = | 1.0318 | m
| Heat Release Rate Calculation |  |  | (Liquids with relatively high flash point, like transformer oil, require
| Q = m"DHc,eff (1-e-kb D) Adike |  |  | localized heating to achieve ignition)
| Q = | 1809.7453 | kW | 1715.3128 | Btu/sec
ESTIMATING POOL FIRE BURNING DURATION
Reference: SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995, Page 3-197.
tb = 4V / pD2n
| Where | tb = burning duration of pool fire (sec)
V = volume of liquid (m3)
D = pool diameter (m)
n = regression rate (m/sec)
Calculation for Regression Rate
| n = | m"/r
| Where | n = regression rate (m/sec)
m" = mass burning rate of fuel (kg/m2-sec)
r = liquid fuel density (kg/m3)
| n = | 6.7105e-05 | m/sec
Burning Duration Calculation
tb = 4V/pD2n
| tb = | 337.3294 | sec | 5.6222 | minutes
Note that a liquid pool fire with a given amount of fuel can burn for long periods of time over small area or for
short periods of time over a large area.
ESTIMATING POOL FIRE FLAME HEIGHT
METHOD OF HESKESTAD
Reference: SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995, Page 2-10.
Hf = 0.235 Q2/5 - 1.02 D
| Where | Hf = pool fire flame height (m)
Q = pool fire heat release rate (kW)
D = pool fire diameter (m)
Pool Fire Flame Height Calculation
Hf = 0.235 Q2/5 - 1.02 D
| Hf = | 3.6695 | m | 12.0389 | ft
METHOD OF THOMAS
Reference: SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995, Page 3-204.
Hf = 42 D (m"/ra √(g D))0.61
| Where | Hf = pool fire flame height (m)
m" = mass burning rate of fuel per unit surface area (kg/m2-sec)
ra = ambient air density (kg/m3)
D = pool fire diameter (m)
g = gravitational acceleration (m/sec2)
Pool Fire Flame Height Calculation
Hf = 42 D (m"/ra √(g D))0.61
| Hf = | 3.1404 | m | 10.3031 | ft
| Calculation Method |  | Flame Height (ft)
| METHOD OF HESKESTAD |  | 12.0389
| METHOD OF THOMAS |  | 10.3031
ESTIMATING POOL FIRE RESULTS FOR RANDOM SIZE SPILLS USING INPUT PARAMETERS
| Area (ft2) | Area (m2) | Diameter (m) | Q (kW) | tb (sec) | Hf (ft) (Heskestad) | Hf (ft) (Thomas)
| 1 | 0.092903 | 0.34393 | 201.0828 | 3035.9642 | 5.2819 | 4.8014
| 2 | 0.18581 | 0.48639 | 402.1656 | 1517.9821 | 6.8605 | 6.1091
| 3 | 0.27871 | 0.5957 | 603.2484 | 1011.9881 | 7.9893 | 7.0335
| 4 | 0.37161 | 0.68786 | 804.3313 | 758.9911 | 8.8983 | 7.7729
| 5 | 0.46452 | 0.76905 | 1005.4141 | 607.1928 | 9.6723 | 8.3996
| 6 | 0.55742 | 0.84245 | 1206.4969 | 505.994 | 10.3531 | 8.949
| 7 | 0.65032 | 0.90995 | 1407.5797 | 433.7092 | 10.965 | 9.4415
| 8 | 0.74322 | 0.97278 | 1608.6625 | 379.4955 | 11.5234 | 9.8899
| 9 | 0.83613 | 1.0318 | 1809.7453 | 337.3294 | 12.0389 | 10.3031
| 10 | 0.92903 | 1.0876 | 2010.8281 | 303.5964 | 12.519 | 10.6873
| 11 | 1.0219 | 1.1407 | 2211.9109 | 275.9967 | 12.9692 | 11.0472
| 12 | 1.1148 | 1.1914 | 2412.9938 | 252.997 | 13.394 | 11.3864
| 13 | 1.2077 | 1.2401 | 2614.0766 | 233.5357 | 13.7967 | 11.7075
| 14 | 1.3006 | 1.2869 | 2815.1594 | 216.8546 | 14.18 | 12.0129
| 15 | 1.3935 | 1.332 | 3016.2422 | 202.3976 | 14.5462 | 12.3044
| 20 | 1.8581 | 1.5381 | 4021.6563 | 151.7982 | 16.1742 | 13.5981
| 25 | 2.3226 | 1.7196 | 5027.0703 | 121.4386 | 17.5572 | 14.6944
| 50 | 4.6452 | 2.432 | 10054.1407 | 60.7193 | 22.6219 | 18.6965
| 75 | 6.9677 | 2.9785 | 15081.211 | 40.4795 | 26.2091 | 21.5255
| 100 | 9.2903 | 3.4393 | 20108.2813 | 30.3596 | 29.079 | 23.7886
Caution! The purpose of this random spill size chart is to aid the user in evaluating the
hazard of random sized spills. Please note that the calculation doe not take into account
the viscosity or volatility of the liquid, or the absorptivity of the surface. The results
generated for small volume spills over large areas should be used with extreme caution.
The above calculations are based on principles developed in the SFPE Handbook of Fire
Protection Engineering, 2nd Edition, 1995.
Calculations are based on certain assumptions and have inherent limitations. The results
of such calculations may or may not have reasonable predictive capabilities for a given
situation, and should only be interpreted by an informed user.
Although each calculation in the spreadsheet has been verified with the results of hand
calculation, there is no absolute guarantee of the accuracy of these calculations.
Any questions, comments, concerns, and suggestions, or to report an error(s) in the
spreadsheets, please send an email to nxi@nrc.gov or mxs3@nrc.gov.
Prepared by: |  | Date |  | Organization
Checked by: |  | Date |  | Organization
Additional Information
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | January 2005
Note on F21: This default value (9.81) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.