Electrical

Systems

Qualification Standard
Reference Guide

October 2006

PURPOSE	1

SCOPE	1

TECHNICAL COMPETENCIES	2

I.	KNOWLEDGE OF ELECTRICAL THEORY & EQUIPMENT	2

1.	Demonstrate a working-level knowledge of electrical and circuit theory, terminology, theorems, laws, and analysis.	2

2.	Electrical systems personnel shall demonstrate a working-level knowledge of basic AC theory.	13

3.	Demonstrate a working-level knowledge of the construction and operation of AC generators, and motors, including operating characteristics, method of torque production, and the advantages of specific motor types).	14

4.	Demonstrate a working-level knowledge of AC reactive components, including inductive and capacitive reactance and phase relationships in reactive circuits.	27

5.	Demonstrate a working-level knowledge of electrical transmission and distribution systems.	30

6.	Demonstrate a working level knowledge of transformers.	44

7.	Demonstrate a working-level knowledge of Uninterruptible Power Supplies (UPS).	48

8.	Demonstrate a working-level knowledge of variable frequency (speed) drives (VFD).	50

9.	Demonstrate a working-level knowledge of electrical test instruments and measuring devices.	52

10.	Demonstrate a familiarity-level knowledge of the principles and concepts of natural phenomena hazards (such as static electricity, reference NFPA 77) and their effect on electrical systems.	56

11.	Demonstrate a working-level knowledge of direct current (DC) generators and motors.	59

12.	Demonstrate a working-level knowledge of battery construction, voltage production, and hazards.  IEEE Std 450. Maintenance, Testing and Replacement of Vented Lead-Acid Batteries for Stationary Applications.	70

II. ELECTRICAL ISSUE IDENTIFICATION & REPORTING	76

1.	Demonstrate a working-level knowledge of surveillance and assessment techniques; reporting; and follow up actions for electrical systems and programmatic elements of an Electrical Safety Program to include:	76

2.	Electrical systems personnel shall demonstrate the ability to communicate (both oral and written) when working or interacting with the contractor, stakeholders, and other internal and external organizations.	81

3.	Become familiar with the ES&H reporting requirements as noted in DOE O 231.1A, Environment, Safety, and Health Reporting.	81

4.	Electrical systems personnel shall demonstrate a working-level knowledge of problem analysis principles and the ability to apply techniques necessary to identify problems, determine potential causes of problems, and identify corrective action(s).	84

III. SAFETY & HEALTH RELATED TO ELECTRICAL SYSTEMS and COMPONENTS	87

1.	Obtain a clear understanding how electrical hazards are addressed via the Integrated Safety Management System process.  Emphasis placed on knowing all applicable site contractor(s) job planning (job hazard analysis, identification and integration of hazard controls within work package), and application of -hazard controls, during the work control process.	87

2.	Obtain a working-level knowledge of Electrical Safety-Related Work Practices (NFPA 70E, Article 110) to include the following:	87

3.	Observe electrical work performed by each site contractor to learn how work is performed within planned controls.  Obtain a working knowledge of site contractor(s) procedure/work control program, and specific work control requirements for each job observed.  The level of rigor of these jobs should allow the candidate to review the functional areas, requirements, and workscope for compliance with NFPA 70E, to include the following:	89

4.	From the jobs observed in Competency 3 above, assess how well contractor management systems (lessons learned and other feedback processes) are integrated with the work planning and ISM process.  Develop a working knowledge of how lessons learned are addressed by each contractor’s Integrated Safety Management System feedback process.  (Reference DOE P 450.4 Safety Management System Policy.)	93

5.	Obtain a working-level knowledge of NFPA 70E, Article 420 requirements, to include:	93

6.	Obtain a working-level knowledge of the DOE Electrical Safety Handbook for safety requirements associated with site R&D operations involving large capacity stored energy, inductor, capacitor and pulsed energy systems to include requirements relating to:	101

7.	Obtain a working-level knowledge of requirements related to safe work practices for laser operations (NFPA 70E, Chapter 3) to include:	104

IV. ELECTRICAL MAINTENANCE MANAGEMENT FOR NUCLEAR AND NON-NUCLAR FACILITIES	108

1.	Become familiar with DOE maintenance management requirements as defined in DOE O 433.1, Maintenance Management Program, and DOE G 433.1-1.	108

2.	Become familiar with NFPA 70B safety requirements for electrical equipment maintenance, to include:	111

3.	Become familiar with the NFPA 70E, Chapter 2, safety-related maintenance requirements relating to:	118

V. ELECTRICAL DESIGN & INSTALLATION (SAFETY AND SYSTEMS)	124

1.	Demonstrate a working-level knowledge of the current national electrical code, and become familiar with the requirements for wiring design and protection (NFPA 70, NFPA 70E, chapter 4) to include:	125

2.	Become familiar with the requirements for the Installation of Lightning Protection Systems (NFPA 780, UL 96 Lightning Protection Components, and UL 96A Installation requirements for Lightning Protection Systems).	129

3.	Demonstrate a working-level knowledge of electrical diagrams, including:	129

4.	Become knowledgeable of the Configuration Management process as applied to electrical documentation, e.g., documenting, controlling, revising, and issuance of electrical drawings.  Also observed how drawings are updated and issued “as built.” (DOE STD 1073, Configuration Management, and DOE O 414.1C Quality)	130

5.	Become familiar with battery installations, maintenance, testing, and replacement as described in NFPA 70E, Chapter 3, IEEE Std-450, and IEEE-C2 National Electrical Safety Code (NESC) to include:	134

6.	Become familiar with ventilation and battery room requirements as cited in NFPA 70E, Chapter 3, IEEE Std-450 and IEEE C2-National Electrical Safety Code (NESC) to include:	135

VI. ELECTRICAL VITAL SAFETY SYSTEMS (VSS)	137

1.	Mandatory Performance Activity: Demonstrate a familiarity-level of knowledge of 10 CFR 830 (Nuclear Safety Management), and DOE O 414.1C that relate to electrical safety programs, processes, and systems, to include:	137

2.	Demonstrate a familiarity-level knowledge of all assigned electrical power vital safety systems, and how they are addressed during the design, construction and operation of nuclear facilities	144

3.	Demonstrate a working-level knowledge of the possible functional interfaces/relationships between all electrical VSS and instrument and control safety software analysis safety software, and design safety software.	146

4.	Document participation with the site contractor system engineer (SE) in a quarterly walkthrough, bi-annual status walkthrough or an assessment for all assigned Electrical VSSs.	149

5.	Demonstrate a familiarity-level knowledge of functional classifications for safety systems and the design expectations associated with electrical systems that carry these functional classifications, as described in DOE O 420.1B, Facility Safety, and its associated guide DOE G 420.1-1.	149

6.	Demonstrate a familiarity-level knowledge of electrical safety systems criteria for VSS (IEEE Stds: 308-2001, 323-2003, 379-2000, 384-1992, and 603-1998; and, DOE O 420.1B and DOE G 420.1-1.)	153

7.	Demonstrate a familiarity-level knowledge of electrical safety design requirements for Emergency, Standby, and UPS systems for VSS (IEEE Stds 387-1984, 650-1990, and 944-1986; and, DOE O 420.1B and DOE G 420.1-1).	160

8.	Demonstrate a familiarity-level knowledge of electrical safety design requirements for VSS Accident Monitoring Instrumentation (IEEE Std 497-2002; and, DOE O 420.1B and DOE G 420.1-1).	167

9.	Demonstrate a familiarity-level knowledge of electrical safety design requirements for VSS Motor Control Centers (MCC) (IEEE Std 649-1991; and, DOE O 420.1B and DOE G 420.1-1).	170

10.	Demonstrate a familiarity-level knowledge of electrical safety design requirements for Digital Computers supporting VSS (IEEE Std 7-4.3.2-2003, Annex E; and, DOE O 420.1B and DOE G 420.1-1).	171

11.	Demonstrate a familiarity-level knowledge of electrical safety design requirements for VSS Protection Systems (IEEE Std 741-1997, and 833-1988; and, DOE O 420.1B and DOE G 420.1-1).	171

12.	Demonstrate a familiarity-level knowledge of electrical safety design requirements for Instrumentation and Control (I&C) Equipment Grounding of VSS (IEEE Std 1050-1996; and, DOE O 420.1B and DOE G 420.1-1).	172

13.	Demonstrate a familiarity-level knowledge of electrical safety design requirements for VSS Motor Operated Valves (IEEE Std 1290-1996; and, DOE O 420.1B and DOE G 420.1-1).	175

Additional Reading Requirements	175

1.	Obtain a clear understanding of electrical safety requirements and practices in the following list of regulatory and consensus standards documents, including the relationship between these documents and which are “enforceable” in your site’s contractors contract.  OSHA (29 CFR 1910 and Subpart S, and 29 CFR 1926 Subparts K and V), NFPA 70E, Standard for Electrical Safety in the Workplace/Maintenance, NFPA-70B, Recommended Practice of Electrical Equipment Maintenance, DOE-HDBK-1092, DOE Electrical Safety Handbook; and 10 CFR 851, Worker Safety and Health Program.	175

2.	Demonstrate a familiarity level knowledge of DOE O 414.1C, Quality Assurance, as it pertains to electrical systems.	178

3.	Demonstrate a familiarity-level of knowledge of DOE O 430.1B, Real Property Asset Management, with regard to life cycle asset management.	184

Selected Bibliography and Suggested Reading	190

# PURPOSE

The purpose of this reference guide is to provide a document that contains the information required for a National Nuclear Security Administration (NNSA) technical employee to successfully complete the Electrical Systems Functional Area Qualification Standard.  In some cases, information essential to meeting the qualification requirements is provided.  Some competency statements require extensive knowledge or skill development.  Reproducing all the required information for those statements in this document is not practical.  In those instances, references are included to guide the candidate to additional resources.

# SCOPE

This reference guide has been developed to address the competency statements in the July 2006 edition of DOE-STD-1170-2006, Electrical Systems Functional Area Qualification Standard.  Competency statements and supporting knowledge and/or skill statements from the qualification standard are shown in contrasting bold type, while the corresponding information associated with each statement is provided below it.  The qualification standard contains 39 competency statements.  Some of the competency statements contain performance-based requirements.  These statements will not be covered in this reference guide.

Every effort has been made to provide the most current information and references available as of November 2006.  However, the candidate is advised to verify the applicability of the information provided.

Please direct your questions or comments related to this document to Mark Alsdorf, at 845-6448.

# TECHNICAL COMPETENCIES

I.	KNOWLEDGE OF ELECTRICAL THEORY & EQUIPMENT

(Each competency statement is a Mandatory Performance Activity (MPA), provided that they are applicable to the candidate’s assigned electrical duties.  For competency statements, reference DOE Electrical Science Fundamentals Handbook 1011 (2-92) as reference source.)

## Demonstrate a working-level knowledge of electrical and circuit theory, terminology, theorems, laws, and analysis.

Explain the basic law of electrostatics.

One of the mysteries of the atom is that the electron and the nucleus attract each other.  This attraction is called electrostatic force, the force that holds the electron in orbit.

Without electrostatic force, the electron, which is traveling at high speed, could not stay in its orbit.  Bodies that attract each other in this way are called charged bodies.  The electron has a negative charge and the nucleus (due to the proton) has a positive charge.

The First Law of Electrostatics

The negative charge of the electron is equal, but opposite to, the positive charge of the proton.  These charges are referred to as electrostatic charges.  In nature, unlike charges (such as electrons and protons) attract each other, and like charges repel each other.  These facts are known as the first law of electrostatics and are sometimes referred to as the law of electrical charges.  This law should be remembered because it is one of the vital concepts in electricity.

Some atoms can lose electrons and others can gain electrons; thus, it is possible to transfer electrons from one object to another.  When this occurs, the equal distribution of negative and positive charges no longer exists.  One object will contain an excess of electrons and become negatively charged, and the other will become deficient in electrons and become positively charged.  The electrons that can move around within an object are said to be free electrons.  The greater the number of these free electrons an object contains, the greater its negative electric charge.  Thus, the electric charge can be used as a measure of electrons.

Reference: DOE-HDBK-1011/1-92, DOE Fundamentals Handbook, Electrical Science, volume 1.

Define the following terms and their relationship in energized circuits:

Resistance

Capacitance

Inductance

Reactance

### Resistance

Resistance is defined as the opposition to current flow.  The amount of opposition to current flow produced by a material depends on the amount of available free electrons it contains and the types of obstacles the electrons encounter as they attempt to move through the material.  Resistance is measured in ohms and is represented by the symbol (R) in equations.  One ohm is defined as that amount of resistance that will limit the current in a conductor to one ampere when the potential difference (voltage) applied to the conductor is one volt.  The shorthand notation for ohm is the Greek letter capital omega (Ω).  If a voltage is applied to a conductor, current flows.  The amount of current flow depends upon the resistance of the conductor.  The lower the resistance, the higher the current flow for a given amount of voltage.  The higher the resistance, the lower the current flow.

### Capacitance

Capacitance is defined as the ability to store an electric charge and is symbolized by the capital letter (C).  Capacitance (C), measured in farads, is equal to the amount of charge (Q) that can be stored in a device or capacitor divided by the voltage (E) applied across the device or capacitor plates when the charge was stored.

### Inductance

Inductance is defined as the ability of a coil to store energy, induce a voltage in itself, and oppose changes in current flowing through it.  The symbol used to indicate inductance in electrical formulas and equations is a capital (L).  The units of measurement are called henries.  The unit henry is abbreviated by using the capital letter (H).  One henry is the amount of inductance (L) that permits one volt to be induced (VL) when the current through the coil changes at a rate of one ampere per second.

### Reactance

In an inductive alternating circuit, the current is continually changing and is continuously inducing an electromotive force (EMF).  Because this EMF opposes the continuous change in the flowing current, its effect is measured in ohms.  This opposition of the inductance to the flow of an alternating current (AC) is called inductive reactance (XL).

Reference: DOE-HDBK-1011/1-92, DOE Fundamentals Handbook, Electrical Science, volume 1.

Explain the following fundamental laws of circuit analysis:

Ohm’s law

Kirchoff’s laws

### Ohm’s Law

In 1827, George Simon Ohm discovered that there was a definite relationship between voltage, current, and resistance in an electrical circuit.  Ohm’s law defines this relationship and can be stated in three ways.

Applied voltage equals circuit current times the circuit resistance.  This is represented by the equation:

E = I x R or E = IR

Current is equal to the applied voltage divided by the circuit resistance.  This is represented by the equation:

I =

Resistance of a circuit is equal to the applied voltage divided by the circuit current.

R or Ω=

where

I = current (A)

E = voltage (V)

R = resistance (Ω)

If any two of the component values are known, the third can be calculated.

### Kirchoff’s Laws

Ohm’s law describes the relationship between current, voltage, and resistance.  It can be applied to circuits that are relatively simple in nature.  However, many circuits are extremely complex and cannot be solved with Ohm’s Law.  These circuits have many power sources and branches that would make the use of Ohm’s Law impractical or impossible.

Through experimentation in 1857, the German physicist Gustav Kirchhoff developed methods to solve complex circuits.  Kirchhoff developed two conclusions, known today as Kirchhoff’s Laws.

Law 1: The sum of the voltage drops around a closed loop is equal to the sum of the voltage sources of that loop (Kirchhoff’s Voltage Law).

Law 2: The current arriving at any junction point in a circuit is equal to the current leaving that junction (Kirchhoff’s Current Law).

Kirchoff’s laws are powerful tools in solving complex and difficult circuits.  Kirchhoff’s laws can be related to conservation of energy and charge if we look at a circuit with one load and source.  Since all of the power provided from the source is consumed by the load, energy and charge are conserved.  Since voltage and current can be related to energy and charge, then Kirchhoff’s laws are only restating the laws governing energy and charge conservation.

Reference: DOE-HDBK-1011/1-92, DOE Fundamentals Handbook, Electrical Science, volume 1.

Explain the use of the following theorems in network analysis and describe their application in circuit reduction techniques:

Thevenin's theorem

Norton's theorem

Maximum power transfer theorem

Superposition theorem

### Thevenin’s Theorem

Thevenin’s theorem states that it is possible to simplify any linear circuit, no matter how complex, to an equivalent circuit with just a single voltage source and series resistance connected to a load.  For a circuit to qualify as linear, all the underlying equations must be linear (no exponents or roots).  If we are dealing with passive components such as resistors, inductors, and capacitors, this is true.  However, there are some components that are nonlinear: that is, their opposition to current changes with voltage and/or current.  We would call circuits containing these types of components nonlinear circuits.

Thevenin’s theorem is especially useful in analyzing power systems and other circuits where one particular resistor in the circuit, called the load resistor, is subject to change, and re-calculation of the circuit is necessary with each trial value of load resistance to determine voltage across the resistor and current through it.

### Norton’s Theorem

Norton’s Theorem states that it is possible to simplify any linear circuit, no matter how complex, to an equivalent circuit with just a single current source and parallel resistance connected to a load.  Just as with Thevenin’s theorem, for a circuit to qualify as linear, all underlying equations must be linear (no exponents or roots).

### Maximum Power Transfer Theorem

The maximum power transfer theorem is an aid to system design.  A load resistance will dissipate the maximum amount of power when that load resistance is equal to the Thevenin/Norton resistance of the network supplying the power.  If the load resistance is lower or higher than the Thevenin/Norton resistance of the source network, its dissipated power will be less than maximum.

This is essentially what is aimed for in stereo system design, where speaker impedance is matched to amplifier impedance for maximum sound power output.  Impedance, the overall opposition to AC and direct current (DC), is very similar to resistance, and must be equal between source and load for the greatest amount of power to be transferred to the load.  A load impedance that is too high will result in low-power output.  A load impedance that is too low will not only result in low-power output, but possibly overheating of the amplifier due to the power dissipated in its internal impedance.

### Superposition Theorem

The superposition theorem takes a complex subject and simplifies it.  The strategy used in the superposition theorem is to eliminate all but one source of power within a network at a time, using series/parallel analysis to determine voltage drops (and/or currents) within the modified network for each power source separately.  Then, once voltage drops and/or currents have been determined for each power source working separately, the values are all superimposed on top of each other (added algebraically) to find the actual voltage drops/currents with all sources active.

Additional information regarding these theorems is available at http://www.allaboutcircuits.com/vol_1/chpt_10/8.html.

Discuss the fundamental relationships in DC circuits among voltage, current, resistance, and power.

### Voltage

Voltage, EMF, or potential difference, is described as the pressure or force that causes electrons to move in a conductor.  In electrical formulas and equations, you will see voltage symbolized by a capital (E), while on laboratory equipment or schematic diagrams, the voltage is often symbolized by a capital (V).

### Current

Electron current, or amperage, is described as the movement of free electrons through a conductor.  In electrical formulas, current is symbolized by a capital (I), while in the laboratory or on schematic diagrams, it is common to use a capital (A) to indicate amps or amperage.

### Resistance

Resistance is defined as the opposition to current flow.  The amount of opposition to current flow produced by a material depends on the amount of available free electrons it contains and the types of obstacles the electrons encounter as they attempt to move through the material.  Resistance is measured in ohms and is symbolized by a capital (R) in equations.  One ohm is defined as that amount of resistance that will limit the current in a conductor to one ampere when the potential difference (voltage) applied to the conductor is one volt.  The shorthand notation for ohm is the Greek letter capital omega (Ω).  If a voltage is applied to a conductor, current flows.  The amount of current flow depends upon the resistance of the conductor.  The lower the resistance, the higher the current flow for a given amount of voltage.  The higher the resistance, the lower the current flow.

### Power

Electricity is generally used to do some sort of work, such as turning a motor or generating heat.  Specifically, power is the rate at which work is done, or the rate at which heat is generated.  The unit commonly used to specify electric power is the watt.  In equations, you will find power symbolized by the capital letter (P), and watts, the units of measure for power, are symbolized by the capital letter (W).  Power is also described as the current (I) in a circuit times the voltage (E) across the circuit.

Reference: DOE-HDBK-1011/1-92, DOE Fundamentals Handbook, Electrical Science, volume 1.

Explain the treatment of inductance and capacitance values in steady-state DC circuits.

When an inductor has a DC current flowing through it, the inductor will store energy in the form of a magnetic field.  An inductor will oppose a change in current flow by the counter electromotive force (CEMF) induced when the field collapses or expands.  Inductors in series are combined like resistors in series.  Inductors in parallel are combined like resistors in parallel.  The time constant for an inductor is defined as the required time for the current either to increase to 63.2 percent of its maximum value or to decrease by 63.2 percent of its maximum value.

A capacitor is constructed of two conductors (plates) separated by a dielectric.  A capacitor will store energy in the form of an electric field caused by the attraction of the positively-charged particles in one plate to the negatively charged particles in the other plate.  The attraction of charges in the opposite plates of a capacitor opposes a change in voltage across the capacitor.  Capacitors in series are combined like resistors in parallel.  Capacitors in parallel are combined like resistors in series.  The capacitive time constant is the time required for the capacitor to charge (or discharge) to 63.2 percent of its fully charged voltage.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, volume 2.

Discuss the fundamental relationships in AC circuits among voltage, current, resistance, reactance, impedance, power, and power factor.

In an inductive AC circuit, the current is continually changing and is continuously inducing an EMF.  Because this EMF opposes the continuous change in the flowing current, its effect is measured in ohms.  This opposition of the inductance to the flow of an alternating current is called inductive reactance (XL).

The magnitude of an induced EMF in a circuit depends on how fast the flux that links the circuit is changing.  In the case of self-induced EMF such as in a coil, a CEMF is induced in the coil due to a change in current and flux in the coil.  This CEMF opposes any change in current, and its value at any time will depend on the rate at which the current and flux are changing at that time.  In a purely inductive circuit, the resistance is negligible in comparison to the inductive reactance.  The voltage applied to the circuit must always be equal and opposite to the EMF of self-induction.

Any change in current in a coil causes a corresponding change of the magnetic flux around the coil.  Because the current changes at its maximum rate when it is going through its zero value at 90° (point b on figure 1) and 270° (point d), the flux change is also the greatest at those times.  Consequently, the self-induced EMF in the coil is at its maximum (or minimum) value at these points as shown in figure 1.  Because the current is not changing at the point when it is going through its peak value at 0° (point a), 180° (point c), and 360° (point e) the flux change is zero at those times.  Therefore, the self-induced EMF in the coil is at its zero value at these points.

Figure 1-Current, self-induced EMF, and applied voltage in an inductive circuit

According to Lenz’s Law, the induced voltage always opposes the change in current.  Referring to figure 1, with the current at its maximum negative value (point a), the induced EMF is at a zero value and falling.  Thus, when the current rises in a positive direction (point a to point c), the induced EMF is of opposite polarity to the applied voltage and opposes the rise in current.  Notice that as the current passes through its zero value (point b) the induced voltage reaches its maximum negative value.  With the current now at its maximum positive value (point c), the induced EMF is at a zero value and rising.  As the current is falling toward its zero value at 180° (point c to point d), the induced EMF is of the same polarity as the current and tends to keep the current from falling.  When the current reaches a zero value, the induced EMF is at its maximum positive value.  Later, when the current is increasing from zero to its maximum negative value at 360° (point d to point e), the induced voltage is of the opposite polarity as the current and tends to keep the current from increasing in the negative direction.  The value of the self-induced EMF varies as a sine wave and lags the current by 90°, as shown in figure 1.  The applied voltage must be equal and opposite to the self-induced EMF at all times; therefore, the current lags the applied voltage by 90° in a purely inductive circuit.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3.

Describe how the following methods produce a voltage:

Electrochemistry

Static electricity

Magnetic induction

Piezoelectric effect

Thermoelectricity

Photoelectric effect

### Electrochemistry

Chemicals can be combined with certain metals to cause a chemical reaction that will transfer electrons to produce electrical energy.  This process works on the electrochemistry principle.  A chemical reaction produces and maintains opposite charges on two dissimilar metals that serve as the positive and negative terminals.  The metals are in contact with an electrolyte solution.  Connecting together more than one of these cells will produce a battery.

### Static Electricity

Atoms with the proper number of electrons in orbit around them are in a neutral state, or have a zero charge.  A body of matter consisting of these atoms will neither attract nor repel other matter that is in its vicinity.  If electrons are removed from the atoms in this body of matter, as happens due to friction when one rubs a glass rod with a silk cloth, it will become electrically positive.  If this body of matter (e.g., the glass rod) comes near, but not in contact with, another body having a normal charge, an electric force is exerted between them because of their unequal charges.  The existence of this force is referred to as static electricity or electrostatic force.

### Magnetic Induction

Magnetic induction is used to produce a voltage by rotating coils of wire through a stationary magnetic field, or by rotating a magnetic field through stationary coils of wire.  This is one of the most useful and widely employed applications of producing vast quantities of electric power.

### Piezoelectric Effect

By applying pressure to certain crystals (such as quartz or Rochelle salts) or certain ceramics (like barium titanate), electrons can be driven out of orbit in the direction of the force.  Electrons leave one side of the material and accumulate on the other side, building up positive and negative charges on opposite sides.  When the pressure is released, the electrons return to their orbits.  Some materials will react to bending pressure, while others will respond to twisting pressure.  This generation of voltage is known as the piezoelectric effect.

### Thermoelectricity

Some materials readily give up their electrons and others readily accept electrons.  For example, when two dissimilar metals like copper and zinc are joined together, a transfer of electrons can take place.  Electrons will leave the copper atoms and enter the zinc atoms.  The zinc gets a surplus of electrons and becomes negatively charged.  The copper loses electrons and takes on a positive charge.  This creates a voltage potential across the junction of the two metals.  The heat energy of normal room temperature is enough to make them release and gain electrons, causing a measurable voltage potential.  As more heat energy is applied to the junction, more electrons are released, and the voltage potential becomes greater.  When heat is removed and the junction cools, the charges will dissipate and the voltage potential will decrease.  This process is called thermoelectricity.

### Photoelectric Effect

Light is a form of energy and is considered by many scientists to consist of small particles of energy called photons.  When the photons in a light beam strike the surface of a material, they release their energy and transfer it to the atomic electrons of the material.  This energy transfer may dislodge electrons from their orbits around the surface of the material.  Upon losing electrons, the photosensitive (light sensitive) material becomes positively charged and an electric force is created.  This process is called the photoelectric effect.

Reference: DOE-HDBK-1011/1-92, DOE Fundamentals Handbook, Electrical Science, volume 1.

Using appropriate data, calculate the total resistance for a circuit containing combinations of parallel and series resistance.

The easiest way to solve these types of circuits is to do it in steps.

Figure 2-Redrawn Circuit Example

Step 1: Find the equivalent resistance of the parallel branch:

Rp =  =  =  = 4Ω

Step 2: Find the resistance of the equivalent series circuit:

RT = R1 + RP = 4Ω + 4 Ω = 8 Ω

Step 3: Find total current (IT):

IT =  =  = 7.5 amps

Step 4: Find I2 and I3.  The voltage across R1 and R2 is equal to the applied voltage (V), minus the voltage drop across R1.

V2 = V3 = V - ITR1 = 60 - (7.5 X 4) = 30 V

Then, I2 and I3 are calculated.

I2 =  =  = 5 amps

I3 =  =  = 2.5 amps

Reference: DOE-HDBK-1011/1-92, DOE Fundamentals Handbook, Electrical Science, volume 1

Using appropriate data for a circuit, calculate the reactance of that circuit.

#### Inductive Reactance

In an inductive AC circuit, the current is continually changing and is continuously inducing an EMF.  Because this EMF opposes the continuous change in the flowing current, its effect is measured in ohms.  This opposition of the inductance to the flow of an alternating current is called inductive reactance (XL).  The mathematical representation of the current flowing in a circuit that contains only inductive reactance is:

I =

where

I = effective current (A)

XL = inductive reactance (W)

E = effective voltage across the reactance (V)

The value of XL in any circuit is dependent on the inductance of the circuit and on the rate at which the current is changing through the circuit.  This rate of change depends on the frequency of the applied voltage.  The mathematical representation for XL is:

XL = 2πf

where

π = ~3.14

f = frequency (Hertz)

L = inductance (Henries)

The magnitude of an induced EMF in a circuit depends on how fast the flux that links the circuits changing.  In the case of self-induced EMF (such as in a coil), a counter EMF is induced in the coil due to a change in current and flux in the coil.  This CEMF opposes any change in current, and its value at any time will depend on the rate at which the current and flux are changing at that time.  In a purely inductive circuit, the resistance is negligible in comparison to the inductive reactance.  The voltage applied to the circuit must always be equal and opposite to the EMF of self-induction.

#### Capacitive Reactance

Capacitive reactance is the opposition by a capacitor or a capacitive circuit to the flow of current.  The current flowing in a capacitive circuit is directly proportional to the capacitance and to the rate at which the applied voltage is changing.  The rate at which the applied voltage is changing is determined by the frequency of the supply; therefore, if the frequency of the capacitance of a given circuit is increased, the current flow will increase.  It can also be said that if the frequency or capacitance is increased, the opposition to current flow decreases; therefore, capacitive reactance, which is the opposition to current flow, is inversely proportional to frequency and capacitance.  Capacitive reactance XC, is measured in ohms, as is inductive reactance.  A mathematical representation for capacitive reactancies:

XC =

where

f = frequency (Hz)

π = ~3.14

C = capacitance (farads)

The following equation is the mathematical representation of capacitive reactance when capacitance is expressed in microfarads (μF).

XC =

The following equation is the mathematical representation for the current that flows in a circuit with only capacitive reactance.

I=

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3.

Note:  Competencies “i” and “j” are performance-based competencies.  The qualifying official will evaluate the completion of these competencies.

## Electrical systems personnel shall demonstrate a working-level knowledge of basic AC theory.

- Define the effective value of an AC relative to DC.

The effective value of AC is the amount of AC that produces the same heating effect as an equal amount of DC.  One-ampere effective value of AC will produce the same amount of heat in a conductor, in a given time, as one ampere of DC.

Describe the relationship between maximum, average, and root-mean-square (RMS) values of voltage and current in an AC waveform.

The relationship between maximum, average, and RMS values of voltage and current in an alternating current waveform are

peak value = average value x 1.57

peak value = effective value (RMS) x 1.414

average value = peak value x 0.637

average value = effective (RMS) x 0.9

effective value (RMS) = average value x 1.11

effective value (RMS) = peak value x 0.707

Using a diagram of two sine waves, describe the phase relationship between the two waves.

The phase difference can be used to describe two different voltages that have the same frequency, which pass through zero values in the same direction at different times.

In figure 3, the angles along the axis indicate the phases of voltages e1 and e2 at any point in time.  At 120°, e1 passes through the zero value, which is 60° ahead of e2 (e2 equals zero at 180°).  The voltage e1 is said to lead e2 by 60 electrical degrees, or it can be said that e2 lags e1 by 60 electrical degrees.

Figure 3-Phase relationship

Phase difference is also used to compare two different currents or a current and a voltage.  If the phase difference between two currents, two voltages, or a voltage and a current is zero degrees, they are said to be in-phase.  If the phase difference is an amount other than zero, they are said to be out-of-phase.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3.

## Demonstrate a working-level knowledge of the construction and operation of AC generators, and motors, including operating characteristics, method of torque production, and the advantages of specific motor types).

Generators

- Describe the basic construction and operation of a simple AC generator.

A simple AC generator consists of a strong magnetic field, conductors that rotate through that magnetic field, and a means by which a continuous connection is provided to the conductors as they are rotating.  The strong magnetic field is produced by a current flow through the field coil of the rotor.  The field coil in the rotor receives excitation through the use of slip rings and brushes.  Two brushes are spring-held in contact with the slip rings to provide the continuous connection between the field coil and the external excitation circuit.  The armature is contained within the windings of the stator and is connected to the output.  Each time the rotor makes one complete revolution, one complete cycle of AC is developed.  A generator has many turns of wire wound into the slots of the rotor.

The magnitude of AC voltage generated by an AC generator is dependent on the field strength and speed of the rotor.  Most generators are operated at a constant speed; therefore, the generated voltage depends on field excitation, or strength.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Describe the development of a sine-wave output in an AC generator.

The elementary AC generator consists of a conductor, or loop of wire, in a magnetic field that is produced by an electromagnet.  The two ends of the loop are connected to slip rings, and they are in contact with two brushes.  When the loop rotates, it cuts magnetic lines of force, first in one direction, and then the other.

At the instant the loop is in the vertical position, the coil sides are moving parallel to the field and do not cut magnetic lines of force.  In this instant, there is no voltage induced in the loop.  As the coil rotates in a counter-clockwise direction, the coil sides will cut the magnetic lines of force in opposite directions.  The direction of the induced voltages depends on the direction of movement of the coil.

Figure 4-Simple AC generator

The induced voltages add in series, making slip ring (X) (in figure 4) positive (+) and slip ring (Y) negative (-).  The potential across resistor (R) will cause a current to flow from (Y) to (X) through the resistor.  This current will increase until it reaches a maximum value when the coil is horizontal to the magnetic lines of force.  The horizontal coil is moving perpendicular to the field and is cutting the greatest number of magnetic lines of force.  As the coil continues to turn, the voltage and current induced decrease until they reach zero, where the coil is again in the vertical position (figure 5).  In the other half revolution, an equal voltage is produced, but the polarity is reversed (figure 5).  The current flow through (R) is now from (X) to (Y) (figure 4).

Figure 5-Developing a sine wave voltage

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Define the following terms in relation to AC generation:

Radians/second

Hertz

Period

A radian is an angle that subtends an arc equal to the radius of a circle.  One radian equals 57.3º.  Radians/second are units of angular velocity.  The time it takes for the generator to complete one cycle is called the period, and the number of cycles per second is called the frequency, which is measured in hertz (Hz).

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Using the type and application of an AC generator, describe the operating characteristics of that generator, including methods of voltage production, advantages of each type, and methods for paralleling.

Note:  This is a performance-based requirement.  A qualifying official will evaluate the completion of this competency.

State the purpose of the following components of an AC generator:

Field

Armature

Prime mover

Rotor

Stator

Slip rings

### Field

The field in an AC generator consists of coils of conductors within the generator that receive a voltage from a source (called excitation) and produce a magnetic flux.  The magnetic flux in the field cuts the armature to produce a voltage.  This voltage is ultimately the output voltage of the AC generator.

### Armature

The armature is the part of an AC generator in which voltage is produced.  This component consists of many coils of wire that are large enough to carry the full-load current of the generator.

### Prime Mover

The prime mover is the component that is used to drive the AC generator.  The prime mover may be any type of rotating machine, such as a diesel engine, a steam turbine, or a motor.

### Rotor

The rotor of an AC generator is the rotating component of the generator.  The rotor is driven by the generator’s prime mover, which may be a steam turbine, gas turbine, or diesel engine.  Depending on the type of generator, this component may be the armature or the field.  The rotor will be the armature if the voltage output is generated there; the rotor will be the field if the field excitation is applied there.

### Stator

The stator of an AC generator is the part that is stationary.  Like the rotor, this component may be the armature or the field, depending on the type of generator.  The stator will be the armature if the voltage output is generated there; the stator will be the field if the field excitation is applied there.

### Slip Rings

Slip rings are electrical connections that are used to transfer power to and from the rotor of an AC generator.  The slip ring consists of a circular conducting material that is connected to the rotor windings and insulated from the shaft.  Brushes ride on the slip ring as the rotor rotates.  The electrical connection to the rotor is made by connections to the brushes.  Slip rings are used in AC generators because the desired output of the generator is a sine wave.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Using the speed of rotation and number of poles, calculate the frequency output of an AC generator.

The frequency of the generated voltage is dependent on the number of field poles and the speed at which the generator is operated, as indicated in the equation below.

f =

where
f = frequency (Hz)
P = total number of poles

N = rotor speed (rpm)

120 = conversion from minutes to seconds and from poles to pole pairs

The 120 in the equation is derived by multiplying the following conversion factors.

X

In this manner, the units of frequency (Hz or cycles/sec.) are derived.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

List the three losses found in an AC generator.

The load current flows through the armature in all AC generators.  Like any coil, the armature has some amount of resistance and inductive reactance.  The combination of these makes up what is known as the internal resistance, which causes a loss in an AC generator.  When the load current flows, a voltage drop is developed across the internal resistance.  This voltage drop subtracts from the output voltage and, therefore, represents generated voltage and power that is lost and not available to the load.

Hysteresis losses occur when iron cores in an AC generator are subject to effects from a magnetic field.  The magnetic domains of the cores are held in alignment with the field in varying numbers, dependent upon field strength.  The magnetic domains rotate, with respect to the domains not held in alignment, one complete turn during each rotation of the rotor.  This rotation of magnetic domains in the iron causes friction and heat.  The heat produced by this friction is called magnetic hysteresis loss.

To reduce hysteresis losses, most AC armatures are constructed of heat-treated silicon steel, which has an inherently low hysteresis loss.  After the heat-treated silicon steel is formed to the desired shape, the laminations are heated to a dull red and then allowed to cool.  This process, known as annealing, reduces hysteresis losses to a very low value.

Rotational or mechanical losses can be caused by bearing friction, brush friction on the commutator, and air friction (called windage), which is caused by the air turbulence due to armature rotation.  Careful maintenance can be instrumental in keeping bearing friction to a minimum.  Clean bearings and proper lubrication are essential to the reduction of bearing friction.  Brush friction is reduced by ensuring: proper brush seating, proper brush use, and maintenance of proper brush tension.  A smooth and clean commutator also aids in the reduction of brush friction.  In very large generators, hydrogen is used within the generator for cooling as it is less dense than air and causes fewer windage losses.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Given the prime mover input and generator output, determine the efficiency of an AC generator.

Efficiency of an AC generator is the ratio of the useful power output to the total power input.  Because any mechanical process experiences some losses, no AC generators can be 100 percent efficient.  Efficiency of an AC generator can be calculated using the following equation.

X 100

Example:	Given a 5 horsepower (hp) motor acting as the prime mover of a generator that has a load demand of 2 kilowatts (kW), what is the efficiency of the generator?

Solution:	To calculate efficiency, the input, and output power must be in the same units.  We know that horsepower and the watt (W) are equivalent units of power.  Therefore, the equivalence of these units is expressed with a conversion factor as follows.

Input power = 5 hp x 746  = 3730 W

Output power = 2 kW = 2000 W

=  = 0.54 X 100 = 54%

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Describe the basis for the kilowatt and kilovolt-amperes ratings of an AC generator.

The kilowatt (power) ratings of an AC generator are based on the ability of the prime mover to overcome generator losses and the ability of the machine to dissipate the internally generated heat.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Describe the conditions that must be met prior to paralleling two AC generators, including consequences of not meeting these conditions.

Most electrical power grids and distribution systems have more than one AC generator operating at one time.  Normally, two or more generators are operated in parallel to increase the available power.  Three conditions must be met prior to paralleling (or synchronizing) AC generators.

Their terminal voltages must be equal.  If the voltages of the two AC generators are not equal, one of the AC generators could be picked up as a reactive load to the other AC generator.  This causes high currents to be exchanged between the two machines, possibly causing generator or distribution system damage.

Their frequencies must be equal.  A mismatch in frequencies of the two AC generators will cause the generator with the lower frequency to be picked up as a load on the other generator (a condition referred to as motoring).  This can cause an overload in the generators and the distribution system.

Their output voltages must be in phase.  A mismatch in the phases will cause large opposing voltages to be developed.  The worst-case mismatch would be 180° out of phase, resulting in an opposing voltage between the two generators of twice the output voltage.  This high voltage can cause damage to the generators and distribution system due to high currents.

During paralleling operations, voltages of the two generators that are to be paralleled are indicated through the use of voltmeters.  Frequency matching is accomplished through the use of output frequency meters.  Phase matching is accomplished through the use of a synchroscope, which is a device that senses the two frequencies and gives an indication of phase differences and a relative comparison of frequency differences.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Describe the difference between a stationary field, rotating armature AC generator, and a rotating field, stationary armature AC generator.

Small AC generators usually have a stationary field and a rotating armature.  One important disadvantage to this arrangement is that the slip ring and brush assembly is in series with the load circuits and, because of worn or dirty components, may interrupt the flow of current.

If the DC field excitation is connected to the rotor, the stationary coils will have AC induced into them.  This arrangement is called a rotating field, stationary armature AC generator.  The rotating field, stationary armature type AC generator is used when large power generation is involved.  In this type of generator, a DC source is supplied to the rotating field coils, which produces a magnetic field around the rotating element.  As the rotor is turned by the prime mover, the field will cut the conductors of the stationary armature, and an EMF will be induced into the armature windings.  This type of AC generator has several advantages over the stationary field, rotating armature AC generator:

A load can be connected to the armature without moving contacts in the circuit.

It is much easier to insulate stator fields than rotating fields.

Much higher voltages and currents can be generated.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Explain the differences between a wye-connected and delta-connected AC generator, including advantages and disadvantages of each type.

In the wye connection, three common ends of each phase are connected together at a common terminal (marked “N” for neutral), and the other three ends are connected to a three-phase line.

In the delta connection, all three phases are connected in series to form a closed loop.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Motors

- Describe how an AC motor produces a rotating magnetic field.

Figure 6 A rotating magnetic field

In an AC motor there are three phases, and the phases are electrically 120º out of phase.  Electrically, the phases are connected to the windings via a wye connection.  Each phase has two windings.

The windings are wound in the same direction and are on opposite sides of the stator.  When electrical current flows through a winding a magnetic field is produced.  The magnetic field is directed across the diameter of the stator.  The magnetic field generated in one phase will depend on the current through that phase.  If the current through that phase is zero, the resulting magnetic field is zero.  If the current is at a maximum value, the resulting field is at a maximum value.

Since the currents in the three windings are 120º out of phase, the magnetic fields produced will also be 120˚ out of phase.  When the current flow in a phase is positive, the magnetic field will develop a north pole at the poles labeled A, B, and C.  When the current flow in a phase is negative, the magnetic field will develop a north pole at the poles labeled A', B', and C'.  The three magnetic fields will combine to produce one field, which will act upon the rotor.  At the end of one cycle of AC, the magnetic field will have shifted through 360˚ or one revolution.  For point T1 on figure 6, the current in phase C is at its maximum positive value.  The resulting magnetic field is established vertically downward, with the maximum field strength developed across the C phase, between pole C (north) and pole C' (south).  At the same instance, the currents in phases A and B are at half of the maximum negative value.  Thus poles A' and B' are weak south poles and poles A and B are weak north poles.  The strong magnetic field between poles C and C' prevents the weaker poles from connecting through the stator to their corresponding matching pole.  Instead, the strong magnetic field is aided by the weaker fields developed across phases A and B, with poles A' and B' being north poles and poles A and B being south poles.

The weak north A' pole is magnetically coupled to the closer weak south B pole rather than coupling through the rotor and the strong C and C' magnetic field.  Additionally, the weak north B' pole is magnetically coupled to the closer weak south A pole.  Thus, overall, one side of the stator has a north pole (centered on the C pole) and the other side of the stator has a south pole (centered on the C' pole).

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

Describe how an AC motor produces torque.

When alternating current is applied to the stator windings of an AC induction motor, a rotating magnetic field is developed.  The rotating magnetic field cuts the bars of the rotor and induces a current in them due to generator action.  The induced current in turn produces a magnetic field, opposite in polarity of the stator field, around the conductors of the rotor.  Because opposite charges attract, the rotor’s magnetic field will try to line up with the magnetic field of the stator.  Since the stator field is rotating continuously, the rotor cannot line up with, or lock onto, the stator field, and therefore must follow behind it.  The torque of an AC induction motor is dependent upon the strength of the interacting rotor and stator fields and the phase relationship between them.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

Using field speed and rotor speed, calculate percent slip in an AC motor.

The following is an example showing how to calculate percent slip in an AC motor.

Example: A four-pole, 60 Hz AC induction motor has a full-load speed of 1735 rpm.  Calculate percent slip in an AC motor.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

Explain the relationship between speed and torque in an AC induction motor.

Slip is the percentage difference between the speed of the rotor and the speed of the rotating magnetic field.

In an AC induction motor, as slip increases from zero to ~10 percent, the torque increases linearly.  As the load and slip are increased beyond full-load torque, the torque will reach a maximum value at about 25 percent slip.  If load is increased beyond this point, the motor will stall and come to a rapid stop.  The typical induction motor breakdown torque varies from 200 to 300 percent of full-load torque.  Starting torque is the value of torque at 100 percent slip and is normally 150 to 200 percent of full-load torque.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

Describe how torque is produced in a single-phase AC motor.

If two stator windings of unequal impedance are spaced 90 electrical degrees apart and connected in parallel to a single-phase source, the field produced will appear to rotate.  This is called phase splitting.

In a split-phase motor, a starting winding is used.  This winding has a higher resistance and lower reactance than the main winding.  When the same voltage (VT) is applied to the starting and main windings, the current in the main winding (IM) lags behind the current of the starting winding (IS).  The angle between the two windings is enough phase difference to provide a rotating magnetic field to produce a starting torque.  When the motor reaches 70 to 80 percent of synchronous speed, a centrifugal switch on the motor shaft opens and disconnects the starting winding.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

Explain why an AC synchronous motor does not have starting torque.

Torque is only developed when running at synchronous speed; therefore, the motor needs some type of device to bring the rotor to synchronous speed.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

Describe how an AC synchronous motor is started.

An AC synchronous motor may be started by a DC motor on a common shaft.  When the motor is brought to synchronous speed, AC current is applied to the stator windings.  The DC motor now acts as a DC generator and supplies DC field excitation to the rotor of the synchronous motor.  The load may now be placed on the synchronous motor.

Synchronous motors are more often started by means of a squirrel-cage winding embedded in the face of the rotor poles.  The DC rotor windings are de-energized and a reduced three-phase voltage is applied to the stator windings.  The motor is then started as an induction motor and brought to ~95 percent of synchronous speed, at which time direct current is applied, and the motor begins to pull into synchronism.  The torque required to pull the motor into synchronism is called the pull-in torque.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

Describe the effects of over and under-exciting an AC synchronous motor.

Keeping the same load, when the field excitation is increased on a synchronous motor, the motor operates at a leading power factor.  If field excitation is reduced, the motor will operate at a lagging power factor.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

State some applications of the following types of AC motors:

Induction

Single-phase

Synchronous

### Induction

The induction motor is the most commonly used AC motor in industrial applications because of its simplicity, rugged construction, and relatively low manufacturing costs.

### Single-Phase

Single-phase motors are used for very small commercial applications such as household appliances and buffers.

### Synchronous

Synchronous motors are used to accommodate large loads and to improve the power factor of transformers in large industrial complexes.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

Describe the differences in starting and operating characteristics of premium efficiency motors.

Since 1997, the Energy Policy Act (EPACT) has required most 1–200 hp general-purpose motors manufactured or imported for sale in the United States to meet minimum efficiency standards.  These motors have been identified as premium efficiency motors.

Premium efficiency motors offer the following benefits:

20 to 60 percent more copper in the windings

More and thinner laminations of higher-quality steel

Optimized air gap between stator and rotor

More efficient rotor-bar designs

Reduced fan losses

Higher quality control during manufacturing

Longer cores to reduce 2R (resistance) losses

Premium efficiency motors usually

have higher service factors

have longer insulation and bearing lives

have lower waste heat output and run cooler

have less vibration and are less noisy

are more likely to withstand voltage variations and harmonics

All of these characteristics increase their reliability.  Because of this, most motor manufacturers offer longer warranties for their premium efficiency designs.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

Describe the characteristics and operation of motor controllers.

Motor controllers range from a simple toggle switch to a complex system using solenoids, relays, and timers.  The basic functions of a motor controller are to control and protect the operation of a motor.  This includes starting and stopping the motor, and protecting the motor from over current, under voltage, and overheating conditions that would cause damage to the motor.  There are two basic categories of motor controllers, the manual controller, and the magnetic controller.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

Explain the following motor terms:

Revolutions per minute (RPM)

National Electrical Manufacturer’s Association (NEMA) frame size

Service factor

Insulation class

NEMA design designation (letter)

Non-symmetrical load

### RPM

RPM is the approximate speed at which a motor operates.  Multi-speed shaded pole motors show maximum speed first, followed by the total number of speeds (e.g., 3000/3-Spd).  Multi-speed split-phase and capacitor-start motors have maximum speed shown first, followed by the second speed (e.g., 1725/1140).  The RPM rating for a gear motor represents output shaft speed.

### NEMA Frame Size

NEMA provides us with frame size standardization, so you can make intelligent choices among the different sizes of motors.

Frame size standardization is important to motor interchangeability.  This means the same horsepower, speed, and enclosure will normally have the same frame size from different motor manufacturers.  Thus, it is possible to replace a motor from one manufacturer with a similar motor from another if they both use standard frame sizes.

### Service Factor

The service factor is a measure of continuous overload capacity at which a motor can operate without overload or damage.  The NEMA standard service factor for totally enclosed motors is 1.0.

### Insulation Class

There are four motor insulation classes: A, B, F, and H.

A: 105°C or 221°F

B: 130°C or 266°F

F: 155°C or 311°F

H: 180°C or 356°F

### NEMA Design Designation (letter)

NEMA has assigned a simple letter designation to four of the most common three-phase AC electric motors.  These motors vary in starting torque and speed regulation.  They are all of squirrel-cage construction, and are available in many sizes.

Design A has normal starting torque (typically 150-170 percent of rated capacity) and relatively high starting current.  Breakdown torque is the highest of all NEMA types.  It can handle heavy overloads for a short-duration.  For Design A, slip is less than or equal to 5 percent.  A typical application is powering of injection-molding machines.

Design B is the most common type of AC induction motor sold.  It has normal starting torque, similar to Design A, but offers low starting current.  Locked rotor torque is good enough to start many loads encountered in industrial applications.  For Design B, slip is less than or equal to 5 percent.  Motor efficiency and full-load power factor are comparatively high, contributing to the popularity of the design.  Typical applications include pumps, fans, and machine tools.

Design C has high starting torque (greater than the previous two designs, at about 200 percent), useful for driving heavy breakaway loads.  These motors are intended for operation near full speed without great overloads.  Starting current is low.  For design C, slip is less than or equal to 5 percent.

Design D has high starting torque (the highest of all the NEMA motor types).  Starting current and full-load speed are low.  High slip values (5–13 percent) make this motor suitable for applications with changing loads and attendant sharp changes in motor speed, such as in machinery with flywheel energy storage.  Speed regulation is poor, making Design D suitable for punch presses, cranes, elevators, and oil well pumps.  Several design subclasses cover the rather wide slip range.  This motor type is usually considered a special order item.

### Non-Symmetrical Load

A three-phase power system is called balanced or symmetrical if the three-phase voltages and currents have the same amplitude and are phase shifted by 120° with respect to each other.  If either or both of these conditions are not met, the system is called unbalanced or non-symmetrical.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

## Demonstrate a working-level knowledge of AC reactive components, including inductive and capacitive reactance and phase relationships in reactive circuits.

- Define the following:

Inductive reactance

Capacitive reactance

Impedance

Resonance

Power factor

Non-symmetrical load

### Inductive Reactance

Inductive reactance is the opposition of the inductance to the flow of an alternating current.

### Capacitive Reactance

Capacitive reactance is the force of a capacitor that acts as a resistor to limit the flow of current.  Capacitive reactance is inversely proportional to the capacitance of the capacitor and the frequency.

### Impedance

Impedance is the total opposition to the flow of an alternating current.  It may consist of any combination of resistance, inductive reactance, and capacitive reactance.  It is measured in ohms.

### Resonance

Resonance is a condition existing in a circuit in which the inductive and capacitive reactance cancels each other out.

### Power Factor

Power factor is the ratio between true power and apparent power.

### Non-Symmetrical Load

A three-phase power system is called balanced or symmetrical if the three-phase voltages and currents have the same amplitude and are phase shifted by 120° with respect to each other.  If either or both of these conditions are not met, the system is called unbalanced or non-symmetrical.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Describe the effect of the phase relationship between current (I) and voltage (E) in an inductive circuit.

The value of the self-induced EMF varies as a sine wave and lags the current by 90˚.  The applied voltage must be equal and opposite to the self-induced EMF at all times; therefore, the current lags the applied voltage by 90˚ in a purely inductive circuit.

The memory aid, “ELI the ICE man,” can be used to remember the voltage/current relationship in AC circuits.  ELI refers to an inductive circuit (L) where voltage (E) leads (comes before) current (I).

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Describe the effect on phase relationship between current (I) and voltage (E) in a capacitive circuit.

In any purely capacitive circuit, current leads applied voltage by 90˚.  The memory aid, “ELI the ICE man,” can be used to remember the voltage/current relationship in AC circuits.  ICE refers to a capacitive circuit (C) where current (I) leads (comes before) voltage (E).

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Determine the value for total current (IT) in a simple parallel resistance-capacitance-inductance (R-C-L) AC circuit.

Total current in a parallel R-C-L circuit is equal to the square root of the sum of the squares of the current flows through the resistance, inductive reactance, and capacitive reactance branches of the circuit.

Because the difference between IL and IC is squared, the order in which the quantities are subtracted does not affect the answer.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Describe the relationship between apparent, true, and reactive power.

The relationship between apparent, true, and reactive power can be described using a triangle.

Figure 7-Triangle describing the relationship between apparent, true, and reactive power

The power triangle equates AC power to DC power by showing the relationship between generator output (apparent power, S) in volt-amperes (VA), usable power (true power, P) in watts, and wasted or stored power (reactive power, Q) in volt-amperes-reactive (VAR).  The phase angle (θ) represents the inefficiency of the AC circuit and corresponds to the total reactive impedance (Z) to the current flow in the circuit.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Describe the indications of an unbalanced load in a three-phase power system.

In a fault condition, the neutral connection in a wye-connected load will carry more current than the phase under a balanced load.  Unbalanced three-phase circuits are indicated by abnormally high currents in one or more of the phases.  This may cause damage to equipment if the imbalance is allowed to continue.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Discuss circuit considerations required for non-symmetrical loads.

For information about non-symmetrical loads see

Dorf, Richard C. The Electrical Engineering Handbook. 1st ed. CRC Press, 1993.

Mablekos, Van E.  The Two Phase Induction Motor.” Section 4.10 in Electric Machine Theory for Power Engineering. New York: Harper and Row, 1980.

Werninck, E. H. Electric Motor Handbook: Alternating Current Motors. 1978.

## Demonstrate a working-level knowledge of electrical transmission and distribution systems.

- Explain the differences between transmission and distribution systems.

Electric power transmission is one process in the transmitting of electricity to consumers.  The term refers to the bulk transfer of electrical power from place to place.  Typically, power transmission is between the power plant and a substation near a populated area.  This is distinct from electricity distribution, which is concerned with the delivery from the substation to the consumers.  Due to the large amount of power involved, transmission normally takes place at high voltage (110 kV or above).  Electricity is usually transmitted over long distance through overhead power transmission lines.  Underground power transmission is used only in densely populated areas such as large cities because of the high cost of installation and maintenance.

Reference: Wikipedia, http://en.wikipedia.org/wiki/Electric_power_transmission

Identify and discuss the advantages and disadvantages associated with underground and aboveground distribution systems.

Underground distribution systems make for more attractive and uncluttered surroundings. Most equipment is buried beneath the surface, providing more space for landscaping.

Underground distribution systems provide a more reliable power supply.  More than 40 percent of power outages are caused by fallen branches or trees near overhead distribution lines, and in certain areas that percentage is much higher.

One disadvantage to underground distribution systems is that they are more costly than overhead wire and are vulnerable to degradation due to moisture, particularly in older cable installations.  Over time the moisture breaks down the cable insulation leaving the cable vulnerable to failures and prolonged outages.  Traditionally, the only long-term solution has been replacement of the degraded cables.

A major problem with underground distribution systems is that of making connections in congested manholes or junction boxes.  The necessary procedure involves soldering conductors, taping joints, and wiping lead-covered cable, and is so complex that it demands considerable skill and is time consuming and costly.

Reference: Dorf, Richard C. The Electrical Engineering Handbook., sections 58.1 and 58.2, 1st ed. CRC Press, 1993.

Describe the function and importance of the following control and protective devices:

Circuit breakers

Protective relays

Fuses

Transient protection

### Circuit Breakers

The purpose of a circuit breaker is to break the circuit and stop the current flow when the current exceeds a predetermined value without causing damage to the circuit or the circuit breaker.  Circuit breakers are commonly used in place of fuses and sometimes eliminate the need for a switch.

### Protective Relays

Protective relays are designed to cause the prompt removal of any part of a power system that might cause damage or interfere with the effective and continuous operation of the rest of the system.  Protective relays are aided in this task by circuit breakers that are capable of disconnecting faulty components or subsystems.

Protective relays can be used for types of protection other than short circuit or over current.  The relays can be designed to protect generating equipment and electrical circuits from any undesirable condition, such as under voltage, under frequency, or interlocking system lineups.

There are two operating principles for protective relays:  electromagnetic attraction and electromagnetic induction.  Electromagnetic attraction relays operate by a plunger being drawn up into a solenoid or an armature that is attracted to the poles of an electromagnet.  This type of relay can be actuated by either DC or AC systems.  Electromagnetic induction relays operate on the induction motor principle whereby torque is developed by induction in a rotor.  This type of relay can be used only in AC circuits.

### Fuses

A fuse is a device that only protects a circuit from an over current condition.  It has a fusible link that is directly heated and destroyed by the current passing through it.  A fuse contains a current-carrying element that is sized so that the heat generated by the flow of normal current through it does not cause it to melt the element.  However, when an over current or short-circuit current flows through the fuse, the fusible link will melt and open the circuit.

### Transient Protection

Power surges and transients are electrical fluctuations caused by lightning or other power utility issues.  The surge or transient is conducted through both power and data lines and can damage or destroy downstream equipment.  Vulnerable circuitry exists in an extremely hostile environment.  Properly applied transient protection can prevent equipment damage, downtime, and data corruption.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, volume 4

Compare and contrast the characteristics of three-phase and single-phase distribution systems.

A three-phase system is a combination of three single-phase systems.  In a three-phase balanced system, power comes from a three-phase AC generator that produces three separate and equal voltages each of which is 120° out of phase with the other voltages.

Three-phase equipment (motors, transformers, etc.) weighs less than single-phase equipment of the same power rating.  They have a wide range of voltages and can be used for single-phase loads.  Three-phase equipment is smaller in size, weighs less, and is more efficient than single-phase equipment.

Three-phase systems can be connected in two different ways.  If the three common ends of each phase are connected at a common point and the other three ends are connected to a three-phase line, it is called a wye connection.  If the three phases are connected in series to form a closed loop, it is called a delta connection.

Reference: DOE-HDBK-1011/3-92, DOE Fundamentals Handbook, Electrical Science, volume 3

Discuss the principles associated with ensuring continual power availability during electrical outages.

Typically there are six types of power anomalies and/or failure incidents experienced by electrical power users: total failures (also known as blackouts), severely reduced voltage (or brownouts), sags, spikes, surges, and noise.

Total failures, or blackouts, constitute a complete loss of electrical power.  It can be total failure throughout an entire geographical location, a single building, or group of buildings, or a single electrical panel within a building.  These failures can cause system and network crashes, PC lockups, and corruption or loss of valuable data from servers and workstations.  These blackouts are often caused by electrical storms, auto accidents involving utility poles, an electrical utility company’s inability to meet user demand (e.g., during sustained hot weather conditions), or simply by the inability of a building’s infrastructure to handle demand on an overloaded circuit.

Severely reduced voltage from the power utility, or a brownout, occurs when the utility company cannot meet customers demand.  This usually occurs in summer months when the use of air conditioning during times of prolonged heat waves taxes the pool of available power.  Sometimes these brownouts are planned by the utility and are directed at specific locations within their power grid.  In this case they are called rolling brownouts.  Today’s power equipment is designed to operate using electrical power that falls within a specific acceptable range.  Brownouts occur where the electrical supply voltage drops below this level.  This lowered voltage places a strain on the electronic components contained within the power equipment and can limit their operational life.  It can also cause immediate failure of those electronic components.

Sags, spikes, and surges are power anomalies caused by electrical storms, extraordinary demands for power from the utility, and other electrical equipment.  For example, the starting of an electrical motor, like an elevator, can sometimes cause momentary sag as the power source tries to meet demand, and then cause a spike once the motor has started and needs less electrical current to sustain operation.  These anomalies are rapid, momentary decreases (sags) or increases (surges or spikes) in voltage levels at the electrical outlet.  They can cause loss of data, total loss of a hard disk, and even catastrophic damage to the network or computing hardware in use.

Electrical noise is electromagnetic interference (EMI) caused by electrical storms, noisy electrical equipment (e.g., motors, welding equipment, etc.), fluorescent lighting, and even radio transmitters.  It can cause events such as system lockups, temporary lapses in computing, circuit connection termination, data transmission errors, and even data corruption or loss.

A complete assessment of power-related risks will help a company determine the appropriate level of protection needed and justify the cost of power-protection equipment.  To determine the level of protection a company requires or can afford, the following questions should be considered:

Does the business experience frequent power failures?

Is there frequent construction going on near or inside of the company’s facilities?

Are facilities located in areas where severe weather events occur, such as earthquakes, tornadoes, and snow/ice/hail storms?

Is the distribution wiring in the facilities over 20 years old?

Do the facilities have emergency generators, and do they supply power to critical systems and network equipment outlets? (Note: Oftentimes generators are in place, but they supply power only to emergency lighting, some elevators, and critical building infrastructure systems, but not to tenants or occupants of the buildings systems.)

When the business experiences downtime is personnel time wasted or does the outage impact the revenue stream?  Has the company performed a cost-of-downtime assessment?

Does the company have mission-critical business networks, systems, and/or processes that must be operational 24/7?

After reviewing the risks posed to an enterprise, the appropriate power protection devices can be selected based on the scope of the potential power interruption.

Short-term power anomalies such as spikes and surges lasting only a few millionths to a few thousandths of a second can be prevented using surge protection devices.  Placed between the network or computing device and the power outlet it is plugged into, a surge protector can prevent these power anomalies from reaching the server, router, or hub.

Intermediate-term power failures, such as blackouts, brownouts, and electrical noise lasting from a few seconds to 30 minutes, are treatable through uninterruptible power supplies (UPSs).  UPS devices contain batteries and an electronic inverter, which converts DC power from batteries to AC power required by the equipment being protected.  Software used in conjunction with a UPS can detect a loss of power and, after a predefined period of time, cause servers to execute their shutdown procedures.  This shutdown allows files to be closed and updated in a protected fashion, eliminating data loss and corruption.  Once power is restored, the system is signaled to start back up.  In the case of brownouts, the UPS detects this condition and can take over the job of supplying power in the proper operating range.

In general, there are three different types of UPS devices.  With an offline standby power supply (SPS), power is usually derived directly from the power line until power fails, at which time a battery-powered inverter turns on to continue supplying power.  The time it takes for the inverter to come online varies by unit.  The battery is charged when line power is available.  Offline UPSs do not compensate for voltages within the 103-132VAC-input window, and therefore are not useful in dealing with minor fluctuations in voltage.  They generally only protect systems from power spikes, and only protect against power sags and line noise when the battery is switched on due to a blackout.  They are generally not suitable for servers, but because of their low cost, they are often used in protecting desktop workstations.

When normal operating line power is present, a line-interactive UPS system conditions power using a Ferro resonant transformer.  The UPS maintains a constant output voltage even with a varying input voltage and provides good protection against line noise.  The UPS transformer also maintains output on its secondary briefly when a total outage occurs.  As with the offline SPS, the line-interactive UPS switches to battery operation if it experiences a significant power surge or complete outage.  It offers adequate protection as long as power sags or outages do not occur with a high degree of frequency in a short period of time, in which case the battery would switch on and off without having enough time to completely charge.  This type of failure mode would reduce available battery time during brownout or blackout conditions.

With a true UPS system, power is supplied continuously from an inverter.  There is no switchover time, and such systems provide the highest level of protection during normal operation.  It can provide line conditioning and voltage regulation and protection.  The true UPS system delivers power under all conditions and continually recharges its battery, making it always ready to respond if a severe power problem occurs.  This type of UPS is most often used for mission critical networks and computing equipment requiring high availability.

The appropriate load size of a UPS can be calculated by adding the volt-amperes (VAs) of the devices to be connected to the UPS.  (If a devices draw is specified in volts and amperes individually instead of VAs, the VA value can be obtained by multiplying the volts by the amperes.  If the device only identifies the number of watts required, the VA value can be calculated by multiplying the number of watts by 1.4.)  For safety, the UPS should have a VA of 40 to 50 percent more than the calculated VA value of the devices connected to it.  This will generally provide a UPS with a battery capable of supplying power long enough to allow the protected devices to properly shut down under the maximum load size.  UPS devices should be selected with enough battery time to power protected devices through brownouts periods.  In most cases, UPSs with battery times of at least 15 to 20 minutes are selected.

Finally, operational tests and maintenance checks should be performed regularly.  Testing for line failure recognition should be conducted monthly, and testing for full power failure shut down and restore capability should be conducted quarterly.

Long-term power failures can last from a few hours to several days.  In this case, alternate long-term power generation equipment is needed.  This can come in the form of portable power generators or generators that have been installed as part of a building’s infrastructure.  These generators are powered by diesel, gasoline, or propane and can continuously supply electricity to a building’s mission critical systems for up to a month.

Such SPSs typically generate electricity in the 152000kW range.  SPSs can be triggered into operation either manually or automatically.  In the manual operation, a user starts up the SPS and, once it has reached speed, manually switches it into operation.  Automatic SPSs switch into operation when the power failure has been detected for a specific period of time and switches out once power is restored.  This switch-in time should be less than the UPS dropout time, otherwise, systems and networks will experience a short-term outage window.

Only experienced personnel, with the aid of electricians, building management personnel, engineering contractors, and equipment vendors should undertake the selection, installation, and testing of SPSs.

The inclusion of an SPS into an enterprise’s power management plan can significantly reduce problems associated with complete loss of power.  The cost of an SPS typically is between $10,000 and $50,000.  Emergency generators also can be rented in case of a prolonged outage.  However, the need for a licensed electrician to connect the generator and approval of the building’s manager are factors affecting its use.

Reference: Power Protection Basics, Dr. James Kennedy, http://www.lucent.com/livelink/0900940380064ec5_Other.pdf#search=%22six%20types%20of%20power%20anomalies%22

Explain the following terms as they relate to power systems:

Fault current

Available fault current

Fault duty

### Fault Current

Fault current, also called short-circuit current, describes current flow during a short.  Fault current passes through all components in the affected circuit.  Fault current is generally very large and, therefore, hazardous. Only the combined impedance of the object responsible for the short, the wire, and the transformer limits its magnitude.

### Available Fault Current

Fault current calculations are a critical piece of the electrical design/engineering puzzle for electrical distribution systems in commercial and industrial installations.  A fault current calculation determines the maximum available current that will be available at a given node, or location, in the system.  Once the fault currents have been calculated, you can then select over current protection equipment, breakers, and fuses with a fault current rating equal to or greater than those values.  If a breaker or fuse isn’t rated to handle the maximum available fault current it might receive, it might not operate properly and its internal parts could fuse together or the device could blow up under the destructive stresses of a fault condition, which could cause serious injury and/or property damage.

Fault current calculations are based on Ohm’s Law (V=I×R).  To determine the maximum current available at any given point in a distribution system, the equation is rearranged to solve for current (I=V÷R).  In a short circuit condition, resistance (R) gets very small and is essentially based on the total resistance in the electrical distribution system, from the derived source of power to the point of the fault.

### Fault Duty

Reference: Dorf, Richard C. The Electrical Engineering Handbook. 1st ed. CRC Press, 1993.

Discuss the safety considerations associated with high-voltage transmission systems.

Safety considerations associated with high-voltage transmission systems fall into three categories: audible noise and radio/television interference, induced currents and hazardous shock, and electric and magnetic fields.

When a transmission line is in operation, an electric field is generated in the air surrounding the conductor.  Corona is the partial electrical breakdown of the insulating properties of the air in the vicinity of the conductors of a transmission line.  When the intensity of the electric field at the conductor surface exceeds the breakdown strength of the surrounding air, a corona discharge occurs at the conductor surface.  Energy and heat are dissipated in small volumes near the surface of the conductors.  Part of this energy is in the form of small local pressure changes that result in audible noise, or in a discharge that results in radio/television interference.

Corona-generated audible noise can be characterized as a hissing, cracking sound which, under certain conditions, is accompanied by a 120-hertz (Hz) hum.  Corona-generated audible noise is of concern primarily for contemporary lines at voltages of 345kV and higher during inclement weather.  The conductors of high-voltage transmission lines are designed to be corona-free under ideal conditions.  However, slight variations and irregularities in the conductor surface cause higher electric fields near the conductor surface, and the occurrence of corona.  The most common source of enhanced electric fields at the conductor surface is water droplets on, or dripping from, the conductors.  Therefore, audible noise from transmission lines is generally associated with wet weather (i.e., wet conductor) phenomenon.  Wet conductors can occur during periods of rain, fog, snow, or icing.  These conditions are expected to occur infrequently (less than 5 percent of the time).  During fair weather, insects and dust on the conductor also can serve as sources of corona.

Corona on transmission line conductors can also generate electromagnetic noise in the frequency bands used for radio and TV signals.  Radio and TV interference, known as gap-type noise, is caused by an oxidized film on the surface of two hardware pieces in contact.  The film acts as an insulator between the surfaces and small electric arcs, which produce noise and interference.

Induced current or spark discharge shocks can occur under certain conditions, in fields associated with 230kV or higher voltage transmission lines, when a person comes into contact with an object in an electric field.  These resulting short-term or long-term effects are the possible nuisances from electric fields.  Studies indicate it is unlikely that electric fields produce long-term health effects.  The grounding of nearby metal objects reduces the potential for these effects.

Whenever electricity is used or transmitted, electric and magnetic fields are created by the electric charges.  An electric field is said to exist in a region of space if a charge, at rest in that space, experiences a force of electrical origin (i.e., electric fields cause free charges to move).  The electric field is a vector quantity; that is, it has both magnitude and direction. The direction corresponds to the direction a positive charge would move in the field.  Sources of electric fields are unbalanced electrical charges (positive or negative) and time-varying magnetic fields.  Transmission lines, distribution lines, house wiring, and appliances all generate electric fields in their vicinity because of unbalanced electrical charge on unshielded energized conductors.  Electric fields are expressed in units of volts per meter (V/m) or kilovolts (thousands of volts) per meter (kV/m).  Electric fields are easily shielded by most objects, including trees, fences, and buildings.

Once electric fields are in motion, they create magnetic fields.  The strength of the magnetic field is proportional to the magnitude of the current in the circuit.  Magnetic fields can be characterized by the force they exert on a moving charge or on an electrical current.  A magnetic field is a vector quantity that is characterized by both magnitude and direction. Electric currents are sources of magnetic fields.  Magnetic fields are expressed as exposure per unit area in units of milligauss (mG).  Magnetic fields are not shielded by most materials.

The spatial uniformity of an electric field depends on the source of the field and on the distance from that source.  On the ground under a transmission line, the electric field is nearly constant in magnitude and direction over distances of a few meters. In proximity to transmission or distribution line conductors, however, the field decreases rapidly as distance (r) from the conductor increases.  Similarly, near small sources such as appliances, the field is not uniform and falls off even more rapidly with distance from the device.  If an energized conductor (source) is inside a grounded conducting enclosure, then the electric field outside the enclosure is zero, and the source is said to be shielded.

Transmission line-related fields decrease at a rate of 1/r2 if currents are balanced and conductors are closed spaced.  Magnetic fields associated with unbalanced phase circuits will fall off inversely from distance to the source (conductor) at a rate of 1/r.  Therefore, if the distance is doubled from the source and the transmission line current is balanced in all three phases, the magnetic field would drop off by a factor of 4.  However, if the phase current is unbalanced and distance from the source is doubled, the field decreases by only one-half of its original intensity.

The electric field created by a high-voltage transmission line extends from the energized conductors to other conducting objects such as the ground, towers, vegetation, buildings, vehicles, and people.  The strength of the vertical component of the electric field at a height of 1 meter (3.28 feet) is frequently used to describe the electric field under transmission lines. Magnetic fields from high voltage transmission lines are produced only when current flows and they have a magnitude that is dependent on the amount of current, not the applied voltage.

Reference: Avenal Energy, http://www.energy.ca.gov/sitingcases/avenal/documents/applicants_files/AFC_CD-ROM/6.18.pdf#search=%22%20%22audible%20noise%20and%20radio%2Ftelevision%20interference%22%22

Explain the requirements for and uses of alternate power supplies.

The following requirements are applicable to engine generators, uninterruptible power supplies, and stationary batteries.

Internal events. The alternate power supply should have the capability to perform its required function over the expected range of environmental and load conditions independent of the normal sources of power.  The environmental considerations should include the effects of anticipated operating conditions and failed plant equipment that may have an adverse impact on the ability of the alternate power supply to perform its function.

External events. The alternate power supply associated distribution systems, and necessary support systems should be protected against those events likely to produce a loss of normal power.  Examples of such events are hurricanes (high winds), tornadoes, floods, ice storms, lightning, fire, and seismic events.  The level of protection should be related to the expected frequency and consequences of total loss of AC power due to the particular event.

Output breakers. Output breaker protection and load breaker protection should be coordinated in accordance with NFPA 110.  A fault on an individual load or circuit should not trip the alternate power supply’s output breaker.

Output breakers should have an interrupt rating greater than or equal to the maximum available fault current at its location.  Output breakers should be located such that a fire at the alternate power supply will not damage the bus feed circuit downstream of the output breaker.  This should prevent a fire at the alternate power supply from causing the loss of ability to feed loads from the normal source.

Reference: DOE-STD-3003-2000, Backup Power Sources for DOE Facilities, 2000

Discuss the uses of different voltages in a facility.

Equipment sensitive to frequency and/or voltage is designed to operate within certain tolerances.  Most equipment is sensitive to large changes in the supply voltage level because more current will flow through a device when the voltage level of the supply is increased (the current through the device is equal to the voltage across the device divided by the impedance of the device).  When a larger current flows, the heat dissipated in the device increases (the heat dissipated by the device is proportional to the square of the current).  Thus, doubling the voltage will typically double the current, resulting in the device dissipating four times the heat.  Most devices cannot tolerate this amount of heat and cannot operate reliably with a supply voltage level more than 10 percent or so higher than their rated voltage.  A transformer can be used to transfer electrical energy with high efficiency from one voltage level to another at the same frequency.

Reference: http://www.usace.army.mil/inet/usace-docs/armytm/tm5-688/chap-2.pdf.

Discuss the reasons for using single-phase versus three-phase power systems in a facility.

In electrical engineering, single-phase electric power refers to the distribution of electric power using a system in which all the voltages of the supply vary in unison.  Single-phase distribution is used when loads are mostly lighting and heating, with few large electric motors.

Reference: http://en.wikipedia.org/wiki/Single_phase

Discuss which systems would benefit from line filtering.

Discuss the types of noise for which systems benefiting from line filtering would be susceptible to without implementation of line filtering.

Power surges, voltage spikes, and electromagnetic noise can all cause potential problems with electronic equipment.  There are many products available to address each area of concern, but one product group addresses all three problems: power line conditioners.  To be considered a power line conditioner, the unit must incorporate surge protection, electromagnetic-interference/radio-frequency interference noise filtering, and voltage regulation.

For equipment in a building that shares its main power line with other buildings or high-current draw devices, the fluctuations in the voltage are likely to exceed the tolerance of equipment at some point.

In general, circuits are designed to operate with a particular supply voltage.  When the supply voltage changes, the operation of the circuit may be adversely affected.  Consequently, some types of equipment must have power supplies that produce the same output voltage regardless of changes in the load resistance or changes in the AC line voltage.  That is where the voltage regulation function of a power conditioner comes into play.  By constantly monitoring the AC voltage level and limiting it when necessary, a more consistent voltage level is maintained, lessening the chances of damage to or erratic behavior of the equipment.

Reference: Info Com International, http://www.infocomm.org/index.cfm?objectID=1E4303D3-3D45-4769-ADED9BF582B8F3D5

Define the terms, Harmonics, Positive, Negative, and Zero sequence currents.

### Harmonics

The term harmonics is used to describe a component of a periodic voltage or current waveform having a frequency that is an integral multiple of the fundamental power line frequency, 60Hz in the U.S.  This irregular waveform results because the waveform required by power electronic loads is quite different than the sinusoidal voltage delivered by the utility.  This ‘non-linear’ current draw results in a distorted waveform.

High levels of harmonic distortion can stress the electrical network within a water treatment facility and on the servicing utility, causing problems for sensitive electronic equipment.  The impact on a facility can be very costly, especially when processes are disrupted or shut down, reducing productivity, increasing repair and maintenance costs, and possibly spilling partially treated or untreated wastewater into nearby waterways.

Reference: Environmental Science and Engineering, http://www.esemag.com/0905/harmonics.html

### Positive, Negative, and Zero Sequence Currents

Sequence components of voltage and current are obtained by transformation using a three-phase vector having a magnitude of 1/3 (per channel) and a phase angle of zero, 120, and -120 degrees.  Zero sequence is the algebraic sum of the three vector phases, divided by three, and in a balanced system, should be zero.  Positive sequence is the product of the three-phase signal vector, multiplied by a vector with reverse phase rotation; in a balanced system, positive sequence should be equal to the voltage (current) of each phase with the same phase angle (relative to GPS) as the Aphase signal.  Negative sequence is the product of the three-phase signal vector, multiplied by a vector with normal phase rotation; in a balanced system, negative sequence should be equal to zero.

Reference: Arbiter Systems,

http://www.arbiter.com/ftp/datasheets/1133a_conv_energy_seq_comp.pdf

Describe the sources of harmonics.

Sources of harmonics are

#### Ideal Rectifiers

Different rectifier drives in industry, traffic, and power transmission realized with solid state technology generate harmonics.  Household electronics are also a source of harmonics.  When studying the harmonics the treatment of rectifier equipment can be reduced to the study of rectifier bridges.

#### Rectifiers in Reality

The ideal harmonic theory is practical in theoretical observation.  In reality, non-characteristic harmonics can often be found among the harmonics generated by rectifiers.

#### Thyristor Switches

In industry, thyristor switches are often used to control resistive loads, e.g. infra-red dryers.  The most common ways of control are the zero-point and phase angle control.

#### Arc Furnaces

There are three kinds of melting furnaces in use in industry: resistance, induction, and arc furnaces.  Resistance furnaces are visible in the network like a resistance load and induction furnaces like a motor load.  Arc furnaces are most problematic for networks.

#### Transformers

A transformer’s harmonic generating effect is based on the magnetic non-linearity of iron.  The magnetic flux density does not grow linearly with increase of magnetic field strength.  Due to the hysteresis of the transformer’s iron core the magnetic flux does not follow the curve form of supply voltage.

Transformer connection, structure of the core, and way of earthing have a remarkable effect on the generation and spreading of harmonics.

#### Other Sources of Harmonics

Other sources of harmonics are discharge and fluorescent lamps, short-circuit motors and generators.  In normal operating conditions generators and short-circuit motors are not significant sources of harmonics.

Reference: http://leeh.ee.tut.fi/harmo/2.htm

Describe the effect of harmonics on the power system and equipment.

The effects of three-phase harmonics on circuits are similar to the effects of stress and high blood pressure on the human body.  High levels of stress or harmonic distortion can lead to problems for the utility’s distribution system, plant distribution system, and any other equipment serviced by that distribution system.  Effects can range from spurious operation of equipment to a shutdown of important plant equipment, such as machines or assembly lines.

Harmonics can lead to power system inefficiency.  Some of the negative ways that harmonics may affect plant equipment are listed below:

#### Conductor Overheating:

A function of the square rms current per unit volume of the conductor.  Harmonic currents on undersized conductors or cables can cause a “skin effect”, which increases with frequency and is similar to a centrifugal force.

#### Capacitors:

Capacitors can be affected by heat rise increases due to power loss and reduced life on the capacitors.  If a capacitor is tuned to one of the characteristic harmonics such as the 5th or 7th, over voltage and resonance can cause dielectric failure or rupture the capacitor.

#### Fuses and Circuit Breakers

Harmonics can cause false or spurious operations and trips, damaging or blowing components for no apparent reason.

#### Transformers

Transformers have increased iron and copper losses or eddy currents due to stray flux losses. This causes excessive overheating in the transformer windings.  Typically, the use of appropriate “K factor” rated units is recommended for non-linear loads.

#### Generators

Generators have similar problems to transformers.  Sizing and coordination is critical to the operation of the voltage regulator and controls.  Excessive harmonic voltage distortion will cause multiple zero crossings of the current waveform.  Multiple zero crossings affect the timing of the voltage regulator, causing interference and operation instability.

#### Utility Meters

Utility meters may record measurements incorrectly, resulting in higher billings to consumers.

#### Drives/Power Supplies:

Drive/power supplies can be affected by misoperation due to multiple zero crossings. Harmonics can cause failure of the commutation circuits, found in DC drives and AC drives with silicon controlled rectifiers (SCRs).

#### Computers/Telephones:

Computers and telephones may experience interference or failures.

Reference: Square D, http://www-ppd.fnal.gov/EEDOffice-w/Projects/CMS/LVPS/mg/8803PD9402.pdf

Describe the typical means of mitigating harmonics and their effects.

There are many ways to reduce harmonics, ranging from variable frequency drive designs to the addition of auxiliary equipment.  The primary methods used today to reduce harmonics are:

#### Power System Design

Harmonics can be reduced by limiting the non-linear load to 30% of the maximum transformer’s capacity.  However, with power factor correction capacitors installed, resonating conditions can occur that could potentially limit the percentage of non-linear loads to 15% of the transformer’s capacity.  If hr equals or is closed to a characteristic harmonic, such as the 5th or 7th, there is a possibility that a resonant condition could occur.

#### 12-Pulse Converter Front End

In this configuration, the front end of the bridge rectifier circuit uses twelve diodes instead of six.  The advantages are the elimination of the 5th and 7th harmonics to a higher order where the 11th and 13th become the predominate harmonics.  This will minimize the magnitude of harmonics, but will not eliminate them.  The disadvantages are cost and construction, which also requires either a Delta-Delta and Delta-Wye transformer, “Zig-Zag” transformer or an autotransformer to accomplish the 30° phase shifting necessary for proper operation.  This configuration also affects the overall drive system efficiency rating because of the voltage drop associated with the transformer configuration requirement.

#### Delta-Delta and Delta-Wye Transformers

This configuration uses two separate utility feed transformers with equal non-linear loads.  This shifts the phase relationship to various six-pulse converters through cancellation techniques, similar to the twelve-pulse configuration.

#### Isolation Transformers

An isolation transformer provides a good solution in many cases.  The advantage is the potential to “voltage match” by stepping up or stepping down the system voltage, and by providing a neutral ground reference for nuisance ground faults.  This is the best solution when utilizing AC or DC drives that use SCRs as bridge rectifiers.

#### Line Reactors

More commonly used for size and cost, the line reactor is the best solution for harmonic reduction when compared to an isolation transformer.  AC drives that use diode bridge rectifier front ends are best suited for line reactors.  Line reactors (commonly referred to as inductors) are available in standard impedance ranges from 1.5%, 3%, 5%, and 7.5%.

#### Harmonic Trap Filters

Used in applications with a high non-linear ratio to system to eliminate harmonic currents.  Filters are tuned to a specific harmonic such as the 5th, 7th, 11th, etc.  In addition, harmonic trap filters provide true distortion power factor correction.

Reference: http://www-ppd.fnal.gov/EEDOffice-w/Projects/CMS/LVPS/mg/8803PD9402.pdf

## Demonstrate a working level knowledge of transformers.

- Define the following terms as they apply to transformers:

Mutual induction

Turns ratio

Impedance ratio

Efficiency

### Mutual Induction

Mutual induction is the production of an electrical voltage in a coil due to the relative position of two inductors, which causes the magnetic lines of force to link with the turns of the other.

### Turns Ratio

Turns ratio is the ratio of the number of turns in the primary winding to the number of turns in the secondary windings of a transformer.

### Impedance Ratio

The ratio between the two impedances is referred to as the impedance ratio.

### Efficiency

The efficiency of a transformer is the ratio of the power output to the power input.

Reference: DOE-HDBK-1011/4-92; DOE Fundamentals Handbook Electrical Science, volume 4 of 4, 1992

Describe the differences between a wye-connected and delta-connected transformer.

In the wye connection, three common ends of each phase are connected together at a common terminal (marked “N” for neutral), and the other three ends are connected to a three-phase line.

In the delta connection, all three phases are connected in series to form a closed loop.

Reference: DOE-HDBK-1011/4-92; DOE Fundamentals Handbook Electrical Science, volume 4 of 4, 1992

Using the type of connection and turns ratios for the primary and secondary of a transformer, calculate voltage, current, and power for each of the following types:

Delta - Delta

Delta - Wye

Wye - Delta

Wye – Wye

The following are examples of these calculations.

### Example 1

Given a three-phase transformer bank with a line voltage of 13.8 kV, primary line current 12.5 A, and a turns ratio of 5:1 with a Delta - Delta connection:

Calculate the voltage across each primary winding.

primary voltage = V = 13800 volts

Calculate the primary phase current.

primary phase current =  =  = 7.22 amps

Calculate the secondary line current.

secondary line current = 5(12.5) = 62.5 amps

Calculate the secondary phase current.

secondary phase current =  =  = 36.1 amps

### Example 2

Given a three-phase transformer bank with a line voltage of 13.8 kV, primary line current 12.5 A, and a turns ratio of 5:1 with a Wye - Wye connection:

Calculate the voltage across each primary winding.

primary voltage =  =  = 7967.4 volts

Calculate the primary phase current

primary phase current = I = 12.5

Calculate the secondary line current

secondary line current = aI = 5(12.5) = 62.5 amps

Calculate the secondary phase current

Secondary phase current = aI = 5(12.5) = 62.5 amps

Reference: DOE-HDBK-1011/4-92; DOE Fundamentals Handbook Electrical Science, volume 4 of 4, 1992

State the applications of each of the following types of transformers:

Distribution

Power

Control

Auto

Isolation

Instrument potential

Instrument current

### Distribution

Distribution transformers are generally used in electrical power distribution and transmission systems.  This class of transformer has the highest power, or volt-ampere ratings, and the highest continuous voltage rating.  The power rating is normally determined by the type of cooling methods the transformer may use.  Some commonly used methods of cooling are by using oil or some other heat-conducting material.  Ampere rating is increased in a distribution transformer by increasing the size of the primary and secondary windings; voltage ratings are increased by increasing the voltage rating of the insulation used in making the transformer.

### Power

Power transformers are used in electronic circuits and come in many different types and applications.  Electronics or power transformers are sometimes considered to be those with ratings of 300 volt-amperes and below.  These transformers normally provide power to the power supply of an electronic device, such as in power amplifiers in audio receivers.

### Control

Control transformers are generally used in electronic circuits that require constant voltage or constant current with a low power or volt-ampere rating.  Various filtering devices, such as capacitors, are used to minimize the variations in the output.  This results in a more constant voltage or current.

### Auto

The autotransformer is generally used in low power applications where a variable voltage is required.  The autotransformer is a special type of power transformer.  It consists of only one winding.  By tapping or connecting at certain points along the winding, different voltages can be obtained.

### Isolation

Isolation transformers are normally low power transformers used to isolate noise from or to ground electronic circuits.  Since a transformer cannot pass DC voltage from primary to secondary, any DC voltage, such as noise, cannot be passed, and the transformer acts to isolate this noise.

### Instrument Potential

The instrument potential transformer steps down voltage of a circuit to a low value that can be effectively and safely used for operation of instruments such as ammeters, voltmeters, wattmeters, and relays used for various protective purposes.

### Instrument Current

The instrument current transformer steps down the current of a circuit to a lower value and is used in the same types of equipment as a potential transformer.  This is done by constructing the secondary coil, consisting of many turns of wire, around the primary coil, which contains only a few turns of wire.  In this manner, measurements of high values of current can be obtained.

A current transformer should always be short-circuited when not connected to an external load.  Because the magnetic circuit of a current transformer is designed for low magnetizing current when under load, this large increase in magnetizing current will build up a large flux in the magnetic circuit and cause the transformer to act as a step-up transformer, inducing an excessively high voltage in the secondary when under no load.

Reference: DOE-HDBK-1011/4-92; DOE Fundamentals Handbook Electrical Science, volume 4 of 4, 1992

Describe the hazardous materials that are associated with transformers.

Wet type transformers are filled with oil.  Fire or explosion is a possibility if the transformer is faulted.  Polychlorinated Biphenyls (PCB) or PCB-contaminated electrical equipment and the treatment of PCB oil spills shall comply with 40 CFR 761.  Oil filled transformers installed near buildings shall comply with FM 5-4/14-8.  Existing PCB or PCB-contaminated equipment shall be identified with warning signs and shall not be relocated or re-used in other existing or new facilities.  Electrical equipment cooling material shall be handled in accordance with 29 CFR 1910.1200.

When venting or opening gas or oil filled equipment, take precautions against explosion, fire, and asphyxiation.  Ensure adequate ventilation is provided.

Extreme care must be taken when dealing with transformers filled with Inerteen.  Inerteen fumes are toxic, especially when heated.  Exposure to the skin may cause skin rashes, so gloves should be worn to prevent contact with the skin.

Gas given off by a selenium rectifier is toxic.  The gas, hydrogen selenide, has a strong, pungent odor.

Although not a material hazard, operators should be aware not to open the circuit of the secondary windings.  Opening the secondary windings of a transformer will increase the flux in the core due to the high primary windings, creating excessive core loss, heating, and dangerously high voltage across the secondary windings.

An additional hazard, although not a material hazard is that in transformers with fans for cooling, the fans may start automatically at any time.  Do not place hands or tools in the fans.

Reference: Electrical Systems Topical Area Self-Study Guide, CS 1.16f, August 1996

Describe the conditions that must be met prior to paralleling two transformers, including consequences of not meeting these conditions.

The following conditions must exist for transformers to operate satisfactorily in parallel:

Connection diagrams must be identical.  Paralleling transformers with different connection diagrams is similar to short circuiting their secondary windings.

Voltage ratios must be the same.  If voltage ratios are not the same, circulating currents will flow in the secondaries with no or little load and the division of load will be improper.

Percent impedance, including primary and secondary leads to each transformer, should be nearly equal.  If the impedance’s are equal and the turn’s ratios are identical, the paralleled transformers will divide the load currents (properly) in proportion to their kVA ratings.  If the percent impedance’s are different, the transformer with the lower percent impedance will take more than its proper share of the load.

Reference: http://polk-burnett.apogee.net/pd/dsdo.asp

## Demonstrate a working-level knowledge of Uninterruptible Power Supplies (UPS).

- Describe how a UPS works.

- Identify the various UPS components.

### How a UPS works

Normal conditions - AC from the normal power supply is converted into DC in the rectifier.  A small trickle charge of DC electricity maintains a charge on the UPS DC battery.  The majority of DC electricity from the rectifier is converted back to AC electricity in the inverter.  The AC electricity passes through a static transfer switch and onto the uninterruptible power supply loads via the distribution panel.

Loss of normal power - When the normal AC electricity power supply is lost, the static transfer switch sense the loss of electricity.  The static transfer switch automatically disconnects the normal power supply and connects the alternate AC power supply.  This allows the alternate power supply to provide power to the uninterruptible power supply loads.

Loss of normal power and alternate power - When the normal AC electricity power supply is lost and the static transfer switch senses power unavailable from the alternate AC power supply, as soon as the DC electricity out of the rectifier drops below the voltage of the UPS battery, electricity flows out of the battery and to the inverter where the DC electricity is converted to AC electricity in the inverter.  The AC electricity passes through a static transfer switch and onto the uninterruptible power supply loads via the distribution panel.  The UPS loads will be supplied with power as long as the charge on the battery lasts.  UPS batteries are sized to provide full load on the system for approximately 20 minutes.

Reference: Electrical Systems Topical Area Self-Study Guide, CS 1.17b. August 1996

### Various UPS Components

Major UPS components include a rectifier charger, a battery bank, and an inverter.

### Rectifier

Each rectifier is adjusted to supply the inverter with nominal power while simultaneously maintaining the level of battery charge, or to recharge the battery after a period of back up.  Each rectifier consists of the following elements:

An anti-mains harmonic feed-back filter

A rectifier bridge controlling the output voltage

A smoothing inductor designed to eliminate residual ripple (The residual AC component must not affect the battery lifespan.)

A command and electronic adjustment logic

Control and monitoring equipment

Following a mains failure and its return, the rectifiers start up automatically.  To avoid mains inrush current during voltage return, it is possible to individually stagger each rectifier start up using a time delay, and the power build-up is progressive (longer than 10 seconds).  Stopping battery recharge is possible without stopping the rectifier, using external data (dry contacts).  When running off generator sets, this function ensures that the battery is not recharged before returning to normal mains.  Each rectifier charger consists of several adjustable voltage set points adapted to the requirements of battery recharge.  Adjustment consists of an automatic compensation system for load voltage according to the ambient temperature within the battery casing.

### Battery Bank

The battery banks are stationary and of the following types:

Sealed lead-acid, mounted and cabled in a matching cabinet

Sealed lead-acid on racks

Open lead-acid on racks

Protection is incorporated in the battery cabinets, which are mounted on the wall.  A device protects each battery against the risk of total discharge.

### Inverter

The inverter design enables the tolerances of different output parameters (voltage, distortion rates, and frequency) to be maintained.  Each inverter consists of a three-phase frequency converter fitted with

a power converter bridge with insulated gate bipolar-type transistors

a parallel series filter

control and command electronics

The operating principle is based on pulse width modulation.  The oscillator provides the frequency reference and is synchronized with the main’s frequency when this is within tolerance.  It operates autonomously when the main is out of tolerance or absent.

It is also possible to desynchronize its operating when, for example the UPS supply is provided by a generator set, the stability of which is incompatible with the load requirements.  In cases of sharp current build, and before the inverter voltage exceeds its tolerance, the load is transferred to the mains without interruption (automatic by-pass).  Once returned to a normal state, the load is automatically supplied by the inverters.  In the case of a non-discriminated short-circuit, the inverters must be shut-off by their electronic protection without any deterioration.  After the inverter has stopped after full battery discharge, the UPS will restart automatically when the mains supply is restored.

Reference: http://www.dts-ups.com/DELPHYS%20DS%203ph-1ph.htm

## Demonstrate a working-level knowledge of variable frequency (speed) drives (VFD).

- Describe the major components and operation of a VFD.

A VFD is a system for controlling the rotational speed of an alternating current (AC) electric motor by controlling the frequency of the electrical power supplied to the motor.  A VFD is a specific type of adjustable speed drive.  VFDs are also known as adjustable frequency drives, variable speed drives, AC drives, or inverter drives.

A variable frequency drive system generally consists of an AC motor, a controller and an operator interface.

#### VFD Motor

The motor used in a VFD system is usually a three-phase induction motor.  Some types of single-phase motors can be used, but three-phase motors are usually preferred.  Various types of synchronous motors offer advantages in some situations, but induction motors are suitable for most purposes and are generally the most economical choice.  Motors that are designed for fixed-speed mains voltage operation are often used, but certain enhancements to the standard motor designs offer higher reliability and better VFD performance.

#### VFD Controller

Variable frequency drive controllers are solid state electronic power conversion devices.  The usual design first converts AC input power to DC intermediate power using a rectifier bridge.  The DC intermediate power is then converted to quasi-sinusoidal AC power using an inverter switching circuit.  The rectifier is usually a three-phase diode bridge, but controlled rectifier circuits are also used.  Since incoming power is converted to DC, many units will accept single-phase as well as three-phase input power (acting as a phase converter as well as a speed controller); however the unit must be derated when using single phase input as only part of the rectifier bridge is carrying the connected load.

As new types of semiconductor switches have been introduced, they have promptly been applied to inverter circuits at all voltage and current ratings for which suitable devices are available.  Currently, insulated gate bipolar transistors are used in most VFD inverter circuits.

AC motor characteristics require the applied voltage to be proportionally adjusted whenever the frequency is changed.  For example, if a motor is designed to operate at 460 volts at 60 Hz, the applied voltage must be reduced to 230 volts when the frequency is reduced to 30 Hz.  Thus the ratio of volts per hertz must be regulated to a constant value (460/60 = 7.67 in this case).  For optimum performance, some further voltage adjustment may be necessary, but nominally constant volts per hertz is the general rule.  The latest method used for adjusting the motor voltage is called pulse width modulation (PWM).  With PWM voltage control, the inverter switches are used to divide the quasi-sinusoidal output waveform into a series of narrow voltage pulses and modulate the width of the pulses.

An embedded microprocessor governs the overall operation of the VFD controller.  The main microprocessor programming is in firmware that is inaccessible to the VFD user.  However, some degree of configuration programming and parameter adjustment is usually provided so that the user can customize the VFD controller to suit specific motor and driven equipment requirements.

#### VFD Operator interface

The operator interface provides a means for an operator to start and stop the motor and adjust the operating speed.  Additional operator control functions might include reversing and switching between manual speed adjustment and automatic control from an external process control signal.  The operator interface often includes an alphanumeric display and/or indication lights and meters to provide information about the operation of the drive.  An operator interface keypad and display unit is often provided on the front of the VFD controller.  The keypad display can often be cable-connected and mounted a short distance from the VFD controller.  Most are also provided with input and output (I/O) terminals for connecting pushbuttons, switches, and other operator interface devices or control signals.  A serial communications port is also often available to allow the VFD to be configured, adjusted, monitored, and controlled using a computer.

Reference: http://en.wikipedia.org/wiki/Variable_Frequency_Drive

Give examples where VFDs are used.

Nearly all VFDs manufactured today are referred to as pulse width modulation drives.  These drives contain electronic circuitry that converts the 60 Hz line power to direct current, then pulses the output voltage for varying lengths of time to mimic an alternating current at the frequency desired.

The majority of VFD applications are for centrifugal pumps and fans.  The savings potential for these devices is the largest, since the theoretical input power varies with the cube of fan/pump speed and volume.

For example, a fan operating at half speed will require only about 13 percent of full speed power.  Losses in the VFD will reduce savings somewhat, but the savings are still very impressive.

Air and water flow control is accomplished by either of several methods, including recirculating a portion of the flow, throttling, variable inlet vanes, and variable frequency drives.

Recirculating part of the flow results in the fan or pump operating at full volume all the time.  Only a portion of the flow is used for the system or process and the rest is recirculated back to the inlet of the fan or pump.  This is the least efficient means of controlling flow.

Throttling essentially chokes the outlet of the pump or fan to decrease flow much like holding your thumb over the end of a garden hose.  The pressure increases and the flow decreases.  This results in some energy savings over a constant volume recirculating system, but is still wasteful.

Variable inlet vanes apply only to fans and compressors, not pumps.  Inlet vanes control flow by pre-spinning the air entering a fan wheel or compressor impeller in the direction of rotation, which effectively varies its capacity.

VFDs can also be applied to what are called constant torque loads.  Unlike the fan and pump power which varies with the cube of speed, constant torque applications vary power in direct proportion to speed.  This results in lower savings for a given reduction in speed, but there are still significant savings available in some applications.  Examples of constant torque systems include conveyors and hydraulically driven injection molding machines.  Positive displacement pumps and compressors are also constant torque machines.  VFDs provide the most efficient part load control of rotary screw air compressors, and are gaining market share in the industry.

VFDs can be installed with manual or automatic bypasses.  In the early days of the VFDs, bypasses were more common since VFDs were not as reliable as they are at the present time.  The bypasses were installed in the event of a drive failure to ensure the system or process would remain on line.  Bypasses are still available but not always installed.  The criticality of the application must be considered in each case to determine whether the added cost and security of a bypass is warranted.

Harmonic filtering may be necessary in some applications.  VFDs can produce harmonics that can make their way back to the rest of the building and interfere with sensitive electronic equipment and machines.  Line reactors can be used on smaller drives of 20 hp and less to dampen and mitigate harmonics.  For larger applications, an isolation transformer may be warranted.  The isolation transformer can be installed either on the drive or on the piece of equipment to be protected from the harmonics.  Because the equipment being protected may be much lower in power, it may be most economical to isolate the piece of equipment from the building supply.

Reference: Alliant Energy, http://www.alliantenergy.com/docs/groups/public/documents/pub/p012399.hcsp

## Demonstrate a working-level knowledge of electrical test instruments and measuring devices.

- Describe the purpose and method of operation of the following in-place measuring devices:

Voltmeter

Ammeter

Ohmmeter

Wattmeter

Ampere-hour meter

Power factor meter

Ground detector

Synchroscope

Megger

Power quality monitors

### Voltmeter

Voltmeters are used extensively in industry where the surveillance of input and/or output voltages is vital for plant operation.  A simple DC voltmeter can be constructed by placing a resistor, called a multiplier, in series with the ammeter meter movement, and marking the meter face to read voltage.  Voltmeters are connected in parallel with the load being measured.

When a voltmeter is connected in a circuit, the voltmeter will draw current from that circuit.  This current causes a voltage drop across the resistance of the meter, which is subtracted from the voltage being measured by the meter.  This reduction in voltage is known as the loading effect and can have a serious effect on measurement accuracy, especially for low current circuits.

The accuracy of a voltmeter is defined as the ratio of measured voltage when the meter is in the circuit to the voltage measured with the meter out of the circuit.

### Ammeter

The measurement of current being supplied to or from a component is measured by an ammeter.  The ammeter measures electric current. It may be calibrated in amperes, milliamperes, or microamperes.  To measure current, the ammeter must be placed in series with the circuit to be tested.  When an ammeter is placed in series with a circuit, it will increase the resistance of that circuit by an amount equal to the internal resistance of the meter.

The accuracy of the ammeter is the ratio of the current when the meter is in the circuit to the current with the meter out of the circuit.

### Ohmmeter

The ohmmeter is an instrument used to determine resistance.  A simple ohmmeter consists of a battery, a meter movement calibrated in ohms, and a variable resistor.

Ohmmeters are connected to a component that is removed from the circuit.  The reason for removing the component is that measurement of current through the component determines the resistance.  If the component remains in the circuit, and a parallel path exists in the circuit, the current will flow in the path of least resistance and give an erroneous reading.

### Wattmeter

The wattmeter is an instrument that measures DC power or true AC power.  The wattmeter uses fixed coils to indicate current, while the movable coil indicates voltage.  The fixed coils in series with one another serve as an ammeter.  The two terminals are connected in series with the load.  The movable coil, and its multiplier resistor, is used as a voltmeter, with the terminals connected in parallel with the load.

Wattmeters are rated in terms of their maximum current, voltage, and power.  All of these ratings must be observed to prevent damage to the meter.

### Ampere-Hour Meter

The ampere-hour meter registers ampere-hours and is an integrating meter similar to the watt-hour meter used to measure electricity usage in a home.  Typical ampere-hour meters are digital indicators similar to the odometer used in automobiles.  The ampere-hour meter is a direct current meter that will register in either direction depending on the direction of current flow.  For example, starting from a given reading, it will register the amount of discharge of a battery; when the battery is placed on charge, it will operate in the opposite direction, returning once again to its starting point.  When this point is reached, the battery has received a charge equal to the discharge, and the charge is stopped.  It is normally desired to give a battery a 10 percent overcharge.  This is accomplished by designing the ampere-hour meter to run 10 percent slow in the charge direction.  These meters are subject to inaccuracies and cannot record the internal losses of a battery.  They attempt to follow the charge and discharge, but inherently do not indicate the correct state of charge.  Similar to an ammeter, the ampere-hour meter is connected in series.  Although the ampere-hour meters were used quite extensively in the past, they have been largely superseded by the voltage-time method of control.

### Power Factor Meter

A power factor meter is a type of electrodynamometer movement when it is made with two movable coils set at right angles to each other.  Two stationary coils are connected in series.  Coils are mounted on a common shaft, which is free to move without restraint or control springs.  These coils are connected with their series resistors.  At a power factor of unity, one potential coil current leads and one lags the current by 30°; thus, the coils are balanced.  A change in power factor will cause the current of one potential coil to become more in phase and the other potential coil to be more out of phase with the current, so that the moving element and pointer take a new position of balance to show the new power factor.

### Ground Detector

The ground detector is an instrument that is used to detect conductor insulation resistance to ground.  An ohmmeter, or a series of lights, can be used to detect the insulation strength of an ungrounded distribution system.  Most power distribution systems in use today are of the grounded variety type.  However, some ungrounded systems still exist.

### Synchroscope

A synchroscope indicates when two AC generators are in the correct phase relation for connecting in parallel and shows whether the incoming generator is running faster or slower than the on-line generator.  The synchroscope consists of a two-phase stator.  The two-stator windings are at right angles to one another, and by means of a phase-splitting network, the current in one phase leads the current of the other phase by 90°, thereby generating a rotating magnetic field.

The stator windings are connected to the incoming generator, and a polarizing coil is connected to the running generator.  The rotating element is unrestrained and is free to rotate through 360°.  It consists of two iron vanes mounted in opposite directions on a shaft, one at the top, and one at the bottom, and magnetized by the polarizing coil.

If the frequencies of the incoming and running generators are different, the synchroscope will rotate at a speed corresponding to the difference.  It is designed so that if incoming frequency is higher than running frequency, it will rotate in the clockwise direction; if incoming frequency is less than running frequency, it will rotate in the counterclockwise direction. When the synchroscope indicates 0° phase difference, the pointer is at the “12 o’clock” position and the two AC generators are in phase.

### Megger

The megger is a portable instrument used to measure insulation resistance.  The megger consists of a hand-driven DC generator and a direct reading ohmmeter.  The moving element of the ohmmeter consists of two coils that are rigidly mounted to a pivoted central shaft and are free to rotate over a C-shaped core.  These coils are connected by means of flexible leads.  The moving element may point in any meter position when the generator is not in operation.

As current provided by the hand-driven generator flows through the coil, the coil will tend to set itself at right angles to the field of the permanent magnet.  With the test terminals open, giving an infinite resistance, no current flows in coil A.  Thereby, coil B will govern the motion of the rotating element, causing it to move to the extreme counter-clockwise position, which is marked as infinite resistance.

### Power Quality Monitors

Power quality monitors are intended to give all necessary information about significant power quality disturbances over a long period varying from weeks to months.  These instruments identify and record the characteristics of many types of disturbances changing on a timescale of microseconds to hours.  Fast transients require high sample rate analog-to-digital converters giving a large data throughput.  Operating over a long timescale, this gives an enormous amount of data to be handled.  These instruments must either record very little of the data handled, have large storage facilities, or communicate the data to a storage facility by means of a modem.  To prevent overloading of memory with discrete event type disturbances, monitors have adjustable thresholds that determine the level at which a disturbance is recorded.

Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe safe methods for using the following portable test equipment:

Ammeter

Voltmeter

Ohmmeter

### Ammeter

Current measuring instruments must always be connected in series with a circuit and never in parallel.  Always check the polarity of the ammeter.  Make certain that the meter is connected to the circuit so that electrons flow into the negative lead of the meter and out of the positive lead of the meter.  (Normally the negative lead is black and the positive lead is red.)

Always set the full-scale deflection of the meter to be larger than the expected current.  To be safe, set the full scale current several times larger than the expected current, and then slowly increase the sensitivity to the appropriate scale.

### Voltmeter

Voltage measuring instruments must always be connected in parallel with (across the) a circuit and never in series.  Always set the full-scale voltage of the meter to be larger than the expected voltage to be measured.

Always insure that the internal resistance of the voltmeter is much greater than the resistance of the component to be measured.

### Ohmmeter

Before measuring the resistance of a circuit, always short the meter test leads together and ensure the meter indicates near zero.  Adjust the meter to indicate zero using the meter adjustment.  When the test leads are taken apart, ensure that the meter reads infinite resistance.

The power supply to the circuit to be measured must always be OFF and/or disconnected.  This prevents the circuit’s source from being applied across the meter and damaging the meter’s movement.  The ohmmeter range selection switch should be positioned so that the indicator is in the middle region of the scale.  This provides better accuracy.

Reference: Reference: DOE-HDBK-1011/4-92, DOE Fundamentals Handbook, Electrical Science, 1992

## Demonstrate a familiarity-level knowledge of the principles and concepts of natural phenomena hazards (such as static electricity, reference NFPA 77) and their effect on electrical systems.

- Discuss the potential impact of lightning on electrical systems at defense nuclear facilities.

For information regarding the impact of lightning on electrical systems see NFPA 780, Standard for the Installation of Lightning Protection Systems, 1997.

Discuss various methods of lightning protection as preventive measures (e.g., surge suppressors, Faraday cages, etc.).

It is DOE policy to install lightning protection on all facilities used for storage, processing, and handling of explosive materials where operations cannot be shut down and personnel evacuated during electrical storms.  Specific operations shall be assessed for the risk of detonation of explosives by lightning.  Such assessment shall consider the need for the protection factors outlined in appendix I, NFPA 780.  When risk is high, as in operations with highly sensitive electrostatic materials or components, operations shall be conducted only in lightning-protected facilities.  Approved lightning protection systems shall conform to the requirements of appendix I, NFPA 780.

Lightning-protection systems should be visually inspected every 7 months and a report on their conditions filed at least annually.  Any evidence of corrosion, broken wires, or connections, or any other problem that negates the system’s usefulness shall be noted and the problem repaired.

Lightning protection systems should be tested electrically every 14 months to ensure testing during all seasons, or immediately following any repair or modification.  The testing shall be conducted only with instruments designed specifically for earth-ground system testing.  The instruments shall be able to measure 10 ohms ±10°10 for ground resistance testing and 1 ohm ±10°10 for bonding testing.  Electrical resistance readings shall be recorded.

Inspection records shall contain the most recent electrical test report and any subsequent visual inspection reports for each building with a lightning-protection system.

In addition to facility lightning protection, the effects of surges resulting from lightning strikes to power distribution systems may be lessened by the use of lightning arrestors and suppressors installed at strategic points in the supply system to the facility.  An assessment addressing the consequences of lightning-induced surges is necessary to determine the degree to which protection should be provided.

A Faraday cage is an enclosure with no apertures (holes, slits, windows, or doors) made of a perfectly conducting material.  No electric fields are produced within the Faraday cage by the incidence of external fields upon it or by currents flowing on the perfect conductor; that is, the perfectly conducting enclosure is a perfect electromagnetic shield.  If no electrical energy sources are within the Faraday cage, then there will be no electric fields within, since none can penetrate the conducting enclosure.

A Faraday cage can enclose an arbitrary volume, so several rooms or buildings, which alone would each be a Faraday cage, can be joined by bonded perfectly conducting conduit to constitute a single Faraday cage.

Since a perfect conductor is an idealization unavailable in nature, perfect Faraday cages do not exist.  However, extremely good Faraday cages are constructed for electromagnetic experiments; they are commonly called screen rooms.  Early screen rooms were made of copper mesh screen with a somewhat tighter mesh than typical aluminum window screen. Screen rooms are also made of welded sheet aluminum or sheet steel.  For all screen rooms, special attention is given to electromagnetic sealing of closed doors and to metallic penetrations for power or communication.  Screen rooms are typically designed to shield the enclosed volume from low-energy, high frequency transmitted electromagnetic waves (e. g., AM/FM radio waves), but not to shield from directly attached lightning flashes.  Welded sheet metal screen rooms can provide extraordinary protection from lightning if the metal is thick enough.  However, the cost of this method is too high for many lightning protection applications involving new construction, and the method is usually impractical for existing construction.

Briefly describe the safety measures and design features commonly used as safeguards against natural hazards and identify the relevant industry consensus standards that codify accepted design and installation practices for these safeguards.

Systems, structures, and components shall be designed, constructed, and operated to withstand the effects of natural phenomena as necessary to ensure the confinement of hazardous material, the operation of essential facilities, the protection of government property, and the protection of life safety for occupants of DOE buildings.  The design process shall consider potential damage and failure of systems, structures, and components due to both direct and indirect natural phenomena effects, including common cause effects and interactions from failures of other systems, structures, and components.  Furthermore, the seismic requirements of Executive Order 12699 shall be addressed.

Systems, structures, and components for new DOE facilities, and additions or major modifications to existing systems, structures, and components shall be designed, constructed, and operated to meet the requirements in the previous paragraph.  Any additions and modifications to existing DOE facilities shall not degrade the performance of existing systems, structures, and components to the extent that the objectives cannot be achieved under the effects of natural phenomena.

There is an established hierarchy in the set of documents that specify natural phenomena hazard (NPH) requirements.  In this hierarchy, 10 CFR 830, Nuclear Safety Management, (for Nuclear Facilities only) has the highest authority followed by DOE O 420.1A, Facility Safety, and the associated Guides, DOE G 420.1-1, Nonreactor Nuclear Safety Design Criteria and Explosive Safety Criteria Guide for use with DOE O 420.1 Facility Safety, and DOE G 420.1-2, Guide for the Mitigation of Natural Phenomena Hazards for DOE Nuclear Facilities and Non Nuclear Facilities.  The four NPH standards (DOE-STDS-1020, 1021, 1022, 1023) are the last set of documents in this hierarchy.

In the event of conflicts in the information provided, the document of higher authority should be utilized (e.g., the definitions provided in the Guides should be utilized even though corresponding definitions are provided in the NPH standards).

Reference the following:

DOE-STD-1020-2002, Natural Phenomena Hazards Design and Evaluation Criteria for Department of Energy Facilities

DOE-STD-1021-93, Natural Phenomena Hazards Performance Categorization Guidelines for Structures, Systems, and Components

DOE-STD-1022-94, Natural Phenomena Hazards Site Characterization Criteria

## Demonstrate a working-level knowledge of direct current (DC) generators and motors.

Generators

- Describe the relationship between shaft speed, field flux, and generated voltage.

An electromechanical generator is a device capable of producing electrical power from mechanical energy, usually the turning of a shaft.  When not connected to a load resistance, generators will generate voltage roughly proportional to shaft speed.  With precise construction and design, generators can be built to produce very precise voltages for certain ranges of shaft speeds, thus making them well-suited as measurement devices for shaft speed in mechanical equipment.

Fields have two measures: a field force and a field flux.  The field force is the amount of push that a field exerts over a certain distance.  The field flux is the total quantity, or effect, of the field through space.  Field force and flux are roughly analogous to voltage and current (flow) through a conductor, respectively, although field flux can exist in totally empty space (without the motion of particles such as electrons) whereas current can only take place where there are free electrons to move.  Field flux can be opposed in space, just as the flow of electrons can be opposed by resistance.  The amount of field flux that will develop in space is proportional to the amount of field force applied, divided by the amount of opposition to flux.  Just as the type of conducting material dictates that conductor’s specific resistance to electric current, the type of insulating material separating two conductors dictates the specific opposition to field flux.

Reference: All About Circuits, http://www.allaboutcircuits.com/vol_1/chpt_13/1.html

Define the following:

Electromotive force

Excitation

Compounding

Armature

Terminal voltage

Load current

Shunt windings

Series windings

### Electromotive Force

Electromotive force is the force that causes electricity to flow between two points with different electrical charges, or the difference of potential between the two points.

### Excitation

The magnetic fields in DC generators are most commonly provided by electromagnets.  A current must flow through the electromagnet conductors to produce a magnetic field.  In order for a DC generator to operate properly, the magnetic field must always be in the same direction.  Therefore, the current through the field winding must be direct current.  This current is known as the field excitation current and can be supplied to the field winding in one of two ways.  It can come from a separate DC source external to the generator (e.g., a separately excited generator) or it can come directly from the output of the generator, in which case it is called a self-excited generator.

In a self-excited generator, the field winding is connected directly to the generator output. The field may be connected in series with the output, in parallel with the output, or a combination of the two.

Separate excitation requires an external source, such as a battery or another DC source.  It is generally more expensive than a self-excited generator.  Separately excited generators are, therefore, used only where self-excitation is not satisfactory.  They would be used in cases where the generator must respond quickly to an external control source or where the generated voltage must be varied over a wide range during normal operations.

### Compounding

The compound generator has a field winding in parallel with the generator armature (the same as a shunt-wound generator) and a field winding in series with the generator armature (the same as a series-wound generator).

The two windings of the compounded generator are made such that their magnetic fields will either aid or oppose one another.

If the two fields are wound so that their flux fields oppose one another, the generator is said to be differentially compounded.  Due to the nature of this type of generator, it is used only in special cases.

If the two fields of a compound generator are wound so that their magnetic fields aid one another, the generator is said to be cumulatively compounded.  As the load current increases, the current through the series field winding increases, increasing the overall magnetic field strength and causing an increase in the output voltage of the generator.  With proper design, the increase in the magnetic field strength of the series winding will compensate for the decrease in shunt field strength.  Therefore, the overall strength of the combined magnetic fields remains almost unchanged, so the output voltage will remain constant.  In reality, the two fields cannot be made so that their magnetic field strengths compensate for each other completely.  There will be some change in output voltage from the no-load to full-load conditions.

### Armature

The purpose of the armature is to provide the energy conversion in a DC machine.  In a DC generator, an external mechanical force, such as a steam turbine, rotates the armature.

This rotation induces a voltage and current flow in the armature.  Thus, the armature converts mechanical energy to electrical energy.

In a DC motor, the armature receives voltage from an outside electrical source and converts electrical energy into mechanical energy in the form of torque.

### Terminal Voltage

Terminal voltage, as applied to DC generators, is defined as the voltage that can be measured at the output of the generator.

### Load Current and Shunt Windings

When the field winding of a generator is connected in parallel with the generator armature, the generator is called a shunt-wound generator.

In the shunt-wound generator, the battery voltage is connected across the field winding.  A steady current (equal to the battery voltage divided by the resistance of the field winding) flows in the field winding, causing it to become an electromagnet.  Usually the field winding is brought out separately from the armature, so the motor has four wires.  With an ohmmeter you can check that there are in fact two windings, a high resistance one (the field) and a low resistance one (the armature).  To control the speed, connect the field winding directly across the battery and drive the armature from a controller.

The excitation current in a shunt-wound generator depends on the output voltage and the field resistance.  Normally, field excitation is maintained between 0.5 and 5 percent of the total current output of the generator.

The shunt-wound generator, running at a constant speed under varying load conditions, has a much more stable voltage output than does a series-wound generator.  Some change in output voltage does take place.  This change is caused by the fact that, as the load current increases, the voltage drop across the armature coil increases, causing output voltage to decrease.  As a result, the current through the field decreases, reducing the magnetic field and causing voltage to decrease even more.  If load current is much higher than the design of the generator, the drop in output voltage is severe.  For load current within the design range of the generator, the drop in output voltage is minimal.

### Series Windings

In a series-wound motor, the armature current flows through the field winding, which is a high-current winding in series with the armature.  Both windings will be low resistance and, with an ohmmeter, it can be difficult to tell them apart.

This series connection gives the series-wound motor a performance much different than the shunt-wound types.

One feature of series-wound motors is that they don’t have a theoretical top speed: as the armature speed increases, the current reduces.  As it does so, the magnetic field reduces. As the field reduces, the motor needs to rotate faster to give the same back EMF.  As the current reduces to zero, the perfect motor would get faster and faster to give an infinite top speed under zero loading.  Fortunately perfect motors don't exist and there is always some residual magnetic field and some friction.  Nevertheless some early traction motors had a nasty habit of over-revving to destruction if a drive shaft broke.  This over-revving is also the rationale behind compound-wound motors, where an extra shunt-wound field provides a permanent field to restrict field reduction and to limit top speed.

This feature of the series-wound motor makes it a good choice for open road vehicles, where a limited top speed isn’t so desirable, and where you want to gain momentum down one hill to get up the next.  However, when you run a series-wound motor at slow speed with a small mechanical load it becomes very inefficient.

Reference: DOE-HDBK-1011/1-92, DOE Fundamentals Handbook, Electrical Science, 1992

State the purpose of the following components of a DC machine:

Armature

Rotor

Stator

Field

### Armature

The purpose of an armature is to provide the energy conversion in a DC machine.

### Rotor

The purpose of the rotor is to provide the rotating element in a DC machine.

### Stator

The stator is the part of a motor or generator that is stationary.  In DC machines, the purpose of the stator is to provide the magnetic field.

### Field

The purpose of the field in a DC machine is to provide a magnetic field for producing either a voltage or a torque.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe self-excited and separately excited generators.

In a self-excited generator, the field winding is connected directly to the generator output.  The field may be connected in series with the output, in parallel with the output, or a combination of the two.

Separate excitation requires an external source, such as a battery or another DC source.  It is generally more expensive than a self-excited generator.  Separately excited generators are, therefore, used only where self-excitation is not satisfactory.  They would be used in cases where the generator must respond quickly to an external control source or where the generated voltage must be varied over a wide range during normal operations.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the operation of compound-wound generators.

If the two fields are wound so that their flux fields oppose one another, the generator is said to be differentially compounded.  Due to the nature of this type of generator, it is used only in special cases.

If the two fields of a compound generator are wound so that their magnetic fields aid one another, the generator is said to be cumulatively compounded.  As the load current increases, the current through the series field winding increases, increasing the overall magnetic field strength and causing an increase in the output voltage of the generator.

With proper design, the increase in the magnetic field strength of the series winding will compensate for the decrease in shunt field strength.  Therefore, the overall strength of the combined magnetic fields remains almost unchanged, so the output voltage will remain constant.  In reality, the two fields cannot be made so that their magnetic field strengths compensate for each other completely.  There will be some change in output voltage from the no-load to full-load conditions.

In practical compounded generators, the change in output voltage from no-load to full-load is less than 5 percent.  A generator with this characteristic is said to be flat-compounded.

For some applications, the series winding is wound so that it overcompensates for a change in the shunt field.  The output gradually rises with increasing load current over the normal operating range of the machine.  This type of generator is called an over-compounded generator.

The series winding can also be wound so that it under compensates for the change in shunt field strength.  The output voltage decreases gradually with an increase in load current.

This type of generator is called an under-compounded generator.

Reference: http://www.tpub.com/content/doe/h1011v2/css/h1011v2_94.htm

Describe how the terminal voltage of a DC generator is adjusted.

DC generator output voltage is dependent on three factors (1) the number of conductor loops in series in the armature, (2) armature speed, and (3) magnetic field strength.  To change the generator output, one of these three factors must be varied.  The number of conductors in the armature cannot be changed in a normally operating generator, and it is usually impractical to change the speed at which the armature rotates.  The strength of the magnetic field, however, can be changed quite easily by varying the current through the field winding.  This is the most widely used method for regulating the output voltage of a DC generator.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

State the basis behind each DC generator rating.

DC generators are rated by current, speed, voltage, and power.  Current is based on the size of the conductor and the amount of heat that can be dissipated in the generator.  Speed is based at the upper limit and is determined by the point at which mechanical damage is done to the machine.  The lower rating is based on the limit for field current.  Voltage is based on the insulation type and design of the machine.  Power is based on the mechanical limitations of the device that is used to turn the generator, and on the thermal limits of conductors, bearings, and other components of the generator.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the internal losses found in a direct current generator.

### Copper Loss

Copper loss is the power lost as heat in the windings.  It is caused by the flow of current through the coils of the DC armature or DC field.  This loss varies directly with the square of the current in the armature or field and the resistance of the armature or field coils.

### Eddy-Current Loss

As the armature rotates within the field, it cuts the lines of flux at the same time that the copper coils of wire that are wound on the armature cut the lines of flux. Since the armature is made of iron, an EMF is induced in the iron, which causes a current to flow.  These circulating currents within the iron core are called eddy-currents.

### Hysteresis Loss

Hysteresis loss occurs when the armature rotates in a magnetic field.  The magnetic domains of the armature are held in alignment with the field in varying numbers, dependent on field strength.  The magnetic domains rotate, with respect to the particles not held in alignment, by one complete turn during each rotation of the armature.  This rotation of magnetic domains in the iron causes friction and heat.  The heat produced by this friction is called magnetic hysteresis loss.

Rotational or Mechanical Loss

Rotational or mechanical loss can be caused by bearing friction, brush friction on the commutator, or air friction (called windage), which is caused by the air turbulence due to armature rotation.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the differences in construction between a shunt-wound and a series-wound direct current generator with respect to the relationship between the field and the armature.

When the field winding of a generator is connected in parallel with the generator armature, the generator is called a shunt-wound generator.  The excitation current in a shunt-wound generator is dependent on the output voltage and the field resistance.  Normally, field excitation is maintained between 0.5 and 5 percent of the total current output of the generator.

When the field winding of a DC generator is connected in series with the armature, the generator is called a series-wound generator.  The excitation current in a series-wound generator is the same as the current the generator delivers to the load.  If the load has a high resistance and only draws a small amount of current, the excitation current is also small. Therefore, the magnetic field of the series field winding is weak, making the generated voltage low.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the relationship between the shunt and series fields for cumulatively compounded and differentially compounded direct current generators.

Series-wound and shunt-wound generators have a disadvantage in that changes in load current cause changes in generator output voltage.  Many applications in which generators are used require a more stable output voltage than can be supplied by a series-wound or shunt-wound generator. One means of supplying a stable output voltage is by using a compound generator.

The compound generator has a field winding in parallel with the generator armature (the same as a shunt-wound generator) and a field winding in series with the generator armature (the same as a series-wound generator).

The two windings of the compounded generator are made such that their magnetic fields will either aid or oppose one another.

If the two fields are wound so that their flux fields oppose one another, the generator is said to be differentially compounded.  Due to the nature of this type of generator, it is used only in special cases.

If the two fields of a compound generator are wound so that their magnetic fields aid one another, the generator is said to be cumulatively compounded.  As the load current increases, the current through the series field winding increases, increasing the overall magnetic field strength and causing an increase in the output voltage of the generator.  With proper design, the increase in the magnetic field strength of the series winding will compensate for the decrease in shunt field strength.  Therefore, the overall strength of the combined magnetic fields remains almost unchanged, so the output voltage will remain constant.  In reality, the two fields cannot be made so that their magnetic field strengths compensate for each other completely.  There will be some change in output voltage from the no-load to full-load conditions.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the voltage-versus-current characteristics for a flat-compounded, over-compounded, and under-compounded direct current generator.

In practical compounded generators, the change in output voltage from no-load to full-load is less than 5 percent.  A generator with this characteristic is said to be flat-compounded.

For some applications, the series winding is wound so that it overcompensates for a change in the shunt field.  The output gradually rises with increasing load current over the normal operating range of the machine.  This type of generator is called an over-compounded generator.

The series winding can also be wound so that it under compensates for the change in shunt field strength.  The output voltage decreases gradually with an increase in load current.  This type of generator is called an under-compounded generator.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Motors

- Describe the basic construction and operation of the following four types of DC motors:

Shunt

Separately excited

Compound-wound

Series

### Shunt

A shunt-wound DC motor has a decreasing torque when speed increases.  The decreasing torque-vs-speed is caused by the armature resistance voltage drop and armature reaction.  At a value of speed near 2.5 times the rated speed, armature reaction becomes excessive, causing a rapid decrease in field flux and a rapid decline in torque until a stall condition is reached.

The characteristics of a shunt-wound motor give it very good speed regulation, and it is classified as a constant-speed motor, even though the speed does slightly decrease as load is increased.  Shunt-wound motors are used in industrial and automotive applications where precise control of speed and torque are required.

### Separately Excited

Separate excitation requires an external source, such as a battery or another DC source.  Separately excited motors are, therefore, used only where self-excitation is not satisfactory. They would be used in cases where the motor must respond quickly to an external control source or where the generated voltage must be varied over a wide range during normal operations.

### Compound-Wound

The compounded motor is desirable for a variety of applications because it combines the characteristics of a series-wound motor and a shunt-wound motor.  The compounded motor has a greater torque than a shunt motor due to the series field; however, it has a fairly constant speed due to the shunt field winding.  Loads such as presses, shears, and reciprocating machines are often driven by compounded motors.

### Series

Since the armature and field in a series-wound motor are connected in series, the armature and field currents become identical.  As the speed decreases, the torque for a series-wound motor increases sharply.  As load is removed from a series motor, the speed will increase sharply.  For these reasons, series-wound motors must have a load connected to prevent damage from high-speed conditions.

The advantage of a series-wound motor is that it develops a large torque and can be operated at low speed.  It is a motor that is well suited for starting heavy loads.  It is often used for industrial cranes and winches where very heavy loads must be moved slowly, and lighter loads moved more rapidly.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

State the function of torque in a DC motor and how it is developed.

Torque is defined as that force which tends to produce and maintain rotation.  The function of torque in a DC motor is to provide the mechanical output or drive the piece of equipment that the DC motor is attached to.

When a voltage is applied to a motor, current will flow through the field winding, establishing a magnetic field.  Current will also flow through the armature winding, from the negative brush to the positive brush.  Since the armature is a current-carrying conductor in a magnetic field, the conductor has a force exerted on it, tending to move it at right angles to that field.  Using the left-hand rule for current-carrying conductors, you will see that the magnetic field on one side is strengthened at the bottom, while it is weakened on the other side.  Using the right-hand rule for motors, we can see that there is a force exerted on the armature that tends to turn the armature in the counter-clockwise direction.  The sum of the forces, in pounds, multiplied by the radius of the armature, in feet, is equal to the torque developed by the motor in pound-feet (lb-ft).

The force that is developed on a conductor of a motor armature is due to the combined action of the magnetic fields.  The force developed is directly proportional to the strength of the main field flux and the strength of the field around the armature conductor.  The field strength around each armature conductor depends on the amount of current flowing through the armature conductor.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the function of CEMF and how it is developed in a DC motor.

A generator action is developed in every motor.  When a conductor cuts lines of force, an EMF is induced in that conductor.  Current to start the armature turning will flow in the direction determined by the applied DC power source.  After rotation starts, the conductor cuts lines of force.  By applying the left-hand rule for generators, the EMF that is induced in the armature will produce a current in the opposite direction.  The induced EMF, as a result of motor operation, is called counter-electromotive force, or CEMF.

Since the CEMF is generated by the action of the armature cutting lines of force, the value of the CEMF will depend on field strength and armature speed.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the relationship between field current and magnetic field size in a DC motor.

There are two conditions that are necessary to produce a force on a conductor.  The conductor must be carrying current and the conductor must be within a magnetic field.  When these two conditions exist, a force will be applied to the conductor, which will attempt to move the conductor in a direction perpendicular to the magnetic field.  This is the basic theory by which all DC motors operate.

Every current-carrying conductor has a magnetic field around it.  The direction of this magnetic field may be found by using the left-hand rule for current-carrying conductors.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe how to adjust the speed of a DC motor.

The field of a DC motor is varied using external devices, usually field resistors.  For a constant applied voltage to the field (E), as the resistance of the field (Rf) is lowered, the amount of current flow through the field (If) increases as shown by Ohm’s law in the following equation.

An increase in field current will cause field flux (Фf) to increase.  Conversely, if the resistance of the field is increased, field flux will decrease.  If the field flux of a DC motor is decreased, the motor speed will increase.  The reduction of field strength reduces the CEMF of the motor, since fewer lines of flux are being cut by the armature conductors, as shown in the following equation.

A reduction of CEMF allows an increase in armature current as shown in the following equation.

This increase in armature current causes a larger torque to be developed.  The increase in armature current more than offsets the decrease in field flux as shown in the following equation.

This increased torque causes the motor to increase in speed.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the relationship between armature current and torque produced in a DC motor.

When a voltage is applied to a motor, current will flow through the field winding, establishing a magnetic field.  Current will also flow through the armature winding.  Since the armature is a current-carrying conductor in a magnetic field, the conductor has a force exerted on it, tending to move it at right angles to that field.  Using the left-hand rule for current-carrying conductors, you will see that the magnetic field is strengthened on one side, while it is weakened on the other side.  Using the right-hand rule for motors, we can see that there is a force exerted on the armature that tends to turn the armature in the counter-clockwise direction.

The force that is developed on a conductor of a motor armature is due to the combined action of the magnetic fields.  The force developed is directly proportional to the strength of the main field flux and the strength of the field around the armature conductor.  The field strength around each armature conductor depends on the amount of current flowing through the armature conductor.  Therefore, the torque that is developed by the motor can be determined using the equation below.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the torque-versus-speed characteristics for a shunt-wound and a series-wound DC motor.

A shunt-wound DC motor has a decreasing torque when speed increases.  The decreasing torque-vs-speed is caused by the armature resistance voltage drop and armature reaction.  At a value of speed near 2.5 times the rated speed, armature reaction becomes excessive, causing a rapid decrease in field flux and a rapid decline in torque until a stall condition is reached.

A series-wound motor works differently.  As the speed decreases, the torque for a series-wound motor increases sharply.  As load is removed from a series motor, the speed will increase sharply.  For these reasons, series-wound motors must have a load connected to prevent damage from high-speed conditions.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Explain why starting resistors may be necessary for large DC motors.

Initially the only component to limit starting current is the armature resistance, which in most DC motors is a very low value.  At the moment a DC motor is started, the armature is stationary and there is no CEMF being generated.

External resistors are placed in series with the armature during the starting period.  Starting resistors are usually incorporated into the motor design to limit starting current to 125 to 200 percent of full-load current.

Without external resistors to prevent the large current flow before the CEMF is established, the large current could cause severe damage to the brushes, commutator, or windings.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

## Demonstrate a working-level knowledge of battery construction, voltage production, and hazards.  IEEE Std 450. Maintenance, Testing and Replacement of Vented Lead-Acid Batteries for Stationary Applications.

- Using a cutaway drawing of a simple multi-cell storage battery, identify the following components and discuss their function:

Positive terminal

Negative terminal

Electrode

Cell

The purpose of a battery is to store chemical energy and to convert this chemical energy into electrical energy when the need arises.

A chemical cell (or voltaic cell) consists of two electrodes of different types of metals or metallic compounds and an electrolyte solution that is capable of conducting an electric current.

A good example of a voltaic cell is one that contains zinc and copper electrodes.  The zinc electrode contains an abundance of negatively charged atoms, and the copper electrode contains an abundance of positively charged atoms.  When these electrodes are immersed in an electrolyte, chemical action begins.  The zinc electrode will accumulate a much larger negative charge because it dissolves into the electrolyte.  The atoms, which leave the zinc electrode, are positively charged and are attracted by the negatively charged ions of the electrolyte; the atoms repel the positively charged ions of the electrolyte toward the copper electrode.

This action causes electrons to be removed from the copper electrode, leaving it with an excess of positive charge.  If a load is connected across the electrodes, the forces of attraction and repulsion will cause the free electrons in the negative zinc electrode to move through the connecting wire and load, and toward the positive copper electrode.

The potential difference that results allows the cell to function as a source of applied voltage.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the hazards associated with storage batteries.

Because batteries store large amounts of energy, there are certain hazards that are associated with battery operation.  These hazards must be fully understood to ensure safe operation of batteries.  Hazards associated with storage batteries fall into three categories: shorted cells, gas generation, and battery temperature.

### Shorted Cells

Cell short circuits can be caused by several conditions, which include the following:

Faulty separators

Lead particles or other metals forming a circuit between the positive and negative plates

Buckling of the plates or excessive sediments in the bottom of the jar

The primary cause of some of these occurrences is overcharging and over discharging of the battery, which causes sediment to build up due to flaking of active material and buckling of cell plates.  Overcharging and over discharging should be avoided at all costs.  Short circuits cause a great reduction in battery capacity.  With each shorted cell, battery capacity is reduced by a percentage equal to one over the total number of cells.

### Gas Generation

A lead-acid battery cannot absorb all the energy from the charging source when the battery is nearing the completion of the charge.  This excess energy dissociates water by way of electrolysis into hydrogen and oxygen.  Oxygen is produced by the positive plate, and hydrogen is produced by the negative plate.  This process is known as gassing.

Gassing is first noticed when cell voltage reaches 2.30–2.35 volts per cell and increases as the charge progresses.  At full charge, the amount of hydrogen produced is about 1 cubic foot per cell for each 63 ampere-hours input.  If gassing occurs and the gases are allowed to collect, an explosive mixture of hydrogen and oxygen can be readily produced.  It is necessary, therefore, to ensure that the area is well ventilated and that it remains free of any open flames or spark-producing equipment.

As long as battery voltage is greater than 2.30 volts per cell, gassing will occur and cannot be prevented entirely.  To reduce the amount of gassing, charging voltages above 2.30 volts per cell should be minimized (e.g., 13.8 volts for a 12-volt battery).

### Battery Temperature

The operating temperature of a battery should preferably be maintained in the nominal band of 60ºF–80°F.  Whenever the battery is charged, the current flowing through the battery will cause heat to be generated by the electrolysis of water.  The current flowing through the battery (I) will also cause heat to be generated (P) during charge and discharge as it passes through the internal resistance (Ri), as illustrated using the formula for power in the following equation.

P = I2Ri

Higher temperatures will give some additional capacity, but they will eventually reduce the life of the battery.  Very high temperatures, 125°F and higher, can actually do damage to the battery and cause early failure.

Low temperatures will lower battery capacity but also prolong battery life under floating (i.e., slightly charging) operation or storage.  Extremely low temperatures can freeze the electrolyte, but only if the battery is low in specific gravity.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Define the following terms:

Voltaic cell

Battery

Electrode

Electrolyte

Specific gravity

Ampere-hour

Electrolysis

Equalizing charge

Float charge

Pilot cell

### Voltaic Cell

A voltaic cell is a combination of materials used to convert chemical energy into electrical energy.  A voltaic or chemical cell consists of two electrodes of different types of metals or metallic compounds and an electrolyte solution that is capable of conducting an electric current.

### Battery

A battery is a group of two or more connected voltaic cells.

### Electrode

An electrode is a metallic compound, or metal, that has an abundance of electrons (negative electrode) or an abundance of positive charges (positive electrode).

### Electrolyte

An electrolyte is a solution that is capable of conducting an electric current.  The electrolyte of a cell may be a liquid or a paste.  If the electrolyte is a paste, the cell is referred to as a dry cell.  If the electrolyte is a solution, it is called a wet cell.

### Specific Gravity

Specific gravity is defined as the ratio comparing the weight of any liquid to the weight of an equal volume of water.  The specific gravity of pure water is 1.000.  Lead-acid batteries use an electrolyte that contains sulfuric acid.  Pure sulfuric acid has a specific gravity of 1.835, since it weighs 1.835 times as much as pure water per unit volume.

### Ampere-Hour

An ampere-hour is defined as a current of one ampere flowing for one hour.  If you multiply the current in amperes by the time of flow in hours, the result is the total number of ampere-hours.  Ampere-hours are normally used to indicate the amount of energy a storage battery can deliver.

### Electrolysis

Electrolysis is the process in which an electric current, flowing through a water solution of a chemical, breaks that compound up into its component parts.

### Equalizing Charge

An equalizing charge is a controlled over charge of a battery bank for the purpose of restoring the equality of charge in all cells.

### Float Charge

A float charge is the voltage required to counteract the self-discharge of the battery at a certain temperature.

### Pilot Cell

A pilot cell is a storage battery cell tested to determine the condition of the entire battery.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the operation of a simple voltaic cell.

A voltaic cell consists of two electrodes of different types of metals or metallic compounds and an electrolyte solution that is capable of conducting an electric current.  A good example of a voltaic cell is one that contains zinc and copper electrodes.  When these electrodes are immersed in an electrolyte, chemical action begins.  The zinc electrode will accumulate a much larger negative charge because it dissolves into the electrolyte.  The atoms that leave the zinc electrode are positively charged and are attracted by the negatively charged ions of the electrolyte.  The atoms repel the positively charged ions of the electrolyte toward the copper electrode.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Explain the relationship between specific gravity and state of charge of a lead-acid battery.

The specific gravity increases.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the relationship between total battery voltage and individual cell voltage for a series-connected battery.

When several cells are connected in series, the total voltage output of the battery is equal to the sum of the individual cell voltages.  In the example of the battery in figure 2, the four 1.5V cells provide a total of 6 volts.  When we connect cells in series, the positive terminal of one cell is connected to the negative terminal of the next cell.  The current flow through a battery connected in series is the same as for one cell.

Figure 2. Cells connected in a series

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Explain the advantage of connecting a battery in parallel with respect to current-carrying capability.

Cells connected in parallel give the battery a greater current capacity.  When cells are connected in parallel, all the positive terminals are connected together, and all the negative terminals are connected together.  The total voltage output of a battery connected in parallel is the same as that of a single cell.

Cells connected in parallel have the same effect as increasing the size of the electrodes and electrolyte in a single cell.  The advantage of connecting cells in parallel is that it will increase the current-carrying capability of the battery.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the difference between primary and secondary cells with respect to recharge capability.

Cells that cannot be returned to good condition, or recharged after their voltage output has dropped to a value that is not usable, are called primary cells.  Dry cells that are used in flashlights and transistor radios (e.g., AA cells, C cells) are examples of primary cells.

Cells that can be recharged to nearly their original condition are called secondary cells.  The most common example of a secondary or rechargeable cell is the lead-acid automobile battery.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

State the advantages of each of the following types of batteries:

Carbon-zinc cell

Alkaline cell

Nickel-cadmium cell

Edison cell

Mercury cell

The advantages of each type of battery are listed below:

The carbon-zinc cell is durable, inexpensive, and comes in a variety of sizes.

The alkaline cell has extended life over that of a carbon-zinc cell of the same size.

The nickel-cadmium cell is a dry cell that can be recharged.  It is a rugged dependable battery under extreme conditions of temperature, shock, and vibration.  It has a long shelf life, heavy weight, large volume, and minimal temperature effect.

The Edison cell is a lighter and more rugged secondary cell than a lead-acid storage battery.

The mercury cell is very rugged, has a relatively long shelf life, provides constant output over varying load, and has the highest capacity of all the cell types.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Explain how gas generation is minimized for a lead-acid battery and the steps to prevent hydrogen buildup.

To reduce the amount of gassing, charging voltages above 2.30 volts per cell should be minimized (e.g., 13.8 volts for a 12-volt battery).

A lead-acid battery cannot absorb all the energy from the charging source when the battery is nearing the completion of the charge.  This excess energy dissociates water by way of electrolysis into hydrogen and oxygen.  At full charge, the amount of hydrogen produced is about one cubic foot per cell for each 63 ampere-hours input.  If gassing occurs and the gases are allowed to collect, an explosive mixture of hydrogen and oxygen can be readily produced.  It is necessary, therefore, to ensure that the area is well ventilated and that it remains free of any open flames or spark-producing equipment.

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Explain how heat is generated in a lead-acid battery.

Whenever the battery is charged, the current flowing through the battery will cause heat to be generated by the electrolysis of water.  The current flowing through the battery (I) will also cause heat to be generated (P) during charge and discharge as it passes through the internal resistance (Ri), as illustrated using the formula for power in the following equation.

P = I2Ri

Reference: DOE-HDBK-1011/2-92, DOE Fundamentals Handbook, Electrical Science, 1992

Describe the various uses of battery banks in DOE facilities.

As the use of battery banks in DOE facilities varies from site to site, the local qualifying official will evaluate the completion of this competency.

Describe how batteries are tested.

As the type of batteries and testing methods vary from site to site, the local qualifying official will evaluate the completion of this competency.

II. ELECTRICAL ISSUE IDENTIFICATION & REPORTING

(Each competency statement is a MPA, provided that they are applicable to the candidate’s assigned electrical duties.)

## Demonstrate a working-level knowledge of surveillance and assessment techniques; reporting; and follow up actions for electrical systems and programmatic elements of an Electrical Safety Program to include:

Management systems;

Problem remediation and trends processes;

Inspection programs;

Training and qualification programs;

Oversight of contractor assurance systems.

- Describe the role of electrical systems personnel in performance oversight of government-owned, contractor-operated (GOCO) facilities.

The role of electrical systems personnel is to ensure that electrical safety requirements necessary for a practical safeguarding of applicable DOE facilities and personnel are being adequately implemented.  Practical safe work procedures include training of skilled and unskilled personnel who have a risk of electrical shock.  For exposure to energized components, safety measures shall protect personnel against both direct contact and indirect contact through use of some conducting medium such as a pole, a ladder, or an effective energy-isolation program, such as lockout/tagout.  In addition, only qualified persons who are capable of working safely on energized circuits and are familiar with the proper use of special precautionary techniques, personal protective equipment, insulating and shielding material, and insulated tools may work on energized equipment.  Electrical systems personnel perform DOE line management oversight of their assigned facilities to ensure that

the contractor is operating facilities safely and efficiently (i.e., within the boundaries of those controls invoked in the facility authorization basis);

the contractor’s management system is effectively controlling conduct of operation as related to electrical systems;

effective lines of communication between DOE and its operating contractors are maintained during periods of normal operation, and following reportable events, in accordance with DOE Orders and requirements.

Reference: Facilities Maintenance Management Reference Guide, July 2006

Describe the assessment requirements and limitations associated with the interface of electrical systems personnel and contractor employees.

As assessment requirements and limitations associated with the interface of electrical systems personnel and contractor employees vary from site to site, the local qualifying official will evaluate the completion of this competency.

Describe how planning, observations, interviews, and document research are used during an assessment.

Effective assessments use a combination of tools and techniques to maximize the productivity of the assessment team and resources.  Such assessment techniques include document reviews, interviews, and observations.  In using these techniques, the assessor should not forget that the objective is to verify accomplishment of an organization’s mission.  To save time, the assessor should gather only data and information relevant to overall program performance and the achievement of program objectives.

It is generally not acceptable to identify suspicions about the adequacy or inadequacy of a program, system, or process.  Investigations should be sufficiently thorough and information gathered with sufficient diligence that accurate, detailed conclusions and issues can be provided to assist the organizations that will receive the final report.

In using any of these techniques, assessors should maintain good records of the assessment results.  These may include personal notes or other information to support the assessment and may be included in the checklist information.  These records are useful in writing the report and any associated findings and recommendations and will become invaluable if questions arise during the report review process.  All classified notes should be disposed of properly in accordance with established and agreed-upon procedures.  A discussion of each of the techniques follows.

Document review.  Document review is used extensively during an assessment to substantiate the information obtained during interviews and observation.  During the course of an assessment, questions may arise concerning what is heard and seen.  The review of documents, including logs, procedures, work orders, and other data provides a method for answering these questions and validating the assessment results.  The drawback of document review is that the accuracy of the records cannot be ascertained by review alone.  This technique should be combined with interviews, observation, inspection, and/or performance testing to complete the picture of performance.  Records and documents should be selected carefully to ensure they adequately characterize the program, system, or process being assessed.

Interviews.  Interviews provide a means to verify the results of observation, document review, inspection, and performance testing.  In addition, interviews allow the responsible person to explain and clarify those results.  The interview helps to eliminate misunderstandings about program implementation and provides a venue where apparent conflicts or recent changes can be discussed and the organization and program expectations can be described.  Tools developed during assessment planning are used to prepare for the interview.  Assessors should also prepare questions in advance to keep the interview focused.

Observation.  Observation, the viewing of actual work activities, is often considered the most effective technique for determining whether performance is adequate.  Assessors should understand the effect their presence has on the person being observed and convey an attitude that is helpful, constructive, positive, and unbiased.  The primary goal during observation is to obtain the most complete picture possible of the performance, which should then be put into perspective relative to the overall program, system, or process.

Before drawing final conclusions, the assessor should verify the results through at least one other technique.

Reference: Facilities Maintenance Management Reference Guide, July 2006

Explain the essential elements of a performance-based assessment, including investigation, fact-finding, and reporting.  Include a discussion of the essential elements and processes of the following assessment activities:

Exit interview

Closure process

Tracking to closure

Follow-up

Contractor corrective action implementation

### Exit Interview

Assessments can gain value from an exit interview.  This interview is used primarily to present the assessment summary and provide the assessed organization an opportunity to verify the factual accuracy of assessment results.  To facilitate this, assessors should be prepared to provide detailed supporting information for those results (ideally, a draft assessment report should be available at this time).  This interview also offers an opportunity for the assessed organization to present its management position and any plans for addressing the results.  Reasonable time should be allowed to discuss any concerns, but this interview should not be used to argue the assessment agenda or methodology.

### Closure Process

In the closure process, contractors send a letter to the directives management group (DMG) requesting closure and stating that the corrective actions in the implementation plan have been completed.  The DMG coordinates approval of the closure with the appropriate division of primary interest and the contracting officer’s representative.

### Tracking to Closure

### After a reasonable period of time has elapsed, follow-up activities should be performed to verify the effectiveness of the corrective action and how it was implemented.  This is referred to as tracking to closure.  There are several ways to verify the implementation of corrective action, including

a reassessment of the deficient areas;

review of new or revised quality-affecting documents such as manuals, procedures, training records;

verification during the next scheduled assessment;

verification by conducting a surveillance covering the areas of concern.

The key thing to remember when verifying corrective action implementation is that verification is necessary.  A solution to a problem may look good on paper but may not be readily implementable.  The failure to adequately identify all root causes will most likely result in a recurrence of the deficiency.  Therefore, an appropriate amount of follow-up is necessary to assure the effectiveness of the corrective action process and to reestablish confidence in the item/service assessed.

### Follow-up

After a reasonable period of time has elapsed, follow-up activities should be performed to verify the effectiveness of the corrective actions and how they were implemented.  The verification should, at a minimum, sample the corrective actions to determine whether the problem/issue to be addressed has been resolved.  The organization's reporting systems (e.g., noncompliance tracking system, occurrence reporting and processing system, external oversight reports and regulatory violations, performance indicators) should be reviewed for evidence of the problem (or a similar problem) recurring.  The same techniques used to conduct assessments may be used for verifying corrective actions; however, there are several common ways to verify the implementation of corrective actions, including the following:

Reassessment of the deficient areas

Review of new or revised quality-affecting documents such as manuals, procedures, and training records

Verification during the next scheduled assessment

Verification by conducting a surveillance covering the areas of concern

### Contractor Corrective Action Implementation

Management responsible for the activities assessed is also responsible for the development of effective corrective action of the problem areas or deficiencies discovered during the assessment.  At a minimum, the corrective action should address

measures to correct each deficiency

identification of all root causes for significant deficiencies

determination of the existence of similar deficiencies

corrective actions to preclude recurrence of like or similar deficiencies

assignment of corrective action responsibility

completion dates for each corrective action

For independent assessments, the proposed corrective action should be reviewed for concurrence by the assessment team leader.  This will help ensure that the planned actions will be effective in resolving the problem areas and deficiencies reported by the assessment team.

Reference: Facilities Maintenance Management Reference Guide, July 2006

Describe the actions to be taken if the contractor challenges the assessment findings and explain how such challenges can be avoided.

Disputes over the assessment findings, the corrective action plan, or its implementation (such as timeliness or adequacy) must be resolved at the lowest possible organizational level.  The organization that disagrees with the disposition of a given issue may elevate the dispute for timely resolution.  The organization that disagrees with the disposition of a given issue must elevate the dispute in a step-wise manner through the management hierarchy.  The dispute must be raised via a deliberate and timely dispute resolution process that provides each party with equal opportunity for input and a subsequent opportunity to appeal decisions up to the Secretary of Energy, if necessary.

Reference: Facilities Maintenance Management Reference Guide, July 2006

Describe the methods by which noncompliance is determined and communicated to contractor and Department management.

During the assessment of contractor activities there are certain criteria useful in determining the acceptance or noncompliance of an item or activity.  The following criteria summarized from 10 CFR 830.120, Quality Assurance, provide the basis for contractor assessments:

Programs. Organizations shall develop a written plan that describes the organizational structure, functional responsibilities, levels of authority, and interfaces for those managing, performing, and assessing adequacy of work.

Personnel training and qualifications. Personnel shall be trained and qualified to ensure they are capable of performing their assigned work.  Training should emphasize correct performance of work, provide understanding of quality requirements, and stimulate professional development.

Quality improvement. The organization shall establish and implement processes to detect and prevent quality problems and to ensure quality improvement.  Items and processes that do not meet established requirements shall be identified, controlled, and corrected.  Correction shall include: identifying the cause of the problems and preventing reoccurrence.  Item reliability, process implementation, and other quality-related information shall be reviewed and data analyzed to identify items and processes needing improvement.

Documents and records. Documents shall be prepared, reviewed, approved, issued, used, and revised to prescribed processes, specified requirements, or established designs.  Records should be maintained and provisions provided for retention, protection, preservation, traceability, accountability, and retrievability.

Work processes. Work should be performed to technical standards and administrative controls.  Work shall be performed under controlled conditions using approved instructions, procedures, or other appropriate means.

Design. The design process should use sound engineering/scientific principles and appropriate standards.  Design work, including changes, shall be incorporated into applicable requirements and design bases.

Procurement. The procurement of items or services must meet established requirements and be performed as specified.  Prospective suppliers shall be evaluated and selected on the basis of specific criteria.

Inspection and testing. Items must be inspected and tested to be deemed acceptable or not acceptable based on established acceptance and performance criteria.

Documented assessment results should be presented to the organization that was assessed and provided to the appropriate levels of management for review.  Strengths and weaknesses affecting the process should be identified so that management can take meaningful action.

Management should evaluate the assessment results to identify improvement actions and determine whether similar problems may exist elsewhere in the organization.  Lessons learned from assessment results should be communicated to other organizations with similar activities or concerns.

Management should track improvement actions until a resolution has been implemented and verified as completed.

Reference: 10 CFR 830.120, Quality Assurance

Describe the role of electrical systems personnel in the contractor performance evaluation process.

The role of electrical systems personnel in the contractor performance evaluation process varies from site to site.  The local qualifying official will evaluate the completion of this competency.

Participate in the evaluation of a contractor’s performance.

Conduct an interview as part of an evaluation of an occurrence.

Develop an assessment report.

Participate in formal meetings between Department management and senior contractor management to discuss the results of electrical systems assessments.

Competencies h-k are performance-based.  The qualifying official will evaluate the completion of these competencies.

## Electrical systems personnel shall demonstrate the ability to communicate (both oral and written) when working or interacting with the contractor, stakeholders, and other internal and external organizations.

- Identify the various internal and external groups with whom electrical systems personnel must interface in the performance of their duties.

- Apply written communication skills in the development of

assessment reports

technical reports

technical papers

- Apply effective and appropriate communications skills when interfacing with the contractor.

These are performance-based competencies.  The qualifying official will evaluate completion of these competencies.

## Become familiar with the ES&H reporting requirements as noted in DOE O 231.1A, Environment, Safety, and Health Reporting.

- Using an occurrence report related to an electrical system or component and using DOE O 231.1A, as a reference, identify the following:

Causes

Corrective actions

Lessons learned

Whether corrective actions have been completed

This is a performance-based competency.  The qualifying official will evaluate the completion of this competency.

State the purpose of the Order

To ensure timely collection, reporting, analysis, and dissemination of information on environment, safety, and health issues as required by law or regulations or as needed to ensure that DOE/NNSA are kept fully informed on a timely basis about events that could adversely affect the health and safety of the public or the workers, the environment, the intended purpose of DOE facilities, or the credibility of the Department.

Reference: DOE O 231.1A

Define the following terms:

Event

Condition

Facility

Notification report

Occurrence report

Reportable occurrence

### Event

An event is something significant and real-time that happens (e.g., pipe break, valve failure, loss of power, environmental spill, earthquake, tornado, and flood).

### Condition

A condition is any as-found state, whether or not resulting from an event, that may have adverse safety, health, quality assurance, operational, or environmental implications.  A condition is usually programmatic in nature; for example, errors in analysis or calculation; anomalies associated with design or performance; or items indicating a weakness in the management process.

### Facility

Facility refers to any equipment, structure, system, process, or activity that fulfills a specific purpose.  Examples include accelerators, storage areas, fusion research devices, nuclear reactors, production or processing plants, coal conversion plants, magnetohydrodynamic experiments, windmills, radioactive waste disposal systems and burial grounds, environmental restoration activities, testing laboratories, research laboratories, transportation activities, and accommodations for analytical examinations of irradiated and un-irradiated components.

### Notification Report

A notification report is the initial documented report, to the Department, of an event or condition that meets the reporting criteria defined in the manual.

### Occurrence Report

An occurrence report is a documented evaluation of an event or condition that is prepared in sufficient detail to enable the reader to assess its significance, consequences, or implications and to evaluate the actions being proposed or employed to correct the condition or to avoid recurrence.

### Reportable Occurrence

A reportable occurrence is an occurrence to be reported in accordance with the criteria defined in the manual.

Reference: DOE M 231.1-2, Occurrence Reporting and Processing of Operations Information, August 2003

Discuss the Department’s policy regarding the reporting of occurrences as outlined in the Order.

It is DOE policy to ensure that the Office of the Secretary and both DOE and DOE contractor line management are kept fully informed on a timely basis of events that could adversely affect national security or the safeguards and security interests of DOE, the health and safety of the public or the workers, the environment, the intended purpose of DOE facilities, or the credibility of the Department.  The following objectives are established in support of this policy:

To establish and maintain a system for reporting operations information related to DOE-owned or -operated facilities, and for processing that information to identify the root causes of occurrences and provide for appropriate corrective action.

To perform the following tasks

timely identification, categorization, notification, and reporting to DOE management of reportable occurrences at DOE-owned or -operated facilities;

review of reportable occurrences to assess the significance, root causes, generic implications, and the need for corrective actions;

timely evaluation and implementation of appropriate corrective actions;

dissemination of occurrence reports to DOE operations and facilities to prevent similar occurrences;

maintenance of a central DOE system for reporting, processing, and retrieving unclassified occurrence reports.

Reference: DOE M 231.1-2, Occurrence Reporting and Processing of Operations Information, August 2003

State the different categories of reportable occurrences and discuss each.

### Operational Emergencies

Occurrences in this category are the most serious occurrences and require an increased alert status for onsite personnel and, in specified cases, for offsite authorities.

### Significance Category 1

Occurrences in this category are those that are not operational emergencies and that have a significant impact on safe facility operations, worker or public safety and health, regulatory compliance, or public/business interests.

### Significance Category R

Occurrences in this category are those identified as recurring, as determined from the periodic performance analysis of occurrences across a site.

### Significance Category 2

Occurrences in this category are those that are not operational emergencies and that have a moderate impact on safe facility operations, worker or public safety and health, regulatory compliance, or public/business interests.

### Significance Category 3

Occurrences in this category are those that are not operational emergencies and that have a minor impact on safe facility operations, worker or public safety and health, regulatory compliance, or public/business interests.

### Significance Category 4

Occurrences in this category are those that are not operational emergencies and that have some impact on safe facility operations, worker or public safety and health, or public/business interests.

Reference: DOE M 231.1-2, Occurrence Reporting and Processing of Operations Information, August 2003

Review a sample of Occurrence Reports and Operating Experience Weekly reports for issues on electrical safety and discuss the lessons learned.

This is a performance-based competency.  The qualifying official will evaluate the completion of this competency.

## Electrical systems personnel shall demonstrate a working-level knowledge of problem analysis principles and the ability to apply techniques necessary to identify problems, determine potential causes of problems, and identify corrective action(s).

- Describe and explain the application of problem analysis techniques, including the following:

Root cause analysis

Causal factor analysis

Change analysis

Barrier analysis

Management oversight risk tree (MORT) analysis

### Root Cause Analysis

Root cause analysis is a term used to denote a class of problem solving methods aimed at identifying the root causes of problems or events.  The practice of root cause analysis is predicated on the belief that problems are best solved by attempting to correct or eliminate root causes.  Any root cause analysis method may be used that includes the following steps:

1.	Identify the problem

2.	Determine the significance of the problem

3.	Identify the causes (conditions or actions) immediately preceding and surrounding the problem

4.	Identify the reasons why the causes in the preceding step existed, working back to the root cause (the fundamental reason which, if corrected, will prevent recurrence of these and similar occurrences throughout the facility).

### Causal Factor Analysis

Events and Causal Factor Analysis identifies the time sequence of a series of tasks and/or actions and the surrounding conditions leading to an occurrence.  The results are displayed in an Events and Causal Factor chart that gives a picture of the relationships of the events and causal factors.

### Change Analysis

Change Analysis is used when the problem is obscure.  It is a systematic process that is generally used for a single occurrence and focuses on elements that have changed.

### Barrier Analysis

Barrier analysis is a systematic process that can be used to identify physical, administrative, and procedural barriers or controls that should have prevented the occurrence.

### MORT

This chart is a checklist of what happened (less than-adequate specific barriers and controls) and why it happened (less-than-adequate management).  To perform the MORT analysis:

1.	Identify the problem associated with the occurrence and list it as the top event.

2.	Identify the elements on the "what" side of the tree that describe what happened in the occurrence (what barrier or control problems existed).

3.	For each barrier or control problem, identify the management elements on the "why" side of the tree that permitted the barrier control problem.

4.	Describe each of the identified inadequate elements (problems) and summarize your findings.

Reference: DOE-NE-STD-1004-92, Root Cause Analysis Guidance Document, February 1992

Describe and explain the application of the following root cause analysis processes in the performance of occurrence investigations:

Event and causal factors charting

Root cause coding

Recommendation generation

### Events and Causal Factors Charting

Events and causal factor analysis is used for multi-faceted problems or long, complex causal factor chains.  The resulting chart is a cause and effects diagram that describes the time sequence of a series of tasks and/or actions and the surrounding conditions leading to an event.  The event line is a time sequence of actions or happenings while the conditions are anything that shapes the outcome and ranges from physical conditions (such as an open valve or noise) to attitude or safety culture.  The events and conditions as given on the chart describe a causal factor chain.  The direct, root, and contributing cause relationships in the causal factor chain are shown in figure 3.

Figure 8 -Causal factor relationships

Reference: DOE-NE-STD-1004-92, Root Cause Analysis Guidance Document, February 1992

### Root Cause Coding

All causes must be identified as required in DOE M 231.1-2, Occurrence Reporting and Processing of Operations Information, section 11, Occurrence Reporting Model, and included in the occurrence report.  The cause codes to be used for reporting are provided in the causal analysis tree, which is also in section 11 of DOE M 231.1-2.  Guidance on selecting the appropriate cause code is provided in DOE G 231.1-2, Occurrence Reporting Causal Analysis Guide.  The cause description field should include a brief discussion to clearly link the event to the cause code(s).

For those occurrences that require a formal root cause analysis, any of the site approved root cause analysis methodologies are permitted.  The methodology used must be included in the cause description field of the occurrence report.

Reference: DOE M 231.1-2, Occurrence Reporting and Processing of Operations Information, 2003

### Recommendation Generation

Following identification of the root causes for a particular causal factor, achievable recommendations for preventing its recurrence are then generated.  The root cause analyst is often not responsible for the implementation of recommendations generated by the analysis.  However, if the recommendations are not implemented, the effort expended in performing the analysis is wasted.  In addition, the events that triggered the analysis should be expected to recur.  Organizations need to ensure that recommendations are tracked to completion.

Reference: Rooney, James and Vanden Heuvel, Lee N., “Root Cause Analysis for Beginners,” Quality Progress, July 2004, http://www.asq.org/pub/qualityprogress/past/0704/qp0704rooney.pdf

Using event and/or occurrence data, apply problem analysis techniques and identify the problems and how they could have been avoided.

Participate in at least one contractor or Department problem analysis and critique the results.

Using data, interpret two fault tree analyses.

Competencies c-e are performance-based.  The qualifying official will evaluate the completion of these competencies.

III. SAFETY & HEALTH RELATED TO ELECTRICAL SYSTEMS and COMPONENTS

(Applies to only candidates who are assigned oversight to electrical operations, construction, and/or maintenance activities.  Each competency statement is a MPA, provided that they are applicable to the candidate’s assigned electrical duties.)

## Obtain a clear understanding how electrical hazards are addressed via the Integrated Safety Management System process.  Emphasis placed on knowing all applicable site contractor(s) job planning (job hazard analysis, identification and integration of hazard controls within work package), and application of -hazard controls, during the work control process.

This is a site-specific competency.  The local qualifying official will evaluate the completion of this competency.

## Obtain a working-level knowledge of Electrical Safety-Related Work Practices (NFPA 70E, Article 110) to include the following:

Multiemployer relationships

Electrical training and qualification programs

Electrical safety program elements

The National Fire Protection Association (NFPA) published the seventh edition of the 70E Standard for Electrical Safety Requirements for Employee Workplaces in February of 2004.  This edition contains an introduction, 4 chapters, 13 annexes, and has many significant changes from the sixth edition:

Total reorganization into the National Electrical Code (NEC) format

Chapter 2 was moved to become chapter 1

Chapter 3 became chapter 2

Chapter 4 became chapter 3

Chapter 1 became chapter 4.

The issue of multi-employer relationships (110.4) is addressed

The addition of multi-employer relationships now makes the employer liable whenever outside contractors are engaged in activities covered by the scope and application of this standard.  The employer and contractor must inform each other of existing hazards, personal protective equipment/clothing requirements, safe work practices, and emergency evacuation procedures applicable to the work to be performed.  This coordination shall include a meeting and documentation.

NFPA 70E covers the full range of electrical safety issues, including safety related work practices, maintenance, special equipment requirements, and installation.  It focuses on protecting people and identifies requirements that are considered necessary to provide a workplace that is free of electrical hazards.  OSHA bases its electrical safety mandates, found in Subpart S part 1910 and Subpart K part 1926, on the comprehensive information found in NFPA 70E. NFPA 70E is recognized as the tool that illustrates how an employer might comply with these OSHA standards.  The relationship between the OSHA regulations and NFPA 70E can be described as OSHA is the “shall” and NFPA 70E the “how.”

OSHA mandates that all services to electrical equipment be done in a de-energized state. Working live can only be under special circumstances.  If it is necessary to work live (>50 volts to ground), the regulations outlined in NFPA 70E, Article 130 should be used as a tool to comply with OSHA mandates Subpart S part 1910.333(a)(1).  Highlights of this article include:

Shock hazard analysis (paragraph 130.2): Determines the voltage to which personnel will be exposed, boundary requirements, and PPE necessary.  Table 130.2 (C) is used to determine boundary distances.

Flash hazard analysis (paragraph 130.3): Determines the flash protection boundary and PPE needed within that boundary.  The flash protection boundary is determined by methods found in 130.3(A) or Annex D of the standard.  Protective clothing is determined by using tables 130.7(C)(9)(a), 130.7(C)(10), and 130.7(C)(11).  See question and answer number 1 for more details.

Remember, OSHA only allows work on live electrical parts under two special circumstances: (1) when continuity of service is required, and (2) when de-energizing equipment would create additional hazards.  In all other cases, lockout/tagout is the law.

Employers are also responsible for complying with the 2002 NEC 110.16 labeling requirements.  This requires all switchboards, panel boards, industrial control panels, and motor control centers to be field marked.  Any equipment installed after 2002 needs to be labeled.  For equipment installed before 2002, labeling must be applied if ANY modifications or upgrades take place.

Reference: http://www.labsafety.com/refinfo/ezfacts/ezf263.htm

## Observe electrical work performed by each site contractor to learn how work is performed within planned controls.  Obtain a working knowledge of site contractor(s) procedure/work control program, and specific work control requirements for each job observed.  The level of rigor of these jobs should allow the candidate to review the functional areas, requirements, and workscope for compliance with NFPA 70E, to include the following:

- Electrical safety-related work practices and establishment of electrically safe work conditions (NFPA 70E, Article 120).  To include, but not limited to lockout/tagout (LOTO), deenergization requirements, zero-energy checks, and the electrically-safe-work condition verification process.

All activities on or near electrically energized systems having “live” parts shall be conducted in accordance with the limitations and procedures specified in the latest version of NFPA 70E and with the safe work practices and conditions that follow.

Only qualified personnel {as defined in NFPA 70E Article 110.6(D)} as authorized by supervisor can perform such work.

Safe Work Practices:

Know the equipment and potential hazards - Define the scope of work.

Submit the scope of work to your supervisor for approval.

Analyze the hazards – use engineered methods to mitigate hazards.

Establish procedures as necessary.

Use barricades or other means to prevent unqualified persons crossing approach boundaries.

Personnel shall employ insulating barriers to prevent themselves and others from leaning into or falling into live parts and to prevent live parts that might become loose from contacting personnel.

Personnel shall wear safety glasses.

Personnel shall not wear metallic personal items (e.g., jewelry, glasses, watches) while working on or near live parts.

Personnel shall use non-conducting ladders when needed.

Always assume a conductor is energized until proven otherwise.

Personnel shall wear voltage rated gloves when using tools on or near live parts.

Personnel shall use only personal protective equipment that is designed [approved. certified] for the hazard.

Personnel shall use only insulated tools when working on or near live parts.

Personnel shall use only tools and instruments that are designed for the system voltage.

Personnel shall not bypass interlocks or safety devices that protect persons against electrical shock—except when absolutely necessary and then only with written approval from your supervisor

Whenever possible, do not work alone.

Safety Watch is required when deemed so by your supervisor.  This person shall be CPR trained and be familiar with removing all sources of power to the devise being worked upon and have ready access to a phone in order to call 911 in case of emergency.

When operating circuit breakers or fused switches.  ALWAYS stand to the side – NEVER directly in front of the device being operated.

Work Conditions:

Personnel should inspect electrical equipment for defective parts, faulty insulation, improper grounding, loose connections, ground faults, and unguarded live parts and should take appropriate remedial action before working on or near live parts.

Personnel should work only where there is adequate clearance.

Personnel should not work on or near live parts that are in a hazardous location (e.g., in wet or damp areas, where there are corrosive or flammable atmospheres).

Restrict non-participants from the work area.

Reference: National Fire Prevention Association, NFPA 70E Chapter 1

- Electrical hazards/risk identification and classification processes, and the use of severity indices, in the application of electrical events analysis and trends. (NFPA 70E, Article 130)

- Electrical work on or near live parts.  To include, but not limited to energized electrical work permits (elements and exemptions), shock and arc-flash hazard analyses, arc flash calculation methodology, arc flash reduction techniques, approach boundaries, and associated PPE. (NFPA 70E, Article 130, and IEEE 1584)

Article 130 states that electrical conductors shall be deenergized before an employee works on or near them unless the employer can demonstrate that deenergizing introduces additional or increased hazards or is infeasible due to equipment design or operational limitations.  Typical examples include, but are not limited to, interruption of life support equipment, deactivation of emergency alarm systems, and shutdown of hazardous location ventilation equipment.  If work must be performed on energized conductors, a shock hazard analysis and flash hazard analysis must be performed.

Reference: http://www.workplacegroup.net/article-implem-NFPA70E.htm

- Safety-related maintenance requirements: grounding and bonding, safety equipment, clear space requirements; substations, switchgear, panels, motor control centers; premises wiring; controller equipment; fuses and circuit breakers; rotating equipment; hazardous locations; batteries and battery rooms, portable electric tools and equipment; and personal safety and protective equipment. (NFPA 70E, Chapter 2, IEEE Std-450)

Electrical equipment is, in most cases, very reliable.  Sometimes this reliability is taken for granted.  A comprehensive electrical equipment maintenance program improves electrical system reliability and thereby reduces exposure of electrical hazards to workers.

Chapter 2 addresses safety-related maintenance requirements for electrical equipment and installations, or parts of either, for the safety of employees who work on, near, or with such equipment:

Reference: http://www.workplacegroup.net/article-implem-NFPA70E.htm

- Safety requirements for special equipment: Such as Research & Development (R&D) electrical safety requirements; work practices for such R&D equipment (i.e. laser operations and power electronic equipment, etc.). (NFPA 70E, Article 400)

- Installation safety requirements: Power systems protection; flash protection; guarding of live parts; wiring design and protection; wiring methods, components, and equipment; specific purpose equipment and installations (cranes and hoists, elevators, HVAC, X-ray equipment, motor controllers, etc.; hazardous locations), and so on. (NFPA 70; and NFPA 70E, Chapter 4)

Specific purpose equipment and installations.

Cranes and hoists. This paragraph applies to the installation of electric equipment and wiring used in connection with cranes, monorail hoists, hoists, and all runways.

Disconnecting means--Runway conductor disconnecting means.  A readily accessible disconnecting means shall be provided between the runway contact conductors and the power supply.

Disconnecting means for cranes and monorail hoists.  A disconnecting means, capable of being locked in the open position, shall be provided in the leads from the runway contact conductors or other power supply on any crane or monorail hoist.

If this additional disconnecting means is not readily accessible from the crane or monorail hoist operating station, means shall be provided at the operating station to open the power circuit to all motors of the crane or monorail hoist.  The additional disconnect may be omitted if a monorail hoist or hand-propelled crane bridge installation meets all of the following:

The unit is floor controlled;

The unit is within view of the power supply disconnecting means; and

No fixed work platform has been provided for servicing the unit.

A limit switch or other device shall be provided to prevent the load block from passing the safe upper limit of travel of any hoisting mechanism.

The dimension of the working space in the direction of access to live parts which may require examination, adjustment, servicing, or maintenance while alive shall be a minimum of 2 feet 6 inches (762 mm).  Where controls are enclosed in cabinets, the door(s) shall open at least 90 degrees or be removable, or the installation shall provide equivalent access.

All exposed metal parts of cranes, monorail hoists, hoists and accessories including pendant controls shall be metallically joined together into a continuous electrical conductor so that the  entire crane or hoist will be grounded in accordance with 29 CFR 1926.404(f).  Moving parts, other than removable accessories or attachments, having metal-to-metal bearing surfaces shall be considered to be electrically connected to each other through the bearing surfaces for grounding purposes.  The trolley frame and bridge frame shall be considered as electrically grounded through the bridge and trolley wheels and its respective tracks unless conditions such as paint or other insulating materials prevent reliable metal-to-metal contact. In this case a separate bonding conductor shall be provided.

Elevators, escalators, and moving walks

Elevators, escalators, and moving walks shall have a single means for disconnecting all ungrounded main power supply conductors for each unit.

If control panels are not located in the same space as the drive machine, they shall be located in cabinets with doors or panels capable of being locked closed.

Electric welders--disconnecting means--Motor-generator, AC transformer, and DC rectifier arc welders.  A disconnecting means shall be provided in the supply circuit for each motor-generator arc welder, and for each AC transformer and DC rectifier arc welder which is not equipped with a disconnect mounted as an integral part of the welder.

Resistance welders.  A switch or circuit breaker shall be provided by which each resistance welder and its control equipment can be isolated from the supply circuit.  The ampere rating of this disconnecting means shall not be less than the supply conductor ampacity.

X-Ray equipment--Disconnecting means--General. A disconnecting means shall be provided in the supply circuit.  The disconnecting means shall be operable from a location readily accessible from the X-ray control.  For equipment connected to a 120-volt branch circuit of 30 amperes or less, a grounding-type attachment plug cap and receptacle of proper rating may serve as a disconnecting means.

More than one piece of equipment.  If more than one piece of equipment is operated from the same high-voltage circuit, each piece or each group of equipment as a unit shall be provided with a high-voltage switch or equivalent disconnecting means.  This disconnecting means shall be constructed, enclosed, or located so as to avoid contact by employees with its live parts.

Control--Radiographic and fluoroscopic types. Radiographic and fluoroscopic-type equipment shall be effectively enclosed or shall have interlocks that deenergize the equipment automatically to prevent ready access to live current-carrying parts.

- Be aware that 29 CFR 1910 and 29 CFR 1926 (OSHA requirements documents) has many, but not all of the electrical safety requirements as NFPA 70E.  For example, NFPA 70E outlines requirement for arc-flash hazard controls, however the mentioned CFR’s do not.

To safely observe electrical work on or near energized electrical conductors, the candidate must be previously trained to the mentioned requirements.  Candidates are not to cross any shock or arc flash boundary.

Reference: 29 CFR 1926.406, Specific Purpose Equipment and Installations.

## From the jobs observed in Competency 3 above, assess how well contractor management systems (lessons learned and other feedback processes) are integrated with the work planning and ISM process.  Develop a working knowledge of how lessons learned are addressed by each contractor’s Integrated Safety Management System feedback process.  (Reference DOE P 450.4 Safety Management System Policy.)

This is a performance-based competency.  The qualifying official will evaluate the completion of this competency.

## Obtain a working-level knowledge of NFPA 70E, Article 420 requirements, to include:

a. Wiring methods – Bonding of enclosures, temporary wiring, and permitted use of cabletrays;

b. Safety positioning and connection of switches;

c. Switch/panelboard location and access requirements;

d. Enclosures for damp and wet locations;

e. Conductor identification requirements;

f. Permitted and non-permitted use of flexible cords and cables;

g. Portable cables over 600 volts;

h. Motor, transformer, and capacitor general use equipment.

### Bonding of Enclosures

General.  Metal raceways, cable trays, cable armor, cable sheath, enclosures, frames, fittings, and other metal non–current-carrying parts that are to serve as grounding conductors, with or without the use of supplementary equipment grounding conductors, shall be effectively bonded where necessary to ensure electrical continuity and the capacity to conduct safely any fault current likely to be imposed on them.  Any nonconductive paint, enamel, or similar coating shall be removed at threads, contact points, and contact surfaces or be connected by means of fittings designed so as to make such removal unnecessary.

Isolated Grounding Circuits.  Where required for the reduction of electrical noise (electromagnetic interference) of the grounding circuit, an equipment enclosure supplied by a branch circuit shall be permitted to be isolated from a raceway containing circuits that supply only that equipment by one or more listed nonmetallic raceway fittings located at the point of attachment of the raceway to the equipment enclosure.  The metal raceway shall comply with provisions of this standard and shall be supplemented by an internal insulated equipment grounding conductor installed to ground the equipment enclosure.

Use of an isolated equipment grounding conductor does not relieve the requirement for grounding the raceway system.

Ducts for Dust, Loose Stock, or Vapor Removal. No wiring systems of any type shall be installed in ducts used to transport dust, loose stock, or flammable vapors.  No wiring system of any type shall be installed in any duct, or any shaft containing only such ducts, used for vapor removal or for ventilation of commercial-type cooking equipment.

### Temporary Wiring

Temporary electrical power and lighting wiring methods may be of a class less than would be required for a permanent installation.  Except as specifically modified in 420.1(B) (1) (a) through 420.1(B) (1) (d), all other requirements of this standard for permanent wiring shall apply to temporary wiring installations.

Time Constraints.

During the Period of Construction. Temporary electrical power and lighting installations shall be permitted during the period of construction, remodeling, maintenance, repair, or demolition of buildings, structures, equipment, or similar activities.

Temporary electrical power and lighting installations shall be permitted for a period not to exceed 90 days for holiday decorative lighting and similar purposes.  Temporary electrical power and lighting installations shall be permitted during emergencies and for tests, experiments, and developmental work.  Temporary wiring shall be removed immediately upon completion of construction or purpose for which the wiring was installed.

General Requirements for Temporary Wiring.

Feeders shall be protected as provided in 410.9.  They shall originate in an approved distribution center.  Conductors shall be permitted within cable assemblies or within multiconductor cords or cables of a type identified for hard usage or extra-hard usage.  For the purpose of this section, Type NM and Type NMC cables shall be permitted to be used in any dwelling, building, or structure without any height limitation.

Exception: Single insulated conductors shall be permitted where installed for the purpose(s) specified in 420.1(B)(3)(c) where accessible only to qualified persons.

Branch Circuits. All branch circuits shall originate in an approved power outlet or panelboard.  Conductors shall be permitted within cable assemblies or within multiconductor cord or cable of a type identified for hard usage or extra-hard usage.  All conductors shall be protected as provided in 410.9.  For the purpose of this section, Type NM and NMC cables shall be permitted to be used in any dwelling, building, or structure without any height limitation.

Exception: Branch circuits installed for the purposes specified in 420.1(B)(3)(b) or 420.1(B)(3)(c) shall be permitted to be run as single insulated conductors.  Where the wiring is installed in accordance with 420.1(B)(1)(c), the voltage to ground shall not exceed 150 volts, the wiring shall not be subject to physical damage, and the conductors shall be supported on Demonstrate a working-level knowledge of AC reactive components, including inductive and capacitive reactance and phase relationships in reactive circuits.

### Cable Trays

Cable Trays.

Uses Permitted. Cable tray shall be permitted to be used as a support system for services, feeders, branch circuits, communications circuits, control circuits, and signaling circuits.  Cable tray installations shall not be limited to industrial establishments.  Where exposed to direct rays of the sun, insulated conductors and jacketed cables shall be identified as being sunlight resistant.  Cable trays and their associated fittings shall be identified for the intended use.

Wiring Methods. The following wiring methods shall be permitted to be installed in cable tray systems: armored cable; communication raceways; electrical metallic tubing; electrical nonmetallic tubing; fire alarm cables; flexible metal conduit; flexible metallic tubing; instrumentation tray cable; intermediate metal conduit; liquid tight flexible metal conduit and liquid tight flexible nonmetallic conduit; metal-clad cable; mineral-insulated, metal-sheathed cable; multi-conductor service-entrance cable; multi-conductor underground feeder and branch circuit cable; multipurpose and communications cables; nonmetallic-sheathed cable; power and control tray cable; power-limited tray cable; optical fiber cables; optical fiber raceways; other factory-assembled, multi-conductor control, signal, or power cables that are specifically approved for installation in cable trays; rigid metal conduit; and rigid nonmetallic conduit.

Uses Not Permitted. Cable tray systems shall not be used in hoist-ways or where subject to severe physical damage.  Cable tray systems shall not be used in environmental airspaces, except as permitted in 420.1(A)(2) to support wiring methods recognized for use in such spaces.

### Safety Positioning and Connection of Switches

Single-Throw Knife Switches. Single-throw knife switches shall be placed so that gravity will not tend to close them.  Single-throw knife switches approved for use in the inverted position shall be provided with a locking device that ensures that the blades remain in the open position when so set.

Double-Throw Knife Switches. Double-throw knife switches shall be permitted to be mounted so that the throw is either vertical or horizontal.  Where the throw is vertical, a locking device shall be provided to hold the blades in the open position when so set.

Connection of Switches. Single-throw knife switches and switches with butt contacts shall be connected so that their blades are de-energized when the switch is in the open position.  Bolted pressure contact switches shall have barriers that prevent inadvertent contact with energized blades.  Single-throw knife switches, bolted pressure contact switches, molded-case switches, switches with butt contacts, and circuit breakers used as switches shall be connected so that the terminals supplying the load are de-energized when the switch is in the open position.

### Switch/Panelboard Location and Access Requirements

Switchboards that have any exposed live parts operating at 50 volts or more shall be located in permanently dry locations and then only where under competent supervision and accessible only to qualified persons.  Switchboards shall be located so that the probability of damage from equipment or processes is reduced to a minimum.  Panelboards shall be mounted in cabinets, cutout boxes, or enclosures designed for the purpose and shall be dead front.

Exception: Panelboards other than of the dead-front, externally operable type shall be permitted where accessible only to qualified persons.

### Enclosures for Damp or Wet Locations.

Damp or Wet Locations. In damp or wet locations, surface-type enclosures within the scope of NFPA 70E shall be placed or equipped so as to prevent moisture or water from entering and accumulating within the cabinet or cutout box, and shall be mounted so there is at least a 6-mm (¼-in.) airspace between the enclosure and the wall or other supporting surface.  Enclosures installed in wet locations shall be weatherproof.

Exception: Nonmetallic enclosures shall be permitted to be installed without the airspace on a concrete, masonry, tile, or similar surface.

Switchboards and Panelboards in Damp or Wet Locations. Switchboards or panelboards in a wet location or outside of a building shall be enclosed in a weatherproof enclosure or cabinet that shall comply with 420.5(A).

### Conductor Identification Requirements

Grounded Conductors. Insulated or covered grounded conductors shall be identified in accordance with NFPA 70E.

Equipment Grounding Conductors. Equipment grounding conductors shall be identified in accordance with NFPA 70E.

Ungrounded Conductors. Conductors that are intended for use as ungrounded conductors, whether used as a single conductor or in multi-conductor cables, shall be finished to be clearly distinguishable from grounded and grounding conductors.  Distinguishing markings shall not conflict in any manner with the surface markings.

### Flexible Cords and Cables.

Suitability. Flexible cords and cables and their associated fittings shall be suitable for the conditions of use and location.

Uses Permitted. Flexible cords and cables shall be used only for the following:

Pendants

Wiring on luminaires (fixtures)

Connection of portable lamps, portable and mobile signs, or appliances

Elevator cables

Wiring on cranes and hoists

Connection of utilization equipment to facilitate frequent interchange

Prevention of the transmission of noise or vibration

Appliances where the fastening means and mechanical connections are specifically designed to permit ready removal for maintenance and repair, and the appliance is intended or identified for flexible cord connection

Data processing cables

Connection of moving parts

Temporary wiring

Attachment Plugs. Where used as permitted in 420.7(B)(1)(3), (9), and (11), each flexible cord shall be equipped with an attachment plug and shall be energized from a receptacle outlet.

Uses Not Permitted. Unless specifically permitted in 420.7(B), flexible cords and cables shall not be used for the following:

As a substitute for the fixed wiring of a structure

Where run through holes in walls, structural ceilings, suspended ceilings, dropped ceilings, or floors

Where run through doorways, windows, or similar openings

Where attached to building surfaces

### Portable Cables Over 600 Volts

#### Construction

Conductors. The conductors shall be 8 American Wire Gauge (AWG) copper or larger and shall employ flexible stranding.

Exception: The size of the insulated ground-check conductor of Type G-GC cables shall be not smaller than 10 AWG.

Shields. Cables operated at over 2000 volts shall be shielded.  Shielding shall be for the purpose of confining the voltage stresses to the insulation.

Equipment Grounding Conductor(s). An equipment grounding conductor(s) shall be provided.  The total area shall not be less than that of the size of the equipment grounding conductor required in NFPA 70E.

Shielding. All shields shall be grounded.

Grounding. Grounding conductors shall be connected in accordance with NFPA 70E.

Minimum Bending Radii. The minimum bending radii for portable cables during installation and handling in service shall be adequate to prevent damage to the cable.

Fittings. Connectors used to connect lengths of cable in a run shall be of a type that lock firmly together.  Provisions shall be made to prevent opening or closing these connectors while energized.  Suitable means shall be used to eliminate tension at connectors and terminations.

Splices and Terminations. Portable cables shall not contain splices unless the splices are of the permanent molded, vulcanized types in accordance with this standard.  Terminations on portable cables rated over 600 volts, nominal, shall be accessible only to authorized and qualified personnel.

### Motor, Transformer, and Capacitor General Use Equipment

#### Motors

In Sight From (Within Sight From, Within Sight). Where one piece of equipment shall be “in sight from,” “within sight from,” or “within sight,” and so forth, of another equipment, the specified equipment is to be visible and not more than 15 m (50 ft) distant from the other.

Disconnecting Means Location

Controller. An individual disconnecting means shall be provided for each controller and shall disconnect the controller.  The disconnecting means shall be located in sight from the controller location.

Exception No. 1: For motor circuits over 600 volts, nominal, a controller disconnecting means capable of being locked in the open position shall be permitted to be out of sight of the controller, provided the controller is marked with a warning label giving the location of the disconnecting means.

Exception No. 2: A single disconnecting means shall be permitted for a group of coordinated controllers that drive several parts of a single machine or piece of apparatus.  The disconnecting means shall be located in sight from the controllers, and both the disconnecting means and the controllers shall be located in sight from the machine or apparatus.

Motor. A separate disconnecting means shall be located in sight from the motor location and the driven machinery location.  The disconnecting means required in accordance with 420.10(E)(1) shall be permitted to serve as the disconnecting means for the motor if it is located in sight from the motor location and the driven machinery location.

Exception: The disconnecting means shall not be required to be in sight from the motor and the driven machinery location under either condition (a) or (b), provided the disconnecting means required in accordance with 420.10(E)(2) is individually capable of being locked in the open position.  The provision for locking or adding a lock to the disconnecting means shall be permanently installed on or at the switch or circuit breaker used as the disconnecting means.

Where such a location of the disconnecting means is impracticable or introduces additional or increased hazard to persons or property

In industrial installations, with written safety procedures, where conditions of maintenance and supervision ensure that only qualified persons service the equipment:  Some examples of increased or additional hazards include, but are not limited to, motors rated in excess of 100 hp, multi-motor equipment, submersible motors, motors associated with variable frequency drives, and motors located in hazardous (classified) locations.

To Be Indicating. The disconnecting means shall plainly indicate whether it is in the open (off) or closed (on) position.

Readily Accessible. At least one of the disconnecting means shall be readily accessible.

Motors Served by Single Disconnecting Means. Each motor shall be provided with an individual disconnecting means.

Exception: A single disconnecting means shall be permitted to serve a group of motors under any one of the following conditions:

Where a number of motors drive several parts of a single machine or piece of apparatus, such as metal and woodworking machines, cranes, and hoists

Where a group of motors is under the protection of one set of branch-circuit protective devices

Where a group of motors is in a single room within sight from the location of the disconnecting means

Motor and Branch-Circuit Overload Protection. Overload devices are intended to protect motors, motor-control apparatus, and motor branch-circuit conductors against excessive heating due to motor overloads and failure to start.  Overload in electrical apparatus is an operating overcurrent that, when it persists for a sufficient length of time, would cause damage or dangerous overheating of the apparatus.  It does include short circuits or ground faults.  These provisions shall not be interpreted as requiring overload protection where it might introduce additional or increased hazards, as in the case of fire pumps.

Protection of Live Parts — All Voltages. Exposed live parts of motors and controllers operating at 50 volts or more shall be guarded against accidental contact by enclosures or by location as follows:

By installation in a room or enclosure that is accessible only to qualified persons

By installation on a suitable balcony, gallery, or platform elevated and arranged so as to exclude unqualified persons

By elevation 2.5 m (8 ft) or more above the floor

Exception to (g): Live parts of motors operating at more than 50 volts between terminals shall not require additional guarding for stationary motors that have commutators, collectors, and brush rigging located inside of motor-end brackets and not conductively connected to supply circuits operating at more than 150 volts to ground.

Guards for Attendants. Where live parts of motors or controllers operating at over 150 volts to ground are guarded against accidental contact only by location, and where adjustment or other attendance might be necessary during the operation of the apparatus, suitable insulating mats or platforms shall be provided so that the attendant cannot readily touch live parts unless standing on the mats or platforms.

#### Transformers.

General. Sections 420.10(F)(2) through 420.10(F)(8) cover the installation of all transformers.  The following transformers are not covered by 420.10(F):

Current transformers

Dry-type transformers that constitute a component part of other apparatus and comply with requirements for such apparatus

Transformers that are an integral part of an X-ray, high-frequency, or electrostatic coating apparatus

Transformers used with Class 2 and Class 3 circuits

Transformers for sign and outline lighting

Transformers for electric-discharge lighting

Transformers used for power-limited fire alarm circuits

Transformers used for research, development, or testing, where effective arrangements are provided to safeguard persons from contacting energized parts

Voltage Warning. The operating voltage of exposed live parts operating at 50 volts or more of transformer installations shall be indicated by signs or visible markings on the equipment or structures.

Dry-Type Transformers Installed Indoors. Dry-type transformers installed indoors and rated over 35 kV shall be installed in a vault.

Oil-Insulated Transformers Installed Indoors. Oil-insulated transformers installed indoors shall be installed in a vault.

Oil-Insulated Transformers Installed Outdoors. Combustible material, combustible buildings, and parts of buildings, fire escapes, and door and window openings shall be safeguarded from fires originating in oil-insulated transformers installed on roofs, attached to or adjacent to a building or combustible material.

#### Capacitors.

Switching: Load Current. Group-operated switches shall be used for capacitor switching and shall be capable of the following:

Carrying continuously not less than 135 percent of the rated current of the capacitor installation

Interrupting the maximum continuous load current of each capacitor, capacitor bank, or capacitor installation that will be switched as a unit

Withstanding the maximum inrush current, including contributions from adjacent capacitor installations

Carrying currents due to faults on capacitor side of switch

Isolation

General. A means shall be installed to isolate from all sources of voltage each capacitor, capacitor bank, or capacitor installation that will be removed from service as a unit.  The isolating means shall provide a visible gap in the electrical circuit adequate for the operating voltage.

Isolating or Disconnecting Switches with No Interrupting Rating. Isolating or disconnecting switches (with no interrupting rating) shall be interlocked with the load-interrupting device or shall be provided with prominently displayed caution signs to prevent switching load current.

Additional Requirements for Series Capacitors. The proper switching sequence shall be ensured by use of one of the following:

Mechanically sequenced isolating and bypass switches

Interlocks

Switching procedure prominently displayed at the switching location

Storage Batteries. Provisions shall be made for sufficient diffusion and ventilation of the gases from the battery to prevent the accumulation of an explosive mixture.

Reference: http://www.agsrhichome.bnl.gov/AGS/Accel/SND/Electrical%20Safety/NFPA%2070E%202004.pdf

## Obtain a working-level knowledge of the DOE Electrical Safety Handbook for safety requirements associated with site R&D operations involving large capacity stored energy, inductor, capacitor and pulsed energy systems to include requirements relating to:

Hazards identification, classification, PPE, and associated work practices;

Equipment configuration, and operational practices;

R&D training and qualifications requirements.

### Hazards Identification

There are many possible types of electrical AC and DC power source hazards in complex R&D systems and the various design philosophies preclude establishing hazard classifications based on voltage alone.  Some of the hazards of working in complex R&D systems are:

Internal component failure can cause excessive voltages.  Internal component open-circuit failure in capacitor banks and Marx generators can result in full voltages across components that may not be appropriately discharged in the usual manner.

Internal component shorts in capacitor banks and Marx generators can result in excessive fault current, causing extreme heat, over-pressurization of capacitor enclosures, and rupture.

Overloading or improper cooling of power supplies can cause excessive temperature rise.

Output circuits and components can remain energized after input power is interrupted.

Auxiliary and control power circuits can remain energized after the main power circuit is interrupted.

When power supplies serve more than one experiment, errors made when switching between experiments may create hazards to personnel.

R&D electrical apparatus may contain large amounts of stored energy, requiring fault analysis.

Liquid coolant leaking from R&D electrical equipment may pose an electrical hazard to personnel.

It is usual for R&D facilities to have equipment that operates at less than 50 V.  Although this equipment is generally regarded as nonhazardous, it is considered hazardous when high currents are involved.  Examples of such equipment are a power supply rated 3 kA at 25 V, a magnet power supply with rated output of 200 A at 40 V, and a bus bar carrying 1 kA at 5 V.

Though there is a low probability of electric shock at voltages less than 50 V, there is a hazard due to arcing and heating in case of an accidental fault.  For example, a tool could drop onto the terminals and initiate an arc, causing severe burns.

### Personnel Protective Equipment

Provide personal protective equipment for electrical work.  Establish documented procedures for its use, care, maintenance, and testing.  [Guidance for these procedures can be found in 29 CFR 1910.137 and 29 CFR 1910.268(f).]

Managers shall ensure that adequate resources are available to provide personal protective equipment in compliance with applicable codes and standards.  In addition, they shall ensure that:

personnel are trained in its use in accordance with documented procedures;

procedures are established and implemented for documented controls of protective equipment such as inventory, storage, maintenance, and testing;

protective equipment requirements and usages are specified in the safe operating procedures;

protective equipment is inspected prior to each use;

high-voltage equipment is inspected prior to each use according to appropriate recognized standards and

grounding equipment, cables, clusters, and sticks, are inspected annually and prior to each use.

### Safe Work Practices

An analysis of high-voltage circuits should be performed by a qualified person before work begins unless all exposed energized parts are guarded as required for high-voltage work.  The analysis must include fault conditions where circuit current could rise above the nominal rated value.  Depending on the results of the analysis, any of the following may apply:

If the analysis concludes that the current is above 5 mA or energy is above 10 joules, then the work is considered to be energized work and should be performed in accordance with DOE-HDBK-1092-2004, section 2, General Requirements and/or section 7, Work In Excess of 600 Volts.

If the analysis concludes that the current is between 0.5 mA and 5 mA and between 0.25 and 10 joules, then the worker may be exposed to a secondary hazard (e.g., startle reaction) that must be mitigated.

If the analysis concludes that the current is below 0.5 mA and below 0.25 joules, then the worker exposure is minimal and no special precautions are required.

High-voltage supplies that use rated connectors and cables where there are no exposed energized parts are not considered hazards.  Connections shall not be made or broken with the power supply energized unless they are designed and rated for this type of duty (e.g., loadbreak elbows).  Inspect cables and connectors for damage and do not use if they are damaged.  Exposed high-voltage parts must be guarded to avoid accidental contact.

### Equipment Configuration

In design and construction of R&D equipment, it is important to remember the following cautions:

Install only components essential to the power supply within the power-supply enclosure.

Provide appropriate separation between high-voltage components and low-voltage supply and/or control circuits.

Provide to personnel a visible indicator that the power supply is energized.

Minimize the number of control stations and provide an emergency shutdown switch where needed.

Where possible, avoid multiple-input power sources.

Apply a label containing emergency shutdown instructions to equipment that is remotely controlled or unattended while energized.

Personnel in R&D labs may encounter energized parts in a variety of configurations, locations, and under environmental conditions that are not usual for most electrical power personnel.  Sometimes the equipment can be designed to incorporate mitigation of the hazards associated with working on such equipment.  If not, then safe operating procedures must be developed and used.

### R&D Training and Qualification Requirements

The following paragraphs provide guidance for determining the qualification process for persons involved with specialized electrical equipment, configurations, or work tasks associated with experiments.  The guidance provided in this section is in addition to the minimum qualifications described in DOE-HDBK-1092-2004, section 2.8, Training and Qualifications of Qualified Workers.

The hazards associated with R&D equipment are sometimes unique because the equipment itself is unique.  These hazards are sometimes made worse because of an uncommon design or the fact that it may be one of a kind.  Special efforts are necessary to identify all the potential hazards that may be present in a specific unique design.  These hazards should be identified and a plan developed to mitigate the associated risk.  Personnel working on R&D equipment shall be qualified to work on this equipment, depending on its unique safety problems.

Personnel assigned to tasks involving R&D equipment shall be apprised of the hazards identified in section 10.7.1 of DOE0HDBK-1092-2004.  It is suggested that they participate in developing mitigation plans to reduce the risks associated with the hazards.

A list of additional experience qualifications should be developed by the appropriate personnel including the workers.  This list should identify specific training requirements necessary for unusual equipment or tasks.

Reference: DOE-HDBK-1092-2004, Electrical Safety, December 2004

## Obtain a working-level knowledge of requirements related to safe work practices for laser operations (NFPA 70E, Chapter 3) to include:

Fail-safe interlocks;

Controlled areas;

Laser characteristics;

Safety training and qualifications;

Safeguarding of personnel.

### Fail-Safe Interlocks

Protective housing which encloses the laser shall be provided with an interlock system which is activated when the protective housing is opened or removed during operation and maintenance.  Fail-safe interlocks shall be provided for any portion of the protective housing which, by design, can be removed or displaced during operation and maintenance.

Portions of the protective housing that are only intended to be removed from any laser or laser system by the service personnel, which then permits direct access to laser radiation shall either:

be interlocked (fail-safe interlock not required) or

require a tool for removal and shall have an appropriate warning label on the panel

If the interlock can be bypassed or defeated, a warning label with the appropriate indications shall be located on the protective housing near the interlock.

A Class 3b laser or laser system should be provided with a master switch.  A Class 4 laser or laser system shall be provided with a master switch.  This master switch shall effect beam termination and/or system shutoff and shall be operated by a key, or by a coded access.

### Controlled Areas

Class 3b lasers shall be operated in a controlled area, unless the beam path is completely enclosed.  Class 4 lasers shall be operated in a controlled area, where all entryway safety controls shall be designed to allow both rapid egress by laser personal at all times and admittance to the laser controlled area under emergency conditions.  If the laser is not fully enclosed, laser operation shall be in a light-tight room with interlocked entrances to assure that the laser will shut off when the door is opened.

Whenever appropriate and possible, Class 4 lasers or laser systems should be controlled and monitored at a position as distant as possible from the emission portal of the laser or laser system.

### Laser Characteristics

Lasers are classified in terms of their potential to cause biological damage.  The pertinent parameters are laser output energy or power, radiation wavelength, exposure duration, and cross sectional area of the laser beam at the point of interest.  Most commercial lasers have an attached label specifying the classification of that laser.  The hazard classification of a laser can be determined using ANSI Z136.1-2000 Section 3 and Appendix A.  (The department of Environmental Health and Safety keeps a copy of this standard for reference)

#### Class 1

A Class 1 laser is considered to be incapable of producing damaging radiation levels, and is, therefore, exempt from most forms of surveillance.  Example: laser printers

#### Class 2

Class 2 lasers and laser systems are visible (0.4 to 0.7 um) continuous wave (CW) and repetitive-pulse lasers and laser systems which can emit accessible radiant energy exceeding the appropriate Class 1 accessible emission limit (AEL) for the maximum duration inherent in the design or intended use of the laser or laser system, but not exceeding the Class 1 AEL for any applicable pulse (emission) duration < 0.25 seconds and not exceeding an average radiant power of 1mW.

A Class 2 laser is a low-powered laser in the visible range that may be viewed directly under carefully controlled exposure conditions.  These lasers are considered safe because the natural reflex of the eye will prevent average exposure from causing damage.  Example: laser pointers

#### Class 3a

Class 3a lasers and laser systems include lasers and laser systems which have an accessible output between 1 and 5 times the Class 1 AEL for wavelengths shorter than 0.4 um or longer than 0.7 um, or less than 5 times the Class 2 AEL for wavelengths between 0.4 and 0.7 um.

Class 3a lasers will normally not produce injury if viewed only momentarily by the unaided eye.  The Class 3a lasers may be a hazard if viewed using optics, e.g., telescopes, microscopes, or binoculars. Example: HeNe lasers above 1 milliwatt, but not exceeding 5 milliwatts; some laser pointers

#### Class 3b

Class 3b lasers and laser systems include:

Ultraviolet (0.18 to 0.4 um) and infrared (1.4 um to 1 mm) lasers and laser systems which can emit during any emission duration within the maximum duration inherent in the design of the laser or laser system, but which (a) cannot emit an average radiant power in excess of 0.5 W for = 0.25 seconds or (b) cannot produce a radiant energy greater than 0.125 Joules within an exposure time < 0.25 seconds.

Visible (0.4 to 0.7 um) or near-infrared (0.7 to 1.4 um) lasers or laser systems which emit in excess of the AEL of Class 3a but which (a) cannot emit an average radiant power in excess of 0.5 W for = 0.25 seconds and (b) cannot produce a radiant energy greater than 0.03 Joules per pulse.

Class 3b lasers may cause severe eye injuries through direct or specular exposure.  Examples: continuous lasers not exceeding 0.5 watts for any period greater than 0.25 seconds, pulsed visible lasers not emitting more than 0.03 joules per pulse, pulsed infrared or ultraviolet lasers not emitting more than 0.125 joules during any period less than 0.25 seconds.

#### Class 4

Class 4 lasers and laser systems are those that emit radiation that exceeds the Class 3b AEL.

Class 4 lasers are a hazard to the eye from the direct beam, specular reflections, and sometimes even from diffuse reflections.  Class 4 lasers can also start fires and can damage skin.  Example: lasers operating at power levels greater than 500 milliwatts for continuous wave lasers or greater than 0.03 Joules for a pulsed system.

### Safety Training

Laser safety training program shall be required for Class 3b and 4 lasers and laser systems.  Laser safety training program should be required for Class 2 and Class 3a lasers and laser systems.  The laser safety training program should include the information in ANSI Z136.1-2000, section 5.

### Safeguarding of Personnel

Eye protection devices which are specifically designed for protection against radiation from Class 3b lasers or laser systems should be administratively required and their use enforced when engineering or other procedural and administrative controls are inadequate to eliminate potential exposure in excess of the applicable maximum permissible exposure (MPE).

Eye protection devices that are specifically designed for protection against radiation from Class 4 lasers or laser systems shall be required and their use enforced when engineering or other procedural and administrative controls are inadequate to eliminate potential exposure in excess of the applicable MPE.

Laser protective eyewear is usually not required for Class 2 and Class 3a lasers or laser systems except in conditions where intentional long-term (>0.25 seconds) direct viewing is required.

Laser protective eyewear may include goggles, face shields, spectacles, or prescription eyewear using special filter materials or reflective coatings (or a combination of both) to reduce the potential ocular exposure below the applicable MPE level.

Eyewear shall have the following requirements:

Protective eyewear shall be used only at the wavelength and energy/power for which it is intended.

Label the protective eyewear with the laser type and/or light wavelength that the eyewear is designed for.

Keep protective eyewear in good condition. Replace damaged or defective eyewear.

ANSI Z136.1-2000 Section 4.6.2 can be used to select appropriate eyewear.

Other Protective Equipment

Protective eyewear should not be considered the primary means to protect against laser radiation. Protective equipment such as beam stops, shields, safety interlocks, and warning lights and horns shall be maintained in proper operating condition and shall be utilized whenever indicated to prevent harmful exposure to laser radiation.

Reference: ANSI Z136.1-2000, Guide for the Safe Use of Lasers, 2000

IV. ELECTRICAL MAINTENANCE MANAGEMENT FOR NUCLEAR AND NON-NUCLAR FACILITIES

(Applies only to candidates assigned oversight of electrical maintenance activities. Each competency statement is a MPA, provided that they are applicable to the candidates assigned electrical duties.)

## Become familiar with DOE maintenance management requirements as defined in DOE O 433.1, Maintenance Management Program, and DOE G 433.1-1.

- Define each of the following maintenance-related terms and explain their relationship to each other.

Corrective

Planned

Preventive

Reliability centered

Predictive

### Corrective

Corrective maintenance refers to the repair of failed or malfunctioning equipment, systems, or facilities to restore the intended function or design condition.  This maintenance does not result in significant extension of expected useful life.

### Planned

Planned maintenance refers to maintenance activities performed prior to equipment failure.  The activities can be initiated by predictive or periodic maintenance results, by vendor recommendations, or by experience.

### Preventive

Preventive maintenance refers to predictive, periodic, and planned maintenance actions taken to maintain a piece of equipment within design operating conditions and extend its life.

### Reliability Centered

Reliability centered maintenance refers to a method for establishing a scheduled maintenance program that can effectively and economically realize the inherent reliability and safety levels of equipment.

### Predictive

Predictive maintenance refers to maintenance activities involving continuous or periodic monitoring and diagnosis to forecast equipment failure.

Reference: DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide for Use with DOE O 433.1, September 2001

Discuss the importance of maintaining a proper balance of preventive and corrective maintenance.

A proper balance of corrective and preventive maintenance should be employed to provide a high degree of confidence that property degradation is identified and corrected, that equipment life is optimized, and that the maintenance program is cost-effective.

Reference: DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide for Use with DOE O 433.1, September 2001

Identify typical maintenance performance indicators, and discuss their importance.

Surveillance, inspecting, and testing activities should provide assurance that the equipment needed for safe and reliable facility operation performs within required limits and that preventive maintenance, defined as including periodic and planned maintenance, is utilized to maintain a piece of equipment within design operating conditions and to realize its maximum reasonable useful life.  The potential impact of seasonal variations should be considered.

A predictive maintenance performance program should be established and utilized to monitor equipment and determine trends.  The program should also analyze parameters, properties, and performance characteristics or signatures of equipment to forecast equipment degradation so that “as-needed” planned maintenance can be performed prior to equipment failure.

Corrective maintenance should be performed in a manner ensuring that quality repairs are performed and that equipment failing or malfunctioning during service is restored in a timely manner.

Reference: DOE Order 4330.4B, Maintenance Management Program (Canceled).

Discuss the relationship between maintenance and conduct of operations, quality assurance, and configuration management.

Maintenance has a primary role in preserving DOE property and ensuring safe and reliable operation of facilities.  The purpose of maintenance guidelines is to describe the 32 key elements of an overall DOE maintenance management program.  Key elements include material that incorporates the concepts included in other DOE Orders associated with matters related to the maintenance program.  For example, the discussion on procedures is consistent with the direction of DOE Order 5480.19, Conduct of Operations Requirements for DOE Facilities.

Similarly, there is considerable carry over from DOE O 414.1, Quality Assurance.  The maintenance guidance, in many cases, repeats the information from the referenced Orders. The material from these Orders is retained in maintenance guidelines to facilitate the maintenance organizations’ incorporation of the elements and their criteria into the program. In many cases the objectives and criteria of all applicable Orders are consistent and can be met by one program.

Reference: DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide for Use with DOE O 433.1, September 2001

Discuss the requirements for receiving and inspecting parts, materials, and equipment.

Policies should be established for the procurement of parts, materials, and equipment.  These policies must be understood by stores and purchasing personnel and other personnel who interface with the stores and purchasing operations, such as maintenance supervisors, planning, and scheduling personnel.

Procedures should be prepared to specifically describe the responsibilities of personnel involved in the procurement function.  Specific procurement actions should be included in these procedures.

A system should be established as part of the design change process to update spare parts needs and remove outdated/obsolete materials from the stock system.

Timely procurement of parts, materials, and equipment for maintenance activities can be enhanced by considering items such as the following:

Early identification of “long lead-time” items

Selection of procurement sources based on approved vendors and past vendor performance

Identification of appropriate quality, engineering, environmental, shelf life, preventive maintenance, and vendor technical manual requirements

Update of spare parts inventory following design modifications

Participation in a “pooled” spare parts system with other facilities that share common or nearby sites

Controls should be developed and maintained throughout the procurement process to help obtain parts, materials, and services in a timely manner.  Controls such as the following should be provided:

Reliability of supplier performance should be verified.  This can be accomplished by audits, inspections, or surveillance of supplier facilities, processes, methods, or records relevant to the part, material, or service provided.

Deficient or nonconforming items should be resolved in an effective and timely manner.  Technical reviews should be initiated promptly to aid in the resolution of these items.

Quality assurance records need to be controlled and maintained to provide documentation for qualified parts and materials and to ensure traceability of parts and materials.

A process should be provided to qualify nonqualified material.  An effective upgrade process will result in improved availability of quality parts and materials.

A process for acceptable substitution should be provided to obtain parts that are no longer available from the original supplier, that have new identification numbers, or that have different material specifications.  Engineering and maintenance experience should be provided to support this process.  Change approval documentation and substitution information should be maintained in a retrievable form.

Reference: DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide for Use with DOE O 433.1, September 2001

Describe the difference between temporary and permanent repairs/work and the requirements and controls in place to prevent inadvertent modifications.

Temporary repairs are temporary modifications to the facility that allow equipment to remain in or be returned to service in a condition that is not the same as the original design specification.  Prior to implementation, temporary repairs should receive a safety review in accordance with the facility temporary modification program to ensure the adequacy of the repair and its effect on personnel and equipment safety and reliability.  Temporary repairs should be tracked after their completion for consideration of permanent repairs.  Permanent corrective action should be taken as soon as practicable.

Reference: DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide for Use with DOE O 433.1, September 2001

Discuss the importance and methods of establishing acceptance criteria for inspection and testing.

Equipment that is important to safe and reliable facility operation should be tested in accordance with approved procedures.  Post maintenance test (PMT) procedures should contain acceptance criteria that aid in measuring the performance of repaired equipment.  Baseline data should be provided, if applicable.

If a surveillance test, calibration, or special procedure does not exist to test particular equipment following maintenance, a special test procedure may be written, or the test may be performed in accordance with instructions written for the work request or work order.  With any of these procedure methods, the required and actual testing performed should be described, data recorded, acceptance criteria specified, and appropriate reviews and approvals performed and documented.  If special test procedures are written to perform PMTs, the appropriate safety and technical reviews should be performed in accordance with facility procedures.

Test instructions should include details such as initial conditions and prerequisites, hold points, cautions, personnel qualification requirements, personnel safety requirements, clear acceptance criteria, and posttest restoration.

Test instructions should be as specific as possible and should avoid using vague criteria such as “verify proper operation” or “check for excessive temperature.”

Reference: DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide for Use with DOE O 433.1, September 2001

## Become familiar with NFPA 70B safety requirements for electrical equipment maintenance, to include:

Electrical preventive maintenance program elements (Ch. 5);

Training requirements (Ch. 5);

Special precautions relating to electronic equipment, e.g., equipment deenergization, zero-energy checks, prevention of shock, grounding requirements for maintenance actions (Ch. 12);

GFCI and GFPE maintenance requirements, e.g., trip tests, records keeping, approved listing of test equipment (Ch. 14);

Testing and test methods: precautions and safety; qualifications of test operators; test equipment; protective device testing (Ch. 20);

Deenergizing and grounding of equipment to provide protection for electrical maintenance personnel, (Ch. 23); g. Grounding requirements, e.g., symptoms and causes of inadequate grounding; grounding system inspection, testing and monitoring; and, solutions to inadequate grounding (Ch. 29).

Maintenance and servicing of transformers, cables, breakers, and motors (Ch. 10, 11, 14, and 17 respectively).

### Electrical Preventive Maintenance

The term “electrical preventive maintenance” (EPM) refers to a program of regular inspection and service of equipment to detect potential problems and to take proper corrective measures through the approved work process controls.

#### Development and Implementation Requirements

An EPM program should be developed and implemented based on the requirements of:

DOE O 433.1, Maintenance Management Program for DOE Nuclear Facilities (2001)

NFPA 70B, Recommended Practice for Electrical Equipment Maintenance (2002)

NFPA 70E, Standard for Standard for Electrical Safety in the Workplace (2004)

NFPA 72, National Fire Alarm Code (2002)

National Electrical Testing Association (1997)

ANSI-C2, National Electrical Safety Code (2002)

#### Definition

An EPM program is defined as the system that manages the conducting of routine inspections and tests and the servicing of electrical equipment so that impending troubles can be detected and reduced or eliminated.  Where designers, installers, or constructors specify, install, and construct equipment with optional auxiliary equipment, that optional equipment should be part of the EPM program.  Records of all inspections, tests, and servicing should be documented and reviewed.

All electrical equipment that is appropriate for EPM should be inspected, tested, and serviced in accordance with an EPM program.

Inspections, tests, and servicing shall be performed by personnel who are qualified for the work to be performed.  These qualifications can be shown by appropriate documentation of work experience, on-the-job, and offsite formal training to verify understanding and retention of minimum knowledge, skills, and abilities.

#### Maintenance

Electrical equipment should be maintained in accordance with the manufacturer’s recommendations and instructions for the local operating environment.  A copy of the manufacturer’s recommendations should be documented and on file.

#### Inspection

If an EPM program does not exist, an inspection, testing, and servicing program should be developed and implemented to establish a baseline to initiate an EPM program.  The inspection frequency should be as recommended by the manufacturer or as otherwise indicated in NFPA 70B.  An initial period of inspection (sometimes several years) provides sufficient knowledge that, when accumulated, may permit increasing or decreasing that interval based upon documented observations and experience.

The EPM program should include the essential elements described in NFPA 70B, Chapter 5, What is an Effective EPM Program?  This includes planning, identifying the main parts, and utilizing available support services for a program.  For example:

Assigning qualified personnel

Surveying and analyzing equipment maintenance requirements

Performing routine inspections and tests

Analyzing inspection and test reports

Prescribing corrective measures

Performing necessary work

Preparing appropriate records.

#### Planning and Developing an EPM Program, and Fundamentals Of EPM

The EPM program should be planned and developed to include each of the functions, requirements, and economic considerations described in NFPA 70B, Chapter 6, Planning and Developing an EPM Program, and NFPA 70B, Chapter 7, Fundamentals of EPM.  Chapter 6 includes surveying the existing electrical system installation, identifying crucial equipment, establishing a systematic program to follow, and developing methods and procedures to plan, analyze, perform, verify, and record.

Electrical drawings should be kept current.  A system of recording changes in electrical systems and then integrating those changes into the applicable drawings should be developed and implemented.

NFPA 70B includes designing to accommodate maintenance, scheduling maintenance, personnel and equipment safety, circuit protection, and initial acceptance testing.

### Training Requirements

Establish qualification requirements, training programs and certifications where appropriate for all personnel.

Prior to performing electrical work, personnel must be qualified to perform job-related electrical tasks as required by 29 CFR 1910.332.

Personnel exposed to the presence of voltages of 50 V or more will have formal electrical safety awareness training.  This training can be in a classroom or on the job.

All training must be documented.

Instructors must provide course outlines.

Proof of successful completion must be maintained in appropriate files.

Minimum training requirements should include

electrical safety awareness;

electrical safety theory;

applicable codes, DOE orders, regulations, and standards;

demonstrations and hands-on practice;

use and care of personal protective equipment;

job-specific safe electrical work practices; and

electrical requirements of safe operating procedures and operating procedures.

Personnel working with high voltage (greater than 600 V) must have specialized electrical awareness training.

Periodic training refresher courses are required to maintain and update skills and code requirements.

Management and supervision who oversee electrical work must have completed Electrical Safety Awareness Training at a level commensurate with the level of work being performed.

### Special Precautions for Electronic Equipment

This section provides guidelines to

complement existing electrical codes and recommend industry standards,

improve electrical safety in the work environment for personnel within the DOE complex.

eliminate the ambiguity and misunderstanding in design, construction and implementation requirements for electrical/electronic equipment, and

assist the Authority Having Jurisdiction in providing information for acceptance of equipment within the scope of DOE-HDBK-1092-2004.

#### Scope

This section addresses enclosed electrical/electronic equipment electrical safety guidelines which are not specifically addressed elsewhere in the DOE Electrical Safety Handbook.  These types of equipment include: instrumentation and test consoles; enclosed electrical/electronic equipment; other laboratory diagnostic electrical/electronic equipment (stationary or mobile) mounted in or on an enclosure, rack or chassis; and special electrical/electronic equipment facility requirements.

#### Grounding and Bonding

Many ground system types exist within electrical equipment.  All metal parts of electrical equipment enclosures and chassis shall be bonded and grounded as per the NEC.  The methods chosen to avoid ground loops and reduce noise shall meet the requirements of the NEC 250.6.

#### Objectional Current Over Grounding Conductors

Enclosed electrical/electronic equipment has both power and signal conductors entering and leaving these enclosures.  Objectionable currents and noise may be the result of the design or installation of conductors and equipment and their grounding locations.  NEC 250.6 addresses these objectionable currents and noise (See Section 10.9.2.1).

NEC 250.6 must be used with care because it seems to give blanket authority to do whatever is necessary to stop objectionable currents from flowing in the grounding system.  This is not the intent.  NEC 250.6D specifically indicates that the introduction of noise or data errors in electronic equipment shall not be considered objectionable currents, as addressed therein.

Therefore, such objectionable currents must be handled in other ways.  NEC section 250.6 principally deals with objectionable currents that can flow over grounding conductors due to severely unbalanced loads or improper installation practices.  NEC 250.96(B) provides requirements for isolation of grounding circuits to reduce electrical noise (EMI).  Because of the complexity and number of interconnections of most grounding systems, the NEC allows modifications of the grounding system and connections in order to address such problems.  Those permitted:

Arrangement to prevent objectionable current.  Grounding of electrical systems, circuit conductors, surge arresters, and conductive noncurrent-carrying materials and equipment shall be installed and arranged in a manner that will prevent an objectionable current over the grounding conductors or grounding paths.  Use of a single-point grounding system, as well as meeting the other requirements of NEC Article 250, will usually overcome problems.

Alterations to stop objectionable current.  If the use of multiple grounding connections results in an objectionable current, one or more of the following alterations are permitted to be made, provided that the requirements of NEC 250.4(A)(5)(B)(4), are met.  Such permitted alterations are:

Discontinue one or more, but not all, of the grounding connections;

Change the locations of the grounding connections;

Interrupt the continuity of the conductor or conductive path interconnecting the grounding connections; and/or

Take other suitable remedial action satisfactory to the authority having jurisdiction.

Temporary currents not classified as objectionable currents.  Temporary currents resulting from accidental conditions, such as ground-fault currents, that occur only while the grounding conductors are performing their intended protective functions shall not be classified as objectionable.  This does not prohibit changes in the system to correct excessive current during a fault condition.

Limitations to permissible alterations.  The intent of NEC 250.6 is not to permit electronic equipment to be operated on AC systems or branch circuits that are not grounded as required by NEC Article 250.  Currents that introduce noise or data errors in electronic equipment are not considered to be the objectionable currents.  Voltage differences and thus objectionable currents may exist because impedances to ground are not equal throughout a grounding system due to variations of the resistance of the earth, improper connections, or other problems.  Even though voltage differences allow unwanted currents to flow in the grounding conductors, and induced noise may travel over this path, it is not to be used as a reason to disconnect all grounding connections to any system component.  At least one grounding connection must remain.

#### Equipment Grounding Conductor

The equipment grounding conductor of a power-supply cord or interconnecting cable should be size in accordance with NEC 250.122 and the associated NEC Table 250.122.  The minimum size equipment grounding conductor is based on the total rating of the enclosed equipments in amperes.  Note that the minimum size equipment grounding conductor may be smaller than the size for the current-carrying conductors; i.e., the grounded (neutral) and ungrounded conductors, which are sized per NEC Article 310.15 – usually following NEC Table 310.16.

Systems feeding power isolation transformers must continue the equipment grounding conductor to the equipment or the ungrounded equipment must be guarded and labeled.  For two-wire cord connected equipment, an equipment grounding connector should be installed according to the manufacturer’s instructions.

### GFCI and GFPE Maintenance Requirements

The EPM program should include the essential ingredients of chapter 14 of NFPA 70B, Ground Fault Protection.  This includes ground-fault circuit interrupters (GFCls) and ground-fault protection for equipment (GFPE).

Ground-fault protective devices are intended to protect personnel and equipment.  There are two distinct types — GFCI and GFPE — and it is extremely important to understand the difference between them.

A GFCI is defined in Article 100 of the NEC as a device intended for the protection of personnel in their job assignments. (See NEC 210.8, 215.9, 427, 527)

A GFPE is defined in Article 100 of the NEC as a system intended to provide protection of equipment from line-to-ground fault currents.  GFPE systems (equipped with or without a test panel) shall be inspected and tested at installation and at specified intervals as recommended by the manufacturer.

### Testing and Test Methods

Sometimes it becomes necessary to check the continuity of power circuits, control circuits, etc., by using a particular testing instrument (volt, ohm, and/or amp meter) designed for the testing involved.  The voltage device used shall be rated for the application.  Proximity testers and solenoid-type devices should not be used to test for the absence of voltage because they do not accurately detect and/or measure voltage.  Also, proximity testers will not detect direct current (DC) or AC voltage in a cable that is shielded.  Proximity testers are very useful in certain applications; for example, for finding cables that go through a panel but that do not terminate in the panel.  However, it should be noted that a proximity tester’s failure to detect voltage does not guarantee that the equipment or device is deenergized.  The absence of voltage can only be verified with a voltmeter rated for the application.

Voltmeters, both analog and digital, are designed for a number of applications from appliance troubleshooting to power system testing.  The type of voltmeter used depends on where in the power system you are using the meter.  The user must read and understand the manufacturer’s instructions on the use and application of the voltmeter.  When a multi-function, multi-scale meter is used, it is important for the user to select the function and scale necessary for the task being performed in order to avoid damage or destruction of the meter and injury to the employee.  The selection of test instruments and equipment shall be based on its application and categorization.

### Deenergizing Equipment

Safe procedures for deenergizing circuits and equipment shall be determined before circuits or equipment are deenergized.  Deenergization procedures shall be included in the lockout/tagout procedure for the circuit or equipment to be deenergized.

### Maintenance and Servicing of Transformers

Ferro-resonance can generate overvoltages of up to 12 times line-to-ground source voltage upon opening of a single-phase device or a poorly synchronized three-phase device.  Violent failure can occur, exposing personnel to the high-voltage failure and accompanying conditions.

Ferro-resonant conditions can result in damage to lightning arresters, switching devices, buried cable, transformers, and associated equipment.

Ferro-resonance can be initiated when all of the following elements are present and the switching means at dip point or takeoff is either a single-phase device or an unsynchronized three-phase device that does not operate all phases within one-half cycle:

System grounded at the source but with no ground at the transformer bank, such as a transformer or transformer bank connected delta on a grounded-wye system.

Shielded cable or overhead conductor length sufficient to create the capacitance necessary.

Transformer size that permits saturation of the iron core at the operating voltage

Transformer unloaded or very lightly loaded.

Prevention or control of ferro-resonance may be accomplished by any of the following measures:

Using a wye-wye transformer connection with both neutrals grounded and tied to the system neutral.

Using only phase-to-neutral (not phase-to-phase) transformer connections for single-phase transformers.

Limiting length of underground cable between transformers and single-pole or poorly synchronized three-pole switching devices.

If single-pole or poorly synchronized switching devices must be used, ensuring that transformer and underground cable are loaded in excess of 2% resistive load of the transformer capacity.

If transformer primary is ungrounded-wye, temporarily grounding the neutrals of the transformers being switched.

Installing close-coupled, high-speed, three-pole switching devices to minimize the duration of the single-phase condition during opening and closing of the circuit.

Reference: DOE-HDBK-1092-2004, Electrical Safety, 2004

## Become familiar with the NFPA 70E, Chapter 2, safety-related maintenance requirements relating to:

Grounding and bonding;

Safety equipment and clear space requirements;

Electrical systems and components;

Hazardous locations;

PPE

Identify and discuss elements of an electrical safety program, including the following:

Two-man rule

- Stored energy

- Component labeling

### Grounding and Bonding

This section presents general rules for the grounding and bonding of electrical installations.

Qualified workers should clearly understand the concepts of grounding practices as required by the NEC.  They should also clearly understand the definition and intent of the following components of a grounding system that are explained in this section:

Grounded conductor

Grounding conductor

Grounding electrode conductor

Bonding jumper

Grounding electrode

Engineering specifications and drawings should identify the requirements for all components and clearly illustrate the grounding electrode system, the grounding electrode conductor, bonding points, and bonding jumpers, and the connection point for the grounded conductor and the grounding conductors.  Where used for installation or construction purposes, these specifications and drawings should also include detailed installation instructions.

Circuit and system grounding consists of connecting the grounded conductor, the equipment grounding conductor, the grounding bus bars, and all non-current-carrying metal parts to ground.

This is accomplished by connecting a properly sized unspliced grounding electrode conductor between the grounding bus bar and the grounding electrode system.  There are three fundamental purposes for grounding an electrical system:

To limit excessive voltage from lightning, line surges, and crossovers with higher voltage lines.

To keep conductor enclosures and non-current-carrying metal enclosures and equipment at zero potential to ground.

To facilitate the opening of overcurrent protection devices in case of insulation failures because of faults, short circuits, etc.

Equipment grounding systems, which consist of interconnected networks of equipment grounding conductors, are used to perform the following functions:

Limit the hazard to personnel (shock voltage) from the non-current-carrying metal parts of equipment raceways and other conductor enclosures in case of ground faults, and

Safely conduct ground-fault current at sufficient magnitude for fast operation of the circuit overcurrent protection devices.

To ensure the performance of the above functions, equipment grounding conductors are required to:

Be permanent and continuous

Have ample capacity to safely conduct ground-fault current likely to be imposed on them; and

Have impedance sufficiently low to limit the voltage to ground to a safe magnitude and to facilitate the operation of the circuit overcurrent protection devices.

Caution shall be taken to ensure that the main bonding jumper and equipment bonding jumper are sized and selected correctly.  Bonding completes the grounding circuit so that it is continuous.  If a ground fault occurs, the fault current will flow and open the overcurrent protection devices.  The means of bonding shall provide the following to ensure the grounding system is intact:

Provide a permanent connection,

Provide a positive continuity at all times, and

Provide ampacity to conduct fault current.

#### Grounded or Ungrounded Systems

Ungrounded systems may provide greater continuity of operations in the event of a fault.  However, the second fault will most likely be more catastrophic than a grounded system fault.  Whenever ungrounded systems are used in a facility, the maintenance personnel should receive training in how to detect and troubleshoot the first fault on an ungrounded system.  “Grounded” means that the connection to ground between the service panel and earth has been made.  Ungrounded electrical systems are used where the designer does not want the overcurrent protection device to clear in the event of a ground fault.

Ground detectors can be installed per NEC to sound an alarm or send a message to alert personnel that a first fault has occurred on one of the phase conductors.  Ground detectors will detect the presence of leakage current or developing fault current conditions while the system is still energized and operating.  By warning of the need to take corrective action before a problem occurs, safe conditions can usually be maintained until an orderly shutdown is implemented.

#### Grounded Systems

Grounded systems are equipped with a grounded conductor that is required to be run to each service disconnecting means.  The grounded conductor can be used as a current-carrying conductor to accommodate all neutral related loads.  It can also be used as an equipment grounding conductor to clear ground faults ahead of the service disconnecting means.  A network of equipment grounding conductors is routed from the service equipment enclosure to all metal enclosures throughout the electrical system.  The equipment grounding conductor carries fault currents from the point of the fault to the grounded bus in the service equipment where it is transferred to the grounded conductor.  The grounded conductor carries the fault current back to the source and returns over the faulted phase and trips open the overcurrent protection device.

Note: A system is considered grounded if the supplying source, such as a transformer or generator is grounded in addition to the grounding means on the supply side of the service equipment disconnecting device for separately derived systems.

The neutral of any grounded system serves two main purposes: (1) it permits the utilization of line-to-neutral voltage and thus will serve as a current-carrying conductor to carry any neutral current, and (2) it plays a vital role in providing a low-impedance path for the flow of fault currents to facilitate the operation of the overcurrent devices in the circuit.

#### Ungrounded Systems

Ungrounded systems operate without a grounded conductor.  In other words, none of the circuit conductors of the electrical system are intentionally grounded to an earth ground such as a metal water pipe, or building steel.  The same network of equipment grounding conductors is provided for ungrounded systems as for solidly grounded electrical systems.  However, equipment grounding conductors (EGCs) are used only to locate phase-to-ground faults and sound some type of alarm.  Therefore, a single sustained line-to-ground fault does not result in an automatic trip of the overcurrent protection device.  This is a major benefit if electrical system reliability is required or if it would result in the shutdown of a continuous process.  However, if an accidental ground fault occurs and is allowed to flow for a substantial time, over-voltages can develop in the associated phase conductors.  Such an over-voltage situation can lead to conductor insulation damage, and while a ground fault remains on one phase of an ungrounded system, personnel contacting one of the other phases and ground are subjected to 1.732 times the voltage they would experience on a solidly neutral grounded system.

#### Grounding Requirements

Alternating current systems of less than 50 volts shall be grounded as required in NEC.  Systems of 50 to 1,000 V should be solidly grounded as required by NEC.  Systems supplying phase-to-neutral loads shall also be solidly grounded.  The following electrical systems are required to be solidly grounded:

240/120-V, single-phase, three-wire

208Y/120-V, three-phase, four-wire

480Y/277-V, three-phase, four-wire

240/120-V, three-phase, four-wire, delta (midpoint of one phase used as a grounded circuit conductor)

The following systems are not required to be solidly grounded:

240-V, three-phase, three-wire delta

480-V, three-phase, three-wire

600-V, three-phase, three-wire.

Reference: DOE-HDBK-1092-2004, Electrical Safety, 2004

### Safety Equipment and Clear Space Requirements

Working space around electrical enclosures or equipment shall be adequate for conducting all anticipated maintenance and operations safely, including sufficient space to ensure safety of personnel working during emergency conditions and workers rescuing injured personnel.  Spacing shall provide the dimensional clearance (discussed in the following subsections) for personnel access to equipment likely to require examination, adjustment, servicing, or maintenance while energized.  Such equipment includes panelboards, switches, circuit breakers, switchgear, controllers, and controls on heating and air conditioning equipment.

These clearances shall be in accordance with NESC and NEC.  These working clearances are not required if the equipment is not likely to require examination, adjustment, servicing, or maintenance while energized.  However, sufficient access and working space is still required.

Reference: DOE-HDBK-1092-1092-2004, Electrical Safety Manual, 2004

### Electrical Systems and Components

Qualified employees performing such tasks as electrical repairs, modifications, and tests on energized electrical systems, parts, and equipment need to comply with the following:

Parts to which an employee might be exposed shall be put into an electrically safe work condition before the employee works on or near them, unless the employer can demonstrate that deenergizing introduces additional or increased hazards or is infeasible due to equipment design or operational limitations.

Personnel shall not work on energized circuits unless they are qualified to do so, or, for training purposes, unless they work under the direct supervision of a qualified person.

Sufficient protection in the form of insulated tools and insulated protective equipment, such as gloves, blankets, sleeves, mats, etc., shall be used while working on energized circuits.

### Hazardous Locations

Hazardous areas and locations are classified by group, class, and division.  These classifications are determined by the atmospheric mixtures of various gases, vapors, dust, and other materials present.  The intensity of the explosion that can occur depends on concentrations, temperatures, and many other factors that are listed in NFPA codes.

Hazardous locations must be well understood by anyone designing, installing, working on, or inspecting electrical equipment and wiring in such areas.  Such locations carry a threat of flammable or combustible gases, vapors, or dusts being present some or all of the time.

Information in the following paragraphs assist in classifying areas or locations with respect to hazardous conditions, whether from atmospheric concentrations of hazardous gases, vapors, and deposits, or from accumulations of readily ignitable materials.

This section covers the requirements for electrical equipment and wiring in locations that are classified according to the properties of the flammable vapors, liquids, or gases or combustible dusts that may be present and the likelihood that a flammable or combustible concentration is present.  The hazardous (classified) locations are assigned the following designations:

Class I Division 1

Class I Division 2

Class II Division 1

Class II Division 2.

Class I, Zone 0, Zone 1, Zone 2

Class III fibers and flyings are not covered here

#### Class I

Class I locations are identified in the NEC as those in which flammable gases or vapors are or may be present in the air in amounts sufficient to create explosive or ignitable mixtures.  Gases or vapors may be continuously or intermittently present.  However, if a gas or vapor is present, there is a potential that a flammable mixture will be present.

From an engineering standpoint, greater precautions are needed if a particular set of conditions is likely to occur (e.g., the presence of a flammable mixture within the explosive range) than if it is unlikely.  This is the reason for dividing hazardous locations into two divisions.

#### Division 1

NEC 500.5 defines Class I Division 1 hazardous locations as those in which:

Ignitable concentrations of flammable gases, liquids, or vapors can exist under normal operating conditions;

Ignitable concentrations of such gases or vapors may exist frequently because of repair or maintenance operations or because of leakage; or

Breakdown or faulty operation of equipment or processes might release ignitable concentrations of flammable gases, liquids, or vapors and might also cause simultaneous failure of electrical equipment.

Note: In each case, ignitable concentrations are mentioned.  This means concentrations between the lower and upper flammable or explosion limits.

NEC Article 100 defines a flammable liquid as one that has a flashpoint below 38°C (100°F) or one whose temperature is raised above its flashpoint.  Flashpoint is the lowest temperature to which a combustible or flammable liquid may be heated before sufficient vapors are driven off and the liquid will flash when brought into contact with a flame, arc, spark, or another ignition source.

#### Division 2

NEC 500.5(B)(2) defines Class I Division 2 locations as those:

In which flammable liquids or gases are handled, processed, or used, but where such materials are normally confined in closed containers or closed systems from which they can escape only in case of accidental rupture or breakdown of such containers or systems or in case of abnormal equipment operation.

In which gases or vapors are normally prevented, by positive mechanical ventilation, from forming ignitable concentrations and which might become hazardous through failure or abnormal operation of the ventilating equipment

That are adjacent to a Class I Division 1 location and to which ignitable concentrations of gases or vapors might occasionally be transmitted unless such transmittal is prevented by adequate positive-pressure ventilation from a source of clean air, and effective safeguards against ventilation failure are provided.

The fine-print note #2 to NEC 500.5 describes a number of areas and occupancies normally classified as Class I Division 2 locations.  For example, piping systems without valves, meters, and devices do not usually cause a hazardous condition, even though they carry flammable liquids, because they are considered a contained system.  Therefore, the surrounding area can be classified as a Class I Division 2 location.

#### Class II

A Class II location is defined in NEC 500 as an area where combustible dust presents a fire or explosion hazard.  Class II locations are divided into two divisions based on the normal presence or absence of dust.

#### Class II Division 1

A Class 11 Division 1 location is one:

In which combustible dust is in the air under normal operating conditions in quantities sufficient to produce explosive or ignitable mixtures;

Where mechanical failure or abnormal operation of machinery or equipment might cause such explosive or ignitable mixtures to be produced and might also provide a source of ignition through simultaneous failure of electrical equipment, operation of protective devices, or other causes; or

In which combustible dusts of an electrically conductive nature may be present in hazardous quantities.

#### Class II Division 2

A Class II Division 2 location is one where:

Combustible dust is not normally in the air in quantities sufficient to produce explosive or ignitable mixtures;

Dust accumulations are normally insufficient to interfere with the normal operation of electrical equipment or other apparatus, but where combustible dust may be suspended in the air as a result of infrequent malfunctioning of handling or processing equipment; and

Combustible dust accumulations on, in, or in the vicinity of the electrical equipment may be sufficient to interfere with the safe dissipation of heat from electrical equipment or may be ignitable by abnormal operation or failure of electrical equipment.

Reference: DOE-HDBK-1092-2004, Electrical Safety, 2004

### PPE

Qualified workers are responsible for avoiding and preventing accidents while performing electrical work, repairs, or troubleshooting electrical equipment.  Personnel shall wear or use PPE and protective clothing that is appropriate for safe performance of work.  Qualified workers need to use appropriate arc-fault PPE whenever they work near electrical equipment that could create an arc flash hazard.

Reference: DOE-HDBK-1092-2004, Electrical Safety, 2004

### Two Man Rule

Never work on a project site alone.  Safety procedures require a minimum of two personnel during the installation, maintenance, or operation of any equipment.

Reference: DOE-HDBK-1092-2004, Electrical Safety, 2004

### Stored Energy

For discharge equipment with stored energy in excess of 10 joules

A discharge point with an impedance capable of limiting the current to 500A or less should be provided.

The discharge point must be identified with a unique marker (example: yellow circular marker with a red slash), and should be labeled "HI Z PT" in large legible letters.

A properly installed grounding hook should first be connected to the current-limiting discharge point and then to a low-impedance discharge point (< 0.1 ohm) that is identified by a unique marker (example: yellow circular marker).

### Component Labeling

For all chassis and rack cabinets (electrical, computer, power distribution, etc.), the manufacturer’s name, trademark, or other descriptive marking of the organization responsible for the product should be identified.

Other markings for power requirements are:

Voltage

Maximum rated current in amperes

Wattage

Frequency

Duration

Duty cycle

Other ratings as specified in the NEC (NEC 110.21)

Reference: DOE-HDBK-1092-2004, Electrical Safety, 2004

V. ELECTRICAL DESIGN & INSTALLATION (SAFETY AND SYSTEMS)

(Applies only to candidates assigned oversight of electrical design and installation activities.  Each competency statement is a MPA, provided that they are applicable to the candidate’s assigned electrical duties.)

## Demonstrate a working-level knowledge of the current national electrical code, and become familiar with the requirements for wiring design and protection (NFPA 70, NFPA 70E, chapter 4) to include:

Use of listed and labeled, Nationally Recognized Test Laboratory (NRTL), electrical equipment (also reference 29 CFR 1910.303 & .399, and 29 CFR 1926.403);

Branch circuits identification;

GFCI protection for personnel;

Outside circuits and conductors for 600 volts (or less) systems;

Overcurrent protection for 600 volts (or less) and greater-than 600 volts circuits;

Grounding and bonding requirements as noted in NFPA 70E Article 410.10.

### NRTL

Electrical equipment is considered to be acceptable either by being listed by an NRTL, designed, manufactured, and tested according to nationally recognized standards, or approved by AHJ-determined criteria.  Procurement and use of equipment not listed by an NRTL should be reviewed by the AHJ.  The extensive testing involved in the listing process usually cannot be duplicated at the user facility, and many of the tests are destructive in nature.  The AHJ should develop an examination acceptance process to ensure appropriate confidence in the safety of the product.

Reference: DOE-HDBK-1092-2004, Electrical Safety, 2004

### Branch Circuits

Branch circuits are the conductors between the last overcurrent device in an electrical system and the outlets, such as receptacles, lighting outlets, and outlets for electrical equipment wired directly into a circuit.  Branch circuits for temporary wiring shall originate inside an approved panel board or power outlet that is rated for the voltages and currents the system is expected to carry.  As with feeders, branch circuit conductors can be contained within multi-conductor cord or cable assemblies.

Reference: DOE-HDBK-1092-2004, Electrical Safety, 2004

### GFCI Protection for Personnel

There are two classes of GFCIs, each with a distinct function.  A Class A GFCI trips when the current to ground has a value in the range of 4 through 6 milliamperes and is used for personnel protection.  A Class A GFCI is suitable for use in branch circuits.  A Class B GFCI (commonly used as ground fault protection for equipment) trips when the current to ground exceeds 20 milliamperes.  A Class B GFCI is not suitable for employee protection.  Ground-fault circuit protection can be used in any location, circuit, or occupancy to provide additional protection from line-to-ground shock hazards because of the use of electric hand tools.  There are four types of GFCIs used in the industry:

Circuit breaker type

Receptacle type

Portable type

Permanently mounted type

The condition of use determines the type of GFCI selected.  For example, if an electrician or maintenance person plugs an extension cord into a non-protected GFCI receptacle, the easiest way to provide GFCI protection is to utilize a portable-type GFCI.

Reference: DOE-HDBK-1092-2004, Electrical Safety, 2004

### Outside Circuits

Outside conductors, 600 volts, nominal, or less.  The following paragraphs apply to branch circuit, feeder, and service conductors rated 600 volts, nominal, or less and run outdoors as open conductors.

Conductors on poles. Conductors supported on poles shall provide a horizontal climbing space not less than the following:

Power conductors below communication conductors--30 inches.

Power conductors alone or above communication conductors: 300 volts or less--24 inches; more than 300 volts--30 inches.

Communication conductors below power conductors with power conductors 300 volts or less--24 inches; more than 300 volts--30 inches.

Clearance from ground. Open conductors shall conform to the following minimum clearances:

10 feet--above finished grade, sidewalks, or from any platform or projection from which they might be reached.

12 feet--over areas subject to vehicular traffic other than truck traffic.

15 feet--over areas other than those specified in paragraph in 29 CFR 1910.304 that are subject to truck traffic.

18 feet--over public streets, alleys, roads, and driveways.

Clearance from building openings. Conductors shall have a clearance of at least 3 feet from windows, doors, porches, fire escapes, or similar locations.  Conductors run above the top level of a window are considered to be out of reach from that window and, therefore, do not have to be 3 feet away.

Clearance over roofs. Conductors shall have a clearance of not less than 8 feet from the highest point of roofs over which they pass, except that:

Where the voltage between conductors is 300 volts or less and the roof has a slope of not less than 4 inches in 12, the clearance from roofs shall be at least 3 feet, or

Where the voltage between conductors is 300 volts or less and the conductors do not pass over more than 4 feet of the overhang portion of the roof and they are terminated at a through-the-roof raceway or approved support, the clearance from roofs shall be at least 18 inches.

Reference: 29 CFR 1910.304, Wiring Design and Protection, July 1, 2006

### Overcurrent Protection

The following requirements apply to overcurrent protection of circuits rated 600 volts, nominal, or less.

Protection of conductors and equipment. Conductors and equipment shall be protected from overcurrent in accordance with their ability to safely conduct current.

Grounded conductors. Except for motor running overload protection, overcurrent devices may not interrupt the continuity of the grounded conductor unless all conductors of the circuit are opened simultaneously.

Disconnection of fuses and thermal cutouts. Except for service fuses, all cartridge fuses which are accessible to other than qualified persons and all fuses and thermal cutouts on circuits over 150 volts to ground shall be provided with disconnecting means.  This disconnecting means shall be installed so that the fuse or thermal cutout can be disconnected from its supply without disrupting service to equipment and circuits unrelated to those protected by the overcurrent device.

Location in or on premises. Overcurrent devices shall be readily accessible to each employee or authorized building management personnel.  These overcurrent devices may not be located where they will be exposed to physical damage nor in the vicinity of easily ignitable material.

Arcing or suddenly moving parts. Fuses and circuit breakers shall be so located or shielded that employees will not be burned or otherwise injured by their operation.

Reference: 29 CFR 1910.304, Wiring Design and Protection, July 1, 2006

The following requirements apply to overcurrent protection over 600 volts.

Feeder and branch-circuit conductors shall have overcurrent protection in each ungrounded conductor located at the point where the conductor receives its supply or at an alternative location in the circuit when designed under engineering supervision that includes but is not limited to consideration of the appropriate fault studies and time-current coordination analysis of the protective devices and the conductor damage curves.

Circuit breakers used for overcurrent protection of 3-phase circuits shall have a minimum of three overcurrent relay elements operated from three current transformers.  The separate overcurrent relay elements shall be permitted to be part of a single electronic protective relay unit.  On 3-phase, 3-wire circuits, an overcurrent relay in the residual circuit of the current transformers shall be permitted to replace one of the phase relays.  An overcurrent relay element, operated from a current transformer that links all phases of a 3-phase, 3-wire circuit, shall be permitted to replace the residual relay element and one of the phase-conductor current transformers.  Where the neutral is not regrounded on the load side of the circuit, the current transformer shall be permitted to link all 3-phase conductors and the grounded circuit conductor (neutral).

Reference: NFPA 70E, Standard for Safety in the Workplace, 2004

### Grounding and Bonding

The following paragraphs cover grounding requirements for systems, circuits, and equipment.

The path to ground from circuits, equipment, and enclosures shall be permanent, continuous, and effective.  Bonding shall be provided where necessary to ensure electrical continuity and the capacity to conduct safely any fault current likely to be imposed.

The following systems that supply premises wiring should be grounded:

The neutral conductor of all 3iwire, DC systems supplying premises wiring shall be grounded.

A 2-wire, DC system supplying premises wiring and operating at greater than 50 volts but not greater than 300 volts shall be grounded.

AC circuits of less than 50 volts shall be grounded under any of the following conditions:

Where supplied by transformers, if the transformer supply systems exceed 150 volts to ground

Where supplied by transformers, if the transformer supply system is ungrounded

Where installed as overhead conductors outside of buildings

AC systems of 50 volts to 1000 volts that supply premises wiring systems shall be grounded under any of the following conditions:

Where the system can be grounded so that the maximum voltage to ground on the ungrounded conductors does not exceed 150 volts

Where the system is rated 3-phase, 4-wire, wye connected in which the neutral is used as a circuit conductor

Where the system is rated 3-phase, 4-wire, delta connected in which the midpoint of one phase winding is used as a circuit conductor

The following AC systems of 50 volts to 1000 volts shall be permitted to be grounded, but shall not be required to be grounded:

Electric systems used exclusively to supply industrial electric furnaces for melting, refining, and tempering

Separately derived systems used exclusively for rectifiers that supply only adjustable speed industrial drives

Separately derived systems supplied by transformers that have a primary voltage rating less than 1000 volts, provided that all of the following conditions are met:

- The system is used exclusively for control circuits.

- The conditions of maintenance and supervision ensure that only qualified persons service the installation.

- Continuity of control power is required.

- Ground detectors are installed on the control system

Where high-impedance grounded neutral systems in which a grounding impedance, usually a resistor, limits the ground-vault current to a low value shall be permitted for 3-phase AC systems of 480 volts to 1000 volts where all of the following conditions are met.

- The conditions of maintenance and supervision ensure that only qualified persons service the installation.

- Continuity of control power is required.

- Ground detectors are installed on the control system

- Line-to-neutral loads are not served

AC systems of 1 kV and over supplying mobile or portable equipment shall be grounded.  Where supplying other than mobile or portable equipment, such systems shall be permitted to be grounded.

The frame of a portable generator shall not be required to be grounded and shall be permitted to serve as the grounding electrode for a system supplied by the generator under the following conditions:

- The generator supplies only equipment mounted on the generator, cord-and-plug connected equipment through receptacles mounted on the generator, or both.

- The non-current-carrying metal parts of equipment and the equipment grounding conductor terminals of the receptacles are bonded to the generator frame.

The frame of a vehicle shall be permitted to serve as the grounding electrode for a system supplied by a generator located on the vehicle under the following conditions:

- The frame of the generator is bonded to the vehicle frame.

- The generator supplies only equipment located on the vehicle or cord-and-plug-connected equipment through receptacles mounted on the vehicle, or both equipment located on the vehicle and cord-and-plug-connected equipment through receptacles mounted on the vehicle or on the generator.

- The non-current-carrying metal parts of equipment and the equipment grounding conductor terminals of the receptacles are bonded to the generator frame.

- The system complies with all other provisions of NFPA-70E, article 410.10.

A system conductor that is required to be grounded shall be bonded to the generator frame where the generator is a component of a separately derived system.

Reference: NFPA-70E, Standard for Safety in the Workplace, 2004

## Become familiar with the requirements for the Installation of Lightning Protection Systems (NFPA 780, UL 96 Lightning Protection Components, and UL 96A Installation requirements for Lightning Protection Systems).

## Demonstrate a working-level knowledge of electrical diagrams, including:

One-line diagrams

Schematics

Construction drawings

As-built drawings

Wiring diagrams

- Using a schematic, identify an electrical component by its symbology.

Using a logic diagram for a control circuit, identify and describe the effects of an action taken.

Using a one-line diagram, identify power sources and loads.

Using a one-line diagram or schematic diagram, analyze the effects of a component failure in a system.

Using a construction drawing, identify the emergency power supplies.

Discuss the origin and purpose of "as-built" drawings.

Elements “a” through “f” are performance-based competencies.  The qualifying official will evaluate the completion of these competencies.

## Become knowledgeable of the Configuration Management process as applied to electrical documentation, e.g., documenting, controlling, revising, and issuance of electrical drawings.  Also observed how drawings are updated and issued “as built.” (DOE STD 1073, Configuration Management, and DOE O 414.1C Quality)

- Discuss the change control process described in DOE STD 1073.

Contractors must establish and use a formal change control process as part of the configuration management process.  The objective of change control is to maintain consistency among design requirements, the physical configuration, and the related facility documentation, even as changes are made.  The change control process is used to ensure changes are properly reviewed and coordinated across the various organizations and personnel responsible for activities and programs at the nuclear facility.

Through the change control process, contractors must ensure that:

changes are identified and assessed through the change control process,

changes receive appropriate technical and management review to evaluate the consequences of the change,

changes are approved or disapproved,

waivers and deviations are properly evaluated and approved or denied and the technical basis for the approval or the denial is documented,

approved changes are adequately and fully implemented or the effects of the partial implementation are evaluated and accepted,

implemented changes are properly assessed to ensure the results of the changes agree with the expectations, and

documents are revised consistent with the changes and the revised documents are provided to the users.

Reference: DOE-STD-1073-2003, Configuration Management, October 2003

Describe the purpose and objectives of the Operational Configuration Management Program.

The basic objectives and general principles of configuration management are the same for all activities.  The objectives of configuration management are to

establish consistency among design requirements, physical configuration, and documentation, including analysis, drawings, and procedures for the activity;

maintain this consistency throughout the life of the facility or activity, particularly as changes are being made.

Reference: DOE-STD-1073-2003, Configuration Management, October 2003

Discuss the following elements of the Configuration Management Program:

Design requirements

Document control

Change control

Assessments

Design reconstitution adjunct

Material condition and aging adjunct

### Design Requirements

The objective of the design requirements element of configuration management is to document the design requirements.  The design requirements define the constraints and objectives placed on the physical and functional configuration.  The design requirements to be controlled under configuration management will envelop the safety basis and, typically, the authorization basis.  Consequently, proper application of the configuration management process should facilitate the contractor’s efforts to maintain the safety basis and the authorization basis.  Contractors must establish procedures and controls to assess new facilities and activities, and modifications to facilities and activities, to identify and document design requirements.

### Document Control

Document control ensures that only the most recently approved versions of documents are used in the process of operating, maintaining, and modifying the nuclear facility.

Document control helps ensure that

important facility documents are properly stored;

revisions to documents are controlled, tracked, and completed in a timely manner;

revised documents are formally distributed to designated users;

information concerning pending revisions is made available.

As controlled documents are updated to reflect changes to the requirements and/or physical installation, the contractor must ensure that

each updated document is uniquely identified and includes a revision number and date;

each outdated document is replaced by the latest revision.

### Change Control

Change control is a process that ensures all changes are properly identified, reviewed, approved, implemented, tested, and documented.

The change control package is the documentation that accompanies a change to a facility, activity, or operation from the planning and initiation through completion of the implementation and testing.  The change control package documents the following, as applicable:

The description of the proposed change sufficient to support technical and management reviews prior to approval

The name and organization of the requester

The description of the potentially affected systems, structures, and components

The reason for the proposed change and any known schedule issues

A list of the alternative solutions considered and the results

The date by which the decision about the change needs to be completed to facilitate timely implementation or to allow implementation to occur concurrent with other activities, such as a planned maintenance shutdown

Constraints

Any other information needed to review, track, approve, or process the proposed change

It also includes related information such as

change request

design package

installation package

post-modification testing documentation

### Assessments

The quality assurance criteria of 10 CFR 830, subpart A, require DOE contractors for nuclear facilities, including activities and operations, to assess management processes and measure the adequacy of work performance.  Furthermore, the assessment criteria require that the persons performing the assessments

have sufficient authority and freedom from line management

are qualified to perform the assessments

The objective of assessing configuration management is to detect, document, determine the cause of, and initiate correction of inconsistencies among design requirements, documentation, and physical configuration.  Properly performed assessments should help identify inconsistencies between these areas, evaluate the root causes for these problems, and prescribe improvements to avoid similar inconsistencies in the future.

The five specific types of assessments are

configuration assessments, which are performed to ensure configuration is managed throughout the construction process for new construction or major modifications;

physical configuration assessments, which are conducted to evaluate the consistency between the physical configuration and the facility documentation;

design assessments, which are done to ensure that design documents have been updated to reflect changes and accurately reflect the physical configuration of the nuclear facility;

post-construction, -modification, or -installation inspections and tests, which are performed either after construction, modification, or installation to verify operation is as expected;

periodic performance assessments, which are conducted to verify that systems and components continue to meet design and performance requirements in their current configurations.

### Design Reconstitution Adjunct

Design reconstitution adjunct is an adjunct program to the configuration management process that accomplishes the one-time effort of identifying, retrieving, extracting, evaluating, verifying, validating, and regenerating missing critical design requirements and basis.  Design reconstitution encompasses the following functions

Developing associated program plans and procedures

Identifying and retrieving design information from identified source documents

Evaluating, verifying, and validating the design information

Resolving discrepancies

Regenerating missing critical design information

Preparing and issuing design information summaries

### Material Condition and Aging Adjunct

The authors of this standard have deleted the discussion on material condition and aging because it is a subject that is more appropriately covered in DOE directives on maintenance.

Reference: DOE-STD-1073-2003, Configuration Management, October 2003

Discuss the purpose, concepts, and general process for applying the graded approach to operational configuration management.

Using the guidance in DOE-STD-1073-2003, discuss the system engineer concept as it applies to oversight of safety systems.  Specifically address the areas of configuration management, assessment of system status and performance, and technical support for operation and maintenance activities or for documented safety analysis (DSA) reviews.

Using DOE O 414.1C, discuss how the pedigree of electrical equipment should be maintained when supporting a nuclear related activity, and/or performing a safety function.

DOE defines graded approach as a process of ensuring that the level of analysis, documentation, and actions used to comply with a requirement are commensurate with:

the relative importance to safety, safeguards, and security;

the magnitude of any hazard involved;

the life cycle stage of a facility;

the programmatic mission of a facility;

the particular circumstances of a facility;

the relative importance of radiological and nonradiological hazards; and

any other relative hazard.

The main purpose of using a graded approach is to determine and apply a level of resources that is appropriate when implementing a program.  The goal is to apply the highest level of resources to the most important equipment in the most important facilities and to avoid such expenditures where they are not warranted.  For a highly hazardous facility such as a large nuclear reactor, which could potentially have serious off-site personnel safety consequences, a significant investment of resources is appropriate for the systems that prevent, detect, or mitigate such consequences.  At the other extreme, for a low-hazard facility—a glovebox operation, for example—where the greatest hazard is localized (i.e., offsite persons and workers at other collocated facilities are not affected), the same investment of resources may not be necessary.  The grading system should take into account both facility grades and SSC grades in determining the appropriate level of resources to be applied.

In applying the graded approach to the configuration management process, the following factors should be considered:

| Relative Importance Factors | Situational/Circumstantial Considerations |
| --- | --- |
| Facility grade | Facility type and technical characteristics |
| SSC grades | Facility remaining lifetime |
|  | Facility operational status and life cycle phase |
|  | Programmatic and technical issues |
|  | Existing programs and procedures |

The first column lists factors that can be used to grade based upon relative importance.  That is, one item can be identified as more important than another and therefore can be assigned a higher priority.  The second column lists special situations and circumstances that are independent of relative importance.

Reference: DOE-STD-1073-2003, Configuration Management, October 2003

The bulleted portion of this competency is performance-based.  The qualifying official will evaluate the completion of this portion of the competency.

## Become familiar with battery installations, maintenance, testing, and replacement as described in NFPA 70E, Chapter 3, IEEE Std-450, and IEEE-C2 National Electrical Safety Code (NESC) to include:

Connections and capacities;

DC systems grounding and ground-fault detection;

DC circuits protection and alarms.

### Connections and Capacities

Batteries usually consist of a number of identical cells connected in series.  The voltage of a series connection of cells is the voltage of a single cell multiplied by the number of cells.  If cells of sufficiently large capacity are available, then two or more series-connected strings of equal numbers of cells could be connected in parallel to achieve the desired rated capacity.  The rated capacity of such a battery is the sum of the capacities of a group of cells comprising a single cell from each of the parallel branches.

Cells of unequal capacity should not be connected in series.  Parallel connections of batteries should be limited to 4 strings.  Parallel connections of batteries are not recommended for constant current-charging applications.  Cells connect in series have high voltages that could produce a shock hazard.

### DC Systems Grounding and Ground Fault Detection

One of the four types of available DC grounding systems should be used

Type 1. The ungrounded DC system in which neither pole of the battery is connected to ground.

Type 2. The solidly grounded DC system where either the positive or negative pole of the battery is connected directly to ground.

Type 3. The resistance grounded DC system, where the battery is connected to ground through a resistance.  The resistance is used to permit operations of a current relay that initiates an alarm.

Type 4. A tapped solid ground, either at the center point or at another point tot suit the load system.

### DC Circuits Protection and Alarms

DC circuits should be protected according to the NEC.  Alarms should be provided for early warning of the following abnormal conditions of battery operation:

For vented batteries:

Overvoltage

Undervoltage

Overcurrent

Ground-fault

For valve regulated lead acid batteries all of the above plus overtemperature, as measured at the pilot cell.

Reference: NFPA-70E, Standard for Safety in the Workplace, 2004

## Become familiar with ventilation and battery room requirements as cited in NFPA 70E, Chapter 3, IEEE Std-450 and IEEE C2-National Electrical Safety Code (NESC) to include:

Ventilation requirements for different battery types;

Battery room restrictions, barriers, illumination, and enclosure requirements;

Battery protection requirements.

### Ventilation Requirements

Batteries should be located in rooms or enclosures with outside vents or in well-ventilated rooms, so arranged to prevent the escape of fumes, gases, or electrolyte spray into other areas.

Ventilation should be provided to prevent liberated hydrogen gas from exceeding 1 percent concentration.  Room ventilation should be adequate to ensure that pockets of trapped hydrogen gas do not occur, particularly at the ceiling, to prevent the accumulation of an explosive mixture.  Exhaust air shall not pass over electrical equipment unless the equipment is listed for the use.  Inlets shall be no higher than the tops of the battery cells and outlets at the highest level in the room.

### Battery Room Restrictions

The battery room should be accessible only to authorized personnel and should be locked when unoccupied.  The battery room and enclosure doors should open outward.  The doors should be equipped with quick-release, quick-opening hardware.  The battery room should be located so that access to the batteries is unobstructed.  DC switching equipment, rotating machinery other than exhaust fans, and other equipment not directly part of the battery and charging facilities should be external to the battery room.  Alternatively, DC switching equipment should be separated from the battery by a partition of a height no less than 6 ft 6 in and of sufficient length to prevent accident contact with live surfaces.  Foreign piping should not pass through a battery room.  Passageways should be of sufficient width to allow the replacement of all battery room equipment.  Emergency exits should be provided as required.  Access and entrance to working space about the battery should be provided as required by NFPA-70E, article 400.15.

### Battery Protection Requirements

The following are general requirements for battery protection.

When the battery capacity exceeds 100 ampere-hours or where the nominal battery voltage exceeds 50 volts, suitable warning notices indicating the battery voltage and the prospective short-circuit current of the installation should be displayed.

Each output conductor should be individually protected by a fuse or circuit breaker positioned as close as practicable to the battery terminals.

Protective equipment should not be located in the battery compartment of the enclosure.

Switching and control equipment should comply with NEC and should be listed for the application.

For an ungrounded battery of nominal voltage that exceeds 120 volts, a ground-fault detector should be provided to initiate a ground-fault alarm.

The battery installation should have an isolating switch installed as close as practicable to the main terminals of the battery.  Where a busway system is installed, the isolating switch may be incorporated into the end of the busway.

Where the battery section exceeds 1120 volts, the installation should include an isolating switch, plugs, or links, as required, to isolate sections of the battery, or part of the battery for maintenance.

The following signs should be posted in appropriate locations:

Electrical hazard warning signs indicating the shock hazard due to the battery voltage and the arc hazard due to the prospective short-circuit current

Chemical hazard warning signs indicating the danger of hydrogen explosion from open flame and smoking and the danger of chemical burns from the electrolyte

Notice for personnel to use and wear protective equipment and apparel

Notice prohibiting access to unauthorized personnel

Reference: NFPA-70E, Standard for Safety in the Workplace, 2004

VI. ELECTRICAL VITAL SAFETY SYSTEMS (VSS)

(Applies only to candidates who are assigned an electrical VSS.  Recommend applying, as appropriate, to candidates who are assigned an electrical system that performs a defense in depth/important to safety function and/or supports a nuclear related activity.  Each competency statement is a MPA, provided that they are applicable to the candidate’s assigned electrical duties.)

## Mandatory Performance Activity: Demonstrate a familiarity-level of knowledge of 10 CFR 830 (Nuclear Safety Management), and DOE O 414.1C that relate to electrical safety programs, processes, and systems, to include:

Knowledge of site VSS interfaces for electrical, software, and instrument and control systems;

The basic purpose of the USQ process;

General purpose and constitution of the DSA;

Purpose and content of Technical Safety Requirements (TSR) documentation.

- Discuss the reasons for performing an Unreviewed Safety Question determination.

A proposed change or test involves a USQ if

the probability of the occurrence or the consequences of an accident or the malfunction of equipment important to safety previously evaluated in the documented safety analysis could be increased,

the possibility of an accident or malfunction of a different type than any evaluated previously in the documented safety analysis could be created, or

a margin of safety could be reduced.

Reference: DOE G 424.1-1A, Implementation Guide for Use in Addressing Unreviewed Safety Question Requirements, July 2006

- Describe the situations for which a safety evaluation is required to be performed.

A safety evaluation is the record that is required to document the review of a change.  This document records the scope of the evaluation and the logic for determining whether or not a USQ exists.

Reference: DOE G 424.1-1A, Implementation Guide for Use in Addressing Unreviewed Safety Question Requirements, July 2006

- Define the conditions for an Unreviewed Safety Question.

A proposed change or test involves a USQ if

the probability or consequences of an accident or malfunction of equipment important to safety could be increased;

the possibility of a different type of accident than previously evaluated in the DSA could be introduced;

margins of safety could be reduced.

Reference: DOE G 424.1-1A, Implementation Guide for Use in Addressing Unreviewed Safety Question Requirements, July 2006

- Describe the responsibilities of contractors authorized to operate defense nuclear facilities regarding the performance of safety evaluations.

Each facility should identify the methods by which facility changes can be made.  After these methods have been identified, each facility must determine what constitutes an acceptable means to make a change; that is, the contractor must clearly control the facility change process and must perform and document changes in accordance with approved procedures. Performing a modification under the guise of maintenance is not acceptable because the proper control processes to analyze the proposed change and document its outcome would probably be absent.  It is necessary to identify all means for performing a change because each one provides a direct input into the USQ process and must be integrated accordingly.

The USQ process is intended to be implemented along with a change control process that includes generalized steps for identifying and describing the temporary or permanent change, technical reviews of the change, management review and approval of the change, implementation of the change, and documenting the change.  As part of the technical reviews of a change, the contractor should perform the appropriate type of safety analysis to ascertain whether the change is indeed safe.  This is accomplished separately from the USQ process. The USQ process is used subsequently to determine if final approval of the change by the contractor is sufficient or if DOE approval must be obtained.

Reference: DOE G 424.1-1A, Implementation Guide for Use in Addressing Unreviewed Safety Question Requirements, July 2006

- Describe the actions to be taken by a contractor upon identifying information that indicates a potential inadequacy of a previous safety analyses or, a possible reduction in the margin of safety, as defined in the TSRs.

Because an inadequacy in the safety analysis has the potential to call into question information relied on for authorization of operations, DOE requires the contractor to

take appropriate action to place or maintain the facility in a safe condition;

expeditiously notify DOE when the information is discovered;

perform a USQ determination and submit the results promptly;

complete an evaluation of the safety of the situation and submit it to DOE before removing any operational restrictions implemented to compensate for the analytical discrepancy.

Reference: DOE G 423.1-1, Implementation Guide For Use in Developing Technical Safety Requirements, October 2001

- Discuss the purpose of the TSRs.

TSRs define the performance requirements of SSCs and identify the safety management programs used by personnel to ensure safety.  TSRs are aimed at confirming the ability of the SSCs and personnel to perform their intended safety functions under normal, abnormal, and accident conditions.  These requirements are identified through hazard analysis of the activities to be performed and identification of the potential sources of safety issues.  Safety analysis to identify and analyze a set of bounding accidents that take into account all potential causes of releases of radioactivity also contribute to the development of TSRs.

Reference: DOE G 423.1-1, Implementation Guide For Use in Developing Technical Safety Requirements, October 2001

- Describe the responsibilities of contractors authorized to operate defense nuclear facilities regarding the TSR.

Section 10 CFR 830.205, Nuclear Safety Management, requires DOE contractors responsible for hazard category 1, 2, and 3 DOE nuclear facilities to develop TSRs.  These TSRs identify the limitations to each DOE-owned, contractor-operated nuclear facility based on the DSA and any additional safety requirements established for the facility.  The TSR rule requires contractors to prepare and submit TSRs for DOE approval.

Reference: DOE G 423.1-1, Implementation Guide For Use in Developing Technical Safety Requirements, October 2001

- Define the following terms and discuss the purpose of each:

Safety limit

Limiting control settings

Limiting conditions for operation

Surveillance requirements

### Safety Limit

SLs are those bounds within which process variables must be maintained for adequate control of the operation and that must not be exceeded in order to protect the integrity of the physical system that is designed to guard against uncontrolled release or radioactivity.  If any SL is exceeded, corrective action must be taken as stated in the technical specification or the affected part of the process, or the entire process if required, must be shut down, unless this action would further reduce the margin of safety.

### Limiting Control Settings

Limiting control settings are settings for automatic alarm or protective devices related to those variables having significant safety functions.  Where an LCS is specified for a variable on which an SL has been placed, the setting must be so chosen that protective action, either automatic or manual, will correct the abnormal situation before an SL is exceeded.

### Limiting Conditions for Operation

Limiting conditions for operation are the lowest functional capability or performance levels of equipment required for safe operation of the facility.

### Surveillance Requirements

Surveillance requirements are requirements relating to test, calibration, or inspection to assure that the necessary quality of systems and components is maintained, that facility operation will be within SLs, and that the LCO will be met.

Reference: DOE G 423.1-1, Implementation Guide For Use in Developing Technical Safety Requirements, October 2001

Describe the general content of each of the following sections of the TSRs:

Use and application

Safety limits

Operating limits

Surveillance requirements

Administrative controls

Basis

Design features

### Use and Application

This section should contain basic information and instructions for using and applying the TSR.

### Safety Limits

SLs should describe as precisely as possible the process variables or the parameters being limited, and should state the limit in measurable units (pressure, temperature, flow, etc.).  In general, SLs should be monitored continuously.

SLs should be based on, and specified in terms of, three basic rules.

Exceeding an SL is a TSR violation for each applicable mode.  Upon exceeding an SL, the following steps should be taken:

The affected parameter must be immediately brought within the SL.

Place the facility in the most stable, safe condition attainable, including shutdown if appropriate.

Reactors are required to shut down immediately (e.g., scram).  At nonreactor nuclear facilities, the TSR should specify actions to be taken that place the involved process in the most stable, safe condition attainable, including shutdown if appropriate.

All other action requirements should be met.

Each SL should have a mode applicability statement.  This statement should consist of a simple list of modes or other conditions for which the SL is applicable.

Action statements should describe the actions to be taken in the event that the SL is not met.  These actions should first place the facility in a safe, stable condition, or should verify that the facility already is safe and stable and will remain so.  Secondly, an action statement should establish the steps and time limits to correct the out-of-specification condition.  The actions should bring the affected parameter immediately within the SL and should affect a shutdown of the facility, within a justified facility-specific time frame, normally less than an hour.  Other actions required after exceeding an SL, including reporting requirements and an evaluation of possible damage caused by exceeding the SL, may be included in the action statement.  A statement prohibiting restart, before DOE approval, of the facility after an SL violation should be included in the action statement of each SL, in section 5 of the TSR, or in both.

### Operating Limits

Operating limits are those limits that are required to ensure the safe operation of a nuclear facility.  The operating limits section may include subsections on limiting control settings and limiting conditions for operation.

### Surveillance Requirements

This section includes requirements relating to test, calibration, or inspection to assure that the necessary operability and quality of safety structures, systems, and components is maintained; that facility operation is within safety limits; and that limiting control settings and limiting conditions for operation are met.

### Administrative Controls

This section should impose administrative requirements necessary to control operation of the facility such that it meets the TSR.  The following topics should be included:

Contractor responsibility.  The facility or plant manager is responsible for overall operation of the nuclear facility and should delegate in writing the succession to this responsibility during his or her absence.

Contractor organization.  On-site and off-site organizations should be described for facility operation and contractor management.

Procedures.  Operations procedures should provide sufficient direction to ensure that the facility is operated within its design basis and supports safe operation of the facility.

Programs.  Programs developed to ensure the safe operation of the facility should be discussed here and thereby committed to by reference.

Minimum operations shift complement.  This section of the ACs should include the maximum daily working hours and maximum number of consecutive days on duty.

Operating support.  A list of facility support personnel that includes name, title, work and home telephone numbers.

Facility staff qualifications and training.  Minimum qualifications for members of the facility staff in positions affecting safety should conform to the requirements of DOE Order 5480.20A, Personnel Selection, Qualification, and Training Requirements for DOE Nuclear Facilities, or a successor document, and should be provided in the AC section.

Record keeping.  Records need to be kept of all information supporting the implementation of the TSR, including operational logs of modes changes, entering actions, surveillances, deviations, procedures, programs, meetings, recommendations, etc.

Reviews and audits.  Describe the methods established to conduct independent reviews and audits.

Deviations from technical safety requirements.  State the actions and reporting to be taken for deviations from TSRs.

### Basis

The TSR bases appendix provides summary statements of the reasons for the selection of each specific SL, OL, and SR.  The bases show how the numerical values, conditions, surveillances, and action statements fulfill the purpose derived from the safety documentation.  Included in the bases should also be a description of the safety functions that each safety system provides and identification of what is included in each safety system.  The level of detail in the description should be sufficient for the operations staff to confirm that the system is operable.  This description is provided so that the operations staff knows exactly what must be operable to consider the entire safety system operable.  The bases appendix references the basis for specific parts of the TSR given in the DSA and other safety documentation.

### Design Features

The design features section describes those design features that, if altered or modified, would have a significant effect on safe operation.  The important attributes of the passive design features that are taken credit for in the accident analyses should be described completely. These design features are normally passive characteristics of the facility not subject to change by operations personnel, e.g., shielding, structural walls, relative locations of major components, installed poisons, or special materials.  Active safety features are normally described in the DSA and are the subject of the various TSRs so they are not normally described in the design features section.  All changes or modifications that impact the safety basis of the facility are subject to the USQ process.  The design features section captures those permanently built-in features critical to safety that do not require, or infrequently require, maintenance or surveillance.

Reference: DOE G 423.1-1, Implementation Guide For Use in Developing Technical Safety Requirements, October 2001

Discuss the basic purposes and objectives of a DSA.

A DSA is the process whereby facility hazards are identified, controls to prevent and mitigate potential accidents involving those hazards are proposed, and commitments are made for design, construction, operation, and disposition to assure adequate safety at DOE nuclear facilities.

Reference: Implementation Guide for Use in Developing Documented Safety Analyses To Meet Subpart B of 10 CFR 830, October 2001

Describe the responsibilities of contractors authorized to operate DOE nuclear facilities regarding the development and maintenance of a DSA.

The contractor responsible for a hazard category 1, 2, or 3 DOE nuclear facility must obtain approval from DOE for the methodology used to prepare the DSA for the facility unless the contractor uses a methodology set forth in table 2 of appendix A to 10 CFR 830.204, Documented Safety Analysis.

The DSA for a hazard category 1, 2, or 3 DOE nuclear facility must, as appropriate for the complexities and hazards associated with the facility

describe the facility (including the design of SSCs and the work to be performed);

provide a systematic identification of both natural and man-made hazards associated with the facility;

evaluate normal, abnormal, and accident conditions, including consideration of natural and man-made external events, identification of energy sources or processes that might contribute to the generation or uncontrolled release of radioactive and other hazardous materials, and consideration of the need for analysis of accidents which may be beyond the design basis of the facility;

derive the hazard controls necessary to ensure adequate protection of workers, the public, and the environment, demonstrate the adequacy of these controls to eliminate, limit, or mitigate identified hazards, define the process for maintaining the hazard controls current at all times, and control their use;

define the characteristics of the safety management programs necessary to ensure the safe operation of the facility, including where applicable, quality assurance, procedures, maintenance, personnel training, conduct of operations, emergency preparedness, fire protection, waste management, and radiation protection;

define a criticality safety program that

ensures that operations with fissionable material remain sub-critical under all normal and credible abnormal conditions,

identifies applicable nuclear criticality safety standards,

describes how the program meets applicable nuclear criticality safety standards.

Reference: Implementation Guide for Use in Developing Documented Safety Analyses To Meet Subpart B of 10 CFR 830, October 2001

Define the following terms and discuss the purpose of each:

Safety basis

Design features

Safety evaluation report

### Safety Basis

Safety basis means the combination of information relating to the control of hazards at a nuclear facility, including design, engineering analyses, and administrative controls upon which DOE depends for its conclusion that activities at the facility can be conducted safely.

### Design Features

Design features means the set of requirements that bound the design of SSCs within the facility.  These design requirements include consideration of safety, plant availability, efficiency, reliability, and maintainability.  Some aspects of the design features are important to safety, although others are not.

### Safety Evaluation Report

The safety evaluation report is a management document that provides the approval authority, the basis for the extent and detail of the DSA review, and the basis for any conditions of DSA approval.

Reference: Implementation Guide for Use in Developing Documented Safety Analyses To Meet Subpart B of 10 CFR 830, October 2001

Describe the requirements for the scope and content of a DSA and discuss the general content of each of the required sections of a DSA.

Refer to DOE-STD-3009-94, Preparation Guide for U.S Department of Energy Nonreactor Nuclear Facility Documented Safety Analyses, at http://www.eh.doe.gov/techstds/standard/std3009/std3009_cn2.pdf, for information regarding this competency.

Discuss the uses that contractor management makes of a DSA.

Contractors, in the preparation of DSAs, identify how the generic safety requirements of the Department apply to the specific facility, and propose commitments under which the contractor undertakes to design, build, and operate the facility to be in conformance with the applicable statutes, federal rules, and DOE directives to ensure facility safety.  The Department reviews the DSA and decides whether to authorize the facility, or to approve the DSA if the facility is already authorized.  In authorizing the facility or approving its DSA, the Department may require modified or alternative commitments.  In this way, the Department and the contractor responsible for the facility or operation arrive at a common understanding of how the Department's safety rules, Orders, and policies apply in the context of the particular facility.  Facility operation is required to be in compliance with the resulting commitments in approved DSAs.

Reference: Implementation Guide for Use in Developing Documented Safety Analyses To Meet Subpart B of 10 CFR 830, October 2001

## Demonstrate a familiarity-level knowledge of all assigned electrical power vital safety systems, and how they are addressed during the design, construction and operation of nuclear facilities

- Mandatory Performance Activity: Walkdown electrical power vital safety systems and locate and identify major components, subsystems, and interfaces.

- Identify all Electrical Power Vital Safety Systems (site specific), and then discuss the functional classifications, safety functions, and functional requirements of these systems.

Elements “a” and “b” are performance-based competencies.  The qualifying official will evaluate the completion of these competencies.

- Discuss electrical power distribution with the regard to the following elements (IEEE Red Book or other sources can be used as a guide in developing the discussion):

Basic design considerations and electrical distribution design

Voltage considerations

Surge voltage protection techniques

System protective devices

Power factor and its effects in electrical distribution systems

Power switching, transformation, and motor-control apparatus

Cable system basics

Busway design

Refer to IEEE-STD-141-1976 (IEEE Red Book), Electrical Power Distribution, for information related to this competency.

Discuss protection and coordination with regard to the following elements (the IEEE Buff book or other sources can be used as a guide in developing the discussion:

Fault calculations

Short-circuit current calculations for single and three-phase circuits.

Instrument transformer basics

Protective relay selection and application

Fuses selection and application

Refer to IEEE-STD-242-1975 (IEEE Buff Book), Protection and Coordination, for information related to this competency.

Discuss electrical system grounding with regard to the following elements (the IEEE Green Book or other source can be used as a guide in developing the discussion):

Electrical system grounding fundamentals

Electrical equipment grounding fundamentals

Static and lightning grounding fundamentals

Refer to IEEE-STD-142-1982 (IEEE Green Book), Grounding, for information related to this competency.

Discuss emergency and standby power with regard to the following elements (the IEEE Orange Book or other source can be used as a guide in developing the discussion):

Emergency and standby power guidelines

Generator and electric utility system fundamentals

Stored energy system fundamentals

Protection device fundamentals

Refer to IEEE-STD-446-1987 (IEEE Orange Book), Emergency and Standby Power, for additional information regarding this competency.

## Demonstrate a working-level knowledge of the possible functional interfaces/relationships between all electrical VSS and instrument and control safety software analysis safety software, and design safety software.

- Identify how functional requirements and applicability of safety analysis and design computer codes are defined, documented, and controlled relative to modeling and data assumptions, design constraints, sizing and timing conditions and input/output parameters as described in DOE O 414.1C, Quality Assurance, and DOE G 414.1-4 Safety Software Guide.

Functional requirements are defined using the following process:

An outline of the target system is developed and presented to the stakeholders for the purpose of soliciting their needs.

A first cut of the system overview diagram is created based on the outline statement.  (Use case diagrams are useful for the purpose.)  As this diagram is a very rough image, it should evolve over time.

Interviews with major stakeholders are conducted to solicit their needs.

Collected needs are defined.

Major functional requirements are identified.

Actors are identified.

Overall risks are analyzed.

Major quality requirements for each quality characteristic, such as safety, reliability, and usability are identified.  A quality model should be used for this purpose.

Required constraints and conditions, including total budget, delivery date, hardware and communication network environment, and available human resources are identified.

The system is refined into sub-systems, and the outline statement is re-defined.  The system overview diagram and project description are refined based on the defined sub-systems.

Reference: A Taxonomy of Safety-Related Requirements, which can be found at http://www.sei.cmu.edu/community/rhas-workshop/firesmith.pdf.

Review a development project for safety analysis or design software.  Explain how the problem being addressed by the software was translated into functional requirements, how the requirements were established and controlled, and how the code was reconciled with the original problem.

This is a performance-based competency.  The qualifying official will evaluate the completion of this competency.

Identify how system-level requirements are established and then assigned to hardware, software, and human components of a digital instrumentation and control system.

Generic safety requirements are established as a priority and placed into the system specification and/or overall project design specifications.  From there, they are flowed into lower-level unit and module specifications.

Other safety requirements, derived from bottom-up analysis, are flowed up from subsystems and components to the system-level requirements.  These new system-level requirements are then flowed down across all affected subsystems.  During the system requirements phase, subsystems and components may not be well defined.  In this case, bottom-up analysis might not be possible until the architectural design phase or even later.

The allocation of the system requirements to software, hardware, and other system components (e.g., humans) may be performed by a group external to the software engineering group (e.g., the system engineering group), and the software engineering group may have no direct control of this allocation.  Within the constraints of the project, the software engineering group takes appropriate steps to ensure that the system requirements allocated to software, which they are responsible for addressing, are documented and controlled.

To achieve this control, the software engineering group reviews the initial and revised system requirements allocated to software to resolve issues before they are incorporated into the software project.  Whenever the system requirements allocated to software are changed, the affected software plans, work products, and activities are adjusted to remain consistent with the updated requirements.

Reference: Requirements Management, http://www2.umassd.edu/swpi/sei/tr25f/tr25_l2a.html

Identify the typical requirements that define functional interfaces between safety software components and the system-level design, as described in DOE O 414.1C, Quality Assurance, and DOE G 414.1-4 Safety Software Guide.

Software requirement specification (SRS) is a specification for a particular software product, program, or set of programs that performs certain functions in a specific environment.  The SRS may be written by one or more representatives of the supplier, one or more representatives of the customer, or by both.  The basic issues that the SRS writer(s) shall address are the following:

Functionality.  What is the software supposed to do?

External interfaces.  How does the software interact with people, the system’s hardware, other hardware, and other software?

Performance.  What is the speed, availability, response time, recovery time of various software functions, etc.?

Attributes.  What are the portability, correctness, maintainability, security, etc., considerations?

Design constraints imposed on an implementation.  Are there any required standards in effect, e.g., implementation language, policies for database integrity, resource limits, operating environment(s)?

It is important to consider the part that the SRS plays in the total project plan.  The software may contain essentially all the functionality of the project or it may be part of a larger system.  In the latter case typically there will be an SRS that will state the interfaces between the system and its software portion, and will place external performance and functionality requirements upon the software portion.  In such cases, the SRS should agree with and expand upon these system requirements.

Reference: IEEE STD- 830-1998, IEEE Recommended Practice for Software Requirements Specifications.

Identify the specific records that must be maintained and the requirements for maintaining these records to document the development of safety system software.

Section 2.3.1.1 of IEEE STD 828-1998, Standard for Software Configuration Management Plans, requires, at a minimum, that all configuration items that are to be delivered be listed in the software configuration management plan.  This fulfills the intent of criterion VIII, Identification and Control of Materials, Parts, and Components, with regard to safety system software if all software deliverables are identified and controlled as configuration items. Criterion III, Design Control, requires measures for design documentation, identification and control of design interfaces, and control of design changes.  Criterion VI, Document Control, requires that all documents that prescribe activities affecting quality, such as instructions, procedures, and drawings, be subject to controls that ensure that documents, including changes, are reviewed for adequacy and approved for release by authorized personnel.  Criterion XVII, Quality Assurance Records, requires in part that sufficient records be maintained so that data that is closely associated with the qualification of personnel, procedures, and equipment will be identifiable and retrievable.  This regulatory guide applies to all aspects of the software life cycle within the system life cycle context.  Therefore, for safety system software, configuration items or controlled documents should include the following:

Software requirements, designs, and code

Support software used in development (exact versions)

Libraries of software components essential to safety

Software plans that could affect quality

Test software requirements, designs, or code used in testing

Test results used to qualify software

Analyses and results used to qualify software

Software documentation

Databases and software configuration data

Commercial software items that are safety system software

Software change documentation

Items that could change because of design changes, review, or audit should be configuration items subject to formal change control.  Other items that may not change but are necessary to ensure correct software production, such as compilers, should also be configuration items, thereby ensuring that all factors contributing to the executable software are understood.  This also is useful in areas such as maintenance, future software development, and tracing the impact of reported bugs.  Items that are retained for historical or statistical purposes may be controlled documents.

Reference: IEEE STD- 830-1998, IEEE Recommended Practice for Software Requirements Specifications.

Review a development project for safety system software.  Explain how the functional interfaces between components and the system level design were established and controlled.

This is a performance-based competency.  The qualifying official will evaluate the completion of this competency.

## Document participation with the site contractor system engineer (SE) in a quarterly walkthrough, bi-annual status walkthrough or an assessment for all assigned Electrical VSSs.

This is a performance-based competency.  The qualifying official will evaluate the completion of this competency.

## Demonstrate a familiarity-level knowledge of functional classifications for safety systems and the design expectations associated with electrical systems that carry these functional classifications, as described in DOE O 420.1B, Facility Safety, and its associated guide DOE G 420.1-1.

- Discuss the purpose, scope, and application of DOE O 420.1B.  Include in this discussion, key terms, essential elements, and personnel responsibilities and authorities.

The purpose of this Order is to establish facility safety requirements for DOE, including NNSA, for

nuclear safety design

criticality safety

fire protection

NPH mitigation

system engineer program

Discuss the project management terminology for which definitions are provided in DOE O 420.1B.

Project management terminology is in DOE O 430.1B, Real Property Asset Management.  There are no project management definitions in DOE O420.1B as indicated in the functional area standard.

Reference: DOE O 430.1B, Real Property Asset Management, September 2003

- Discuss in detail the roles played by various management levels within the Department as they relate to the project management system.

Three themes regarding roles and responsibilities necessary to achieve defined project objectives include:

Strengthening line management accountability for successful project management results;

Defining the roles, responsibilities, authority, and accountability of the Federal Project Management Team relative to the contractor Project Management Team; and

Developing effective Integrated Project Teams to assist the Federal Project Director in planning, programming, budgeting, and successfully acquiring capital assets.

Line managers are responsible for successfully developing, executing, and managing projects within the approved Performance Baseline.  Delegation of authority from one line manager to a lower-level line manager must be documented and consistent with DOE delegation authorities and the qualifications of the lower-level line manager.  Although the authority and responsibility for decision-making may be delegated to a lower-level manager, the senior manager remains accountable for the decisions made by subordinate managers.

Key roles and responsibilities of line managers are described in the following sections:

Heads of Field Organizations

Direct initial project planning and execution roles for projects assigned by the Acquisition Executive.

Initiate definition of mission need based on input from sites, laboratories, and program offices.

Establish the integrated project team.

Oversee development of project definition, technical scope, and budget to support mission need.

Initiate development of the acquisition strategy before CD-1 (during the period preceding designation of the Federal Project Director).

Perform functions as Acquisition Executive when so delegated.

Develop project performance measures, and monitor and evaluate project performance throughout the project’s life cycle.

Allocate resources throughout the program.

Oversee the project line-management organization and ensure the line project teams have the necessary experience, expertise, and training in design engineering, safety and security analysis, construction, and testing.

Serve as the Federal Project Director until the Federal Project Director is appointed.

Ensures that safety is fully integrated into design and construction for high-risk, high-hazard, and hazard category 1, 2, and 3 nuclear facilities.

Acquisition Executives.

The following roles and responsibilities are for illustrative purposes, and each designated Acquisition Executive is guided by the specific limits of his/her delegated authority.

Approve Critical Decisions (CD-0 cannot be delegated below the Program Secretarial Officer level).

Appoint and Chair Acquisition Advisory Boards to provide advice and recommendations on key project decisions.

Approve the appointment of the Federal Project Director.

Designate the Design Authority at CD-1.

Monitor the effectiveness of Federal Project Directors and their support staff.

Approve project changes in compliance with change control levels identified in Project Execution Plans.

Conduct monthly and quarterly project performance reviews.

Ensure that safety is fully integrated into design and construction for high-risk, high-hazard, and hazard category 1, 2, and 3 nuclear facilities.

Federal Project Director.

Successful performance of DOE projects depends on professional and effective project management by the Federal Project Director.  The Federal Project Director is responsible and accountable to the Acquisition Executive/Program Secretarial Officer or delegated authority, as appropriate, for executing the project.

The Federal Project Director’s assigned project must meet cost, schedule, and performance targets unless circumstances beyond the control of the project director result in cost overruns and/or delays.  Federal Project Directors must demonstrate initiative in incorporating and managing an appropriate level of risk to ensure best value for the government.  In cases where significant cost overruns and/or delays occur, the Federal Project Director alerts senior management in a timely manner and takes appropriate steps to mitigate these cost overruns or delays.

Roles and responsibilities of the Federal Project Director’s team must be clearly defined relative to the contractor management team.  Further guidance is provided in DOE M 413.3-1.

Attains and maintains certification in concert with the requirements outlined in DOE O 361.1A before they are delegated authority to serve as a Federal Project Director.

Plans, implements, and completes a project using a Systems Engineering approach.

Initiates development and implementation of key project documentation (e.g., Project Execution Plan).

Defines project cost, schedule, performance, and scope baselines.

Is responsible for design, construction, environmental, safety, security, health, and quality efforts performed comply with the contract, public law, regulations, and Executive Orders.

Is responsible for timely, reliable, and accurate integration of contractor performance data into the project’s scheduling, accounting, and performance measurement systems.

Evaluates and verifies reported progress; makes projections of progress and identifies trends.

Serves as the single point of contact between Federal and contractor staff for all matters relating to a project and its performance.

Serves as the Contracting Officer’s Representative, as determined by the Contracting Officer.

Leads the Integrated Project Team and provides broad program guidance.  Delegates appropriate decision-making authority to the Integrated Project Team members.

Prepares and maintains the Integrated Project Team Charter and operating guidance with Integrated Project Team support.

Approves changes in compliance with the approved change control process documented in the Project Execution Plan.

Ensures that safety is fully integrated into design and construction for high-risk, high-hazard, and hazard category 1, 2, and 3 nuclear facilities.

Reference: DOE O 413.3A, Program and Project Management for the Acquisition of Capital Assets, July 2006

- Discuss the purpose of “critical decisions.”  Include in this discussion the responsible authorities for critical decisions.

The five critical decisions are major milestones approved by the Secretarial Acquisition Executive or Acquisition Executive that establish the mission need, recommended alternative, acquisition strategy, the performance baseline, and other essential elements required to ensure that the project meets applicable mission, design, security, and safety requirements.  Each critical decision marks an increase in commitment of resources by the Department and requires successful completion of the preceding phase or critical decision.  Collectively, the critical decisions affirm the following:

There is a need that cannot be met through other than material means;

The selected alternative and approach is the optimum solution;

Definitive scope, schedule, and cost baselines have been developed;

The project is ready for implementation; and

The project is ready for turnover or transition to operations.

Reference: DOE O 413.3A, Program and Project Management for the Acquisition of Capital Assets, July 2006

- Describe the process by which projects are designated.

Projects are designated as major system projects, other projects, or environmental restoration projects.

A major system (MS) project is any project or system of projects with a total project cost of $400M or greater or any other project so designated by the Office of the Secretary.  A project may be designated as an MS either solely by the Office of the Secretary or by the Deputy Secretary in response to recommendations from the appropriate PSO or head of a departmental office, which is endorsed by the appropriate Under Secretary.  The Office of Engineering and Construction Management maintains and periodically publishes a list of MS projects.

A project designated as an “other” project is any project with a total project cost less than $400M and not designated as an MS project, including line item projects, general plant projects, and capital equipment and information technology projects, whether funded by capital or operating funds.

Environmental restoration and facility disposition projects are driven by the regulatory requirements in the Comprehensive Environmental Response, Compensation, and Liability Act (CERCLA) or in the Conservation and Recovery Act (RCRA).  Therefore critical decisions for these projects are different from those of a traditional construction project.

Reference: DOE O 413.3A, Program and Project Management for the Acquisition of Capital Assets, July 2006

- Define the term “safety-class” and discuss the implications of an electrical system carrying this functional classification.

Safety-class refers to nuclear safety structures, systems, and components (SSCs) that are relied upon to protect the safety and health of the off-site public as identified by safety analyses.

Safety class electrical systems must be designed to preclude single point failure.

References: DOE HDBK-1188-2006, Glossary of Environment, Safety, the Health Terms, January 2006 and DOE O 420.1B, Facility Safety, December 2005

- Define the term “safety-significant” and discuss the implications of an electrical system carrying this functional classification.

Safety-significant refers to SSCs that are not designated as safety-class SSCs, but whose preventive or mitigative function is a major contributor to defense in depth (i.e., prevention of uncontrolled material release) and/or worker safety as determined from hazard analyses.

As a general rule of thumb, safety-significant SSC designations based on worker safety are limited to those SSCs whose failure is estimated to result in a prompt worker fatality or serious injuries or significant radiological or chemical exposures to workers.  The term, serious injuries, as used in this definition, refers to medical treatment for immediately life-threatening or permanently disabling injuries (e.g., loss of eye, loss of limb).

The general rule of thumb cited above is neither an evaluation guideline nor a quantitative criterion.  It represents a lower threshold of concern for which safety significant SSC designation may be warranted.  Estimates of worker consequences for the purpose of safety-significant SSC designation are not intended to require detailed analytical modeling.  Considerations should be based on engineering judgment of possible effects and the potential added value of safety-significant SSC designation.

Reference: DOE HDBK-1188-2006, Glossary of Environment, Safety, the Health Terms, January 2006

## Demonstrate a familiarity-level knowledge of electrical safety systems criteria for VSS (IEEE Stds: 308-2001, 323-2003, 379-2000, 384-1992, and 603-1998; and, DOE O 420.1B and DOE G 420.1-1.)

- Identify and describe the requirements for principal design criteria of electrical power systems supporting VSS (Class 1E power systems): Design Basis and Design Basis Events; Independence; the Equipment Qualification process for Class 1E power systems; Single-Failure Criterion; Requirements for connecting of non-Class 1E systems to Class 1E systems; Class 1E protection requirements.

#### Design Basis and Design Basis Events

Each holder of or an applicant for a license for a nuclear power plant, other than a nuclear power plant for which the certifications required under 10 CFR 50.82(a)(1) have been submitted, shall establish a program for qualifying electric equipment important to safety.  This includes equipment that is relied on to remain functional during and following design basis events to ensure the capability to prevent or mitigate the consequences of accidents that could result in potential offsite exposures.

Design basis events are defined as conditions of normal operation, including anticipated operational occurrences, design basis accidents, external events, and natural phenomena for which the plant must be designed to ensure that all electric equipment important to safety functions.

#### Independence

The onsite electric power supplies, including the batteries, and the onsite electric distribution system, shall have sufficient independence, redundancy, and testability to perform their safety functions assuming a single failure.

The protection system shall be designed to assure that the effects of natural phenomena, and of normal operating, maintenance, testing, and postulated accident conditions on redundant channels do not result in loss of the protection function, or shall be demonstrated to be acceptable on some other defined basis.  Design techniques, such as functional diversity or diversity in component design and principles of operation, shall be used to the extent practical to prevent loss of the protection function.

#### Equipment Qualification Process

See element “d” of this competency for a description of the equipment qualification process.

#### Single Failure

A single failure means an occurrence that results in the loss of capability of a component to perform its intended safety functions.  Multiple failures resulting from a single occurrence are considered to be a single failure.  Fluid and electric systems are considered to be designed against an assumed single failure if neither (1) a single failure of any active component (assuming passive components function properly) nor (2) a single failure of a passive component (assuming active components function properly), results in a loss of the capability of the system to perform its safety functions.

#### Requirements for Connecting Non-Class 1E systems to Class 1E systems

Non-Class 1E, non-division associated components must be electrically isolated from Class 1E systems by an acceptable Class 1E isolation device or have an adequate justification and analysis for Non-Class 1E isolation.

#### Class 1E Protection Requirements

Pursuant to the provisions of 10 CFR 50.34, an application for a construction permit must include the principal design criteria for a proposed facility.  The principal design criteria establish the necessary design, fabrication, construction, testing, and performance requirements for SSCs that are important to safety; that is, SSCs that provide reasonable assurance that the facility can be operated without undue risk to the health and safety of the public.  The following criteria apply to electric power systems.

Criterion 17--Electric power systems.  An onsite electric power system and an offsite electric power system shall be provided to permit functioning of SSCs important to safety.  The safety function for each system (assuming the other system is not functioning) shall be to provide sufficient capacity and capability to assure that (1) specified acceptable fuel design limits and design conditions of the reactor coolant pressure boundary are not exceeded as a result of anticipated operational occurrences and (2) the core is cooled and containment integrity and other vital functions are maintained in the event of postulated accidents.

Electric power from the transmission network to the onsite electric distribution system shall be supplied by two physically independent circuits (not necessarily on separate rights of way) designed and located so as to minimize to the extent practical the likelihood of their simultaneous failure under operating and postulated accident and environmental conditions.  A switchyard common to both circuits is acceptable.  Each of these circuits shall be designed to be available in sufficient time following a loss of all onsite AC power supplies and the other offsite electric power circuit, to assure that specified acceptable fuel design limits and design conditions of the reactor coolant pressure boundary are not exceeded.  One of these circuits shall be designed to be available within a few seconds following a loss-of-coolant accident to assure that core cooling, containment integrity, and other vital safety functions are maintained.

Provisions shall be included to minimize the probability of losing electric power from any of the remaining supplies as a result of, or coincident with, the loss of power generated by the nuclear power unit, the loss of power from the transmission network, or the loss of power from the onsite electric power supplies.

Criterion 18--Inspection and testing of electric power systems.  Electric power systems important to safety shall be designed to permit appropriate periodic inspection and testing of important areas and features, such as wiring, insulation, connections, and switchboards, to assess the continuity of the systems and the condition of their components.  The systems shall be designed with a capability to test periodically (1) the operability and functional performance of the components of the systems, such as onsite power sources, relays, switches, and buses, and (2) the operability of the systems as a whole and, under conditions as close to design as practical, the full operation sequence that brings the systems into operation, including operation of applicable portions of the protection system, and the transfer of power among the nuclear power unit, the offsite power system, and the onsite power system.

Reference: Nuclear Regulatory Commission, Regulatory Guide 1.32, Criteria for Power System for Nuclear Power Plants

- Identify and describe the requirements for supplementary design criteria of electrical power systems supporting VSS (Class 1E power systems): Class 1E power systems; AC power systems; DC power systems; Instrumentation and control power systems; Execute and Sense-and-Command features.

#### Class 1E Power Systems

The safety function of an electrical power system is to provide power to systems and components that require electrical power to perform their safety functions.  A safety-significant or safety-class electrical power system is defined as the system or component that provides actuation or motive force to safety equipment.  These systems consist of onsite AC/DC power supply systems and associated distribution systems and components (e.g., conduits, wiring, cable trays, etc.).

Safety-class electrical power must be designed against single-point failure in accordance with the criteria in section 5.1.1.2 of DOE G 420.1-1.  Redundancy requirements for electrical systems pertain to normal and alternative power sources and should be analyzed on a case-by-case basis.  For safety-significant systems, redundancy is not required if it can be shown that there is sufficient response time to provide an alternative source of electrical power.

Environmental capability of safety-class electrical equipment must be demonstrated by testing, analysis, and operating experience, or a combination of these methods in accordance with section 5.1.3 of DOE G 420.1-1.

For the commercial nuclear industry, a multitude of ANSI/IEEE Standards define the requirements for the manufacture, installation, and testing of reactor Safety Class 1E electrical systems and components.  The Safety Class 1E requirements may not be directly applicable to the safety-class category defined for nonreactor nuclear facilities.  These standards, however, contain useful and significant information that should be considered.  Table 5.5 in DOE G 420.1-1 lists a minimal set of national codes and standards that should be addressed for safety-significant and safety-class electrical systems, keeping in perspective the applicable use of ANSI/IEEE standards for Safety Class 1E components.  Table 5.6 presents a list of ANSI/IEEE standards that can be used for guidance in specific applications. Before using these standards, their applicability to the design(s) being considered should be reviewed.

#### Instrumentation and Control Power Systems

The safety functions of instrumentation, control, and alarm systems are to provide information on out-of-tolerance conditions/abnormal conditions; ensure the capability for manual or automatic actuation of safety systems and components; ensure safety systems have the means to achieve and maintain a fail-safe shutdown condition on demand under normal or abnormal conditions; and/or actuate alarms to reduce public or site-personnel risk (e.g., effluent monitoring components and systems).

The design of safety-class and safety-significant instrumentation and control systems must incorporate sufficient independence, redundancy, diversity, and separation to ensure that all safety-related functions associated with such equipment can be performed under postulated accident conditions as identified in the safety analysis.  Safety-significant components should be evaluated as to the need for redundancy on a case-by-case basis.  Under all circumstances, safety class instrumentation, controls, and alarms must be designed so that failure of non-safety equipment will not prevent the former from performing their safety functions.

Safety-significant and safety-class instrumentation, control, and alarm-system designs must ensure accessibility for inspection, maintenance, calibration, repair, or replacement.

Safety-class instrumentation, control, and alarm systems must provide the operators sufficient time, information, and control capabilities to perform the following safety functions:

#### Execute and Sense-and-Command Features

IEEE Std 603-1991 specifies the need to ensure acceptable response time for the instrumentation and control system in order to accomplish necessary safety functions.  Consideration of the sampling rate of plant variables is an important aspect of the design of a digital system when satisfying this criterion.

The non-safety system interactions with protection systems should be limited such that the requirements of 10 CFR 50, appendix A, GDC 24, Separation of Protection and Control System, are met.  Where the event of concern is a simple failure of a sensing channel shared between control and protection functions, acceptable approaches are

isolating the protection system from channel failure by providing additional redundancy.

isolating the control system from channel failure by using data validation techniques to select a valid control input.

designing the communications path to be a broadcast only from the protection system to the control system.

The inspections, tests, analyses, and acceptance criteria should require an analysis or demonstration that no single credible event, including all direct and consequential results of that event, can cause a non-safety system action that results in condition requiring protective action and can concurrently prevent the protective action in those sense and command feature channels designated to provide principal protection against the condition.

Reference: DOE G 420.1-1, Nonreactor Nuclear Safety Design Criteria and Explosives Safety Criteria Guide for Use with DOE O 420.1, Facility Safety, March 2000

- Describe the relationship between surveillance and test requirements and design of electrical systems supporting the VSS.

General Design Criterion 21, Protection System Reliability and Testability, of appendix A, General Design Criteria for Nuclear Power Plants, to 10 CFR 50 requires, in part, that the protection system be designed to permit its periodic testing during reactor operation, including a capability to test channels independently to determine failures and losses of redundancy that may have occurred.  General Design Criterion 18, Inspection and Testing of Electric Power Systems, requires, in part, that electric power systems important to safety be designed to permit periodic testing, including periodic testing of the performance of the components of the system and the system as a whole.  The testing should be carried out under conditions as close to design as practical and should involve the full operational sequence, including operation of portions of the protection system, as well as the transfer of power among the nuclear power unit, the offsite power system, and the onsite power system.  Criterion XI, Test Control, of appendix B, Quality Assurance Criteria for Nuclear Power Plants and Fuel Reprocessing Plants, to 10 CFR 50 requires, in part, that a test program be established to ensure that all testing, including operational testing required to demonstrate that systems and components will perform satisfactorily in service, is identified and performed in accordance with written test procedures.

Reference: Nuclear Regulatory Commission, Regulatory Guide 1.118, Periodic Testing of Electric Power and Protection Systems, April 1995

- Discuss the Equipment Qualification process for Class 1E power systems in support of VSS: Principles of equipment qualification; Qualification methods; the Qualification Program; and, documentation requirements.

The electric equipment qualification program must include and be based on the following:

Temperature and pressure. The time-dependent temperature and pressure at the location of the electric equipment important to safety must be established for the most severe design basis accident during or following which this equipment is required to remain functional.

Humidity. Humidity during design basis accidents must be considered.

Chemical effects. The composition of chemicals used must be at least as severe as that resulting from the most limiting mode of plant operation (e.g., containment spray, emergency core cooling, or recirculation from containment sump).  If the composition of the chemical spray can be affected by equipment malfunctions, the most severe chemical spray environment that results from a single failure in the spray system must be assumed.

Radiation. The radiation environment must be based on the type of radiation, the total dose expected during normal operation over the installed life of the equipment, and the radiation environment associated with the most severe design basis accident during or following which the equipment is required to remain functional, including the radiation resulting from recirculating fluids for equipment located near the recirculating lines and including dose-rate effects.

Aging. Equipment qualified by test must be preconditioned by natural or artificial (accelerated) aging to its end-of-installed life condition.  Consideration must be given to all significant types of degradation which can have an effect on the functional capability of the equipment. If preconditioning to an end-of-installed life condition is not practicable, the equipment may be preconditioned to a shorter designated life. The equipment must be replaced or refurbished at the end of this designated life unless ongoing qualification demonstrates that the item has additional life.

Submergence (if subject to being submerged).

Synergistic effects. Synergistic effects must be considered when these effects are believed to have a significant effect on equipment performance.

Margins. Margins must be applied to account for unquantified uncertainty, such as the effects of production variations and inaccuracies in test instruments.  These margins are in addition to any conservatisms applied during the derivation of local environmental conditions of the equipment unless these conservatisms can be quantified and shown to contain appropriate margins.

Reference: 10 CFR 50.49, Environmental Qualification of Electric Equipment Important to Safety for Nuclear Power Plants, July 2006,

- Discuss the concept of ‘Independence’: Identify some of the general criteria for attaining ‘Independence’, e.g., physical separation, electrical isolation and devices, methods of achieving independence, and associated circuits; Describe the general concept of ‘Specific Separation Criteria, e.g., area classification and separation distances; Discuss the major requirements for circuit breakers and fuses to be considered as ‘isolation’ devices.

Section 4.6 of IEEE Std. 279-1971 requires, in part, that channels that provide signals for the same protective function must be independent and physically separated.  Section 5.6.1 of IEEE Std. 603-1998 states, “Redundant portions of a safety system provided for a safety function shall be independent of, and physically separated from, each other to the degree necessary to retain the capability of accomplishing the safety function during and following any design basis event requiring that safety function.”  General Design Criterion (GDC) 17, Electric Power Systems, in appendix A to 10 CFR 50 requires, in part, that electric power from the transmission network to the onsite electric distribution system shall be supplied by two physically independent circuits that are designed and located so as to minimize to the extent practical the likelihood of their simultaneous failure under operating and postulated accident and environmental conditions.  GDC 21, Protection System Reliability and Testability, requires, in part, that redundancy and independence designed into the protection system shall be sufficient to assure that no single failure results in a loss of the protection function.  GDC 22, Protection System Independence, requires that the effects of natural phenomena, and of normal operating, maintenance, testing, and postulated accident conditions on redundant channels do not result in loss of the protection function.

Reference: Nuclear Regulatory Commission, Regulatory Guide 1.75, Criteria for Independence of Electrical Safety Systems, February 2005

- State the general requirement for the single-failure criterion (SFC) and identify the major conditions used to apply the SFC to safety systems design: independence and redundancy; nondetectable, cascaded, common-cause failures; Design Basis Events; and shared systems.

Any single failure within the protection system should not prevent proper protective action at the system level when required.  Section 5.1 of IEEE STD 603-1998 states that the safety system must perform all safety functions required for a design basis event in the presence of (a) any single detectable failure within the safety systems concurrent with all identifiable but nondetectable failures, (b) all failures caused by the single failure, and (c) all failures and spurious system actions that cause or are caused by the design basis event requiring the safety functions.  The single failure could occur prior to, or at any time during, the design basis event for which the safety system is required to function.

Reference: Nuclear Regulatory Commission, Regulatory Guide 1.53, Application of the Single-Failure Criterion to Safety Systems, November 2003

## Demonstrate a familiarity-level knowledge of electrical safety design requirements for Emergency, Standby, and UPS systems for VSS (IEEE Stds 387-1984, 650-1990, and 944-1986; and, DOE O 420.1B and DOE G 420.1-1).

Note: IEEE STD 944-1986 was withdrawn on February 6, 2006.

- Identify and discuss the principal design criteria for standby power supplies supporting VSS: capability; ratings; interactions; design and application considerations; design features.

Emergency power systems are at the top of the hierarchy of backup power systems.  Legally required standby systems hold the No. 2 spot.  Optional standby systems are third in the pecking order.  Basically, their level of importance corresponds to the order in which they appear in the NEC.

A system is legally required when any government agency having jurisdiction says it is.  The rules that dictate what kinds of emergency loads are legally required are found in the locally adopted building code, such as the International Building Code or NFPA 101 Life Safety Code.  Unlike emergency systems, legally required systems do not directly protect the lives of the public at large.  They prevent shutting down specific loads — the loss of which would create hazards or impede rescue operations.  Hospital communications systems, for example, because evacuation instructions announced over the public address system are part of a rescue operation.  Article 701 of the NEC governs the installation, operation, and maintenance of such systems.

Legally required circuits and equipment supply illumination or power upon interruption of the normal electrical supply.  They provide electric power to aid in firefighting, rescue operations, control of health hazards, and similar operations.  They typically supply such loads as communications systems, ventilation and smoke removal systems, sewage disposal, lighting, and potentially dangerous industrial processes.  Surprisingly enough, they might also include fire pumps and elevators, which many people automatically assume are emergency loads.  The definition of “Legally Required Standby Systems” in 701.2 contains a Fine Print Note (FPN) that lists some of the items that might be a legally standby system…but be careful — FPNs are informational only [90.5(C)].  Do not depend on this FPN as a comprehensive list.  Always consult the AHJ and/or fire marshal to find out what is legally required.

A standby power system is optional when it is not required by Article 700 or Article. 701.  These systems protect public or private facilities or property where life safety does not depend on the performance of the system.  These systems are not required for rescue operations.

They may supply on-site generated power to selected loads automatically or manually.  These are typically installed to provide an alternate source of power.  This can be for a variety of facilities, including industrial and commercial buildings, farms, and even residences.  They serve such loads as heating and refrigeration systems, data-processing systems, communications systems, and industrial processes.  They may also serve any load that the customer considers important enough to warrant a backup system, but not important enough for a building code to require it, such as a break room refrigerator or that important coffee maker. These systems may be permanently installed, or they may be arranged for a connection to a premises wiring system from a portable alternate power supply.  A portable generator does not fall within the scope of Article 702, unless the generator is connected to the premises wiring.

It should come as no surprise that the AHJ must approve all equipment used in legally required systems.  What may surprise you is this same rule applies to optional systems.

While there are compelling operational and economic reasons to conduct testing and maintenance of optional systems, doing so is not an NEC requirement.  But for legally required systems, it is.

Legally required standby system testing consists of acceptance testing and operational testing.  The AHJ must conduct or witness an acceptance test of the emergency system upon completion of the installation, and periodically thereafter.  The systems must also be periodically tested to ensure they are in proper operating condition.  Running the system to power the loads of the facility is a generally accepted method of operational testing.  In fact, you must provide a means to test these systems under the maximum anticipated load condition.  In addition, you must maintain records of testing and maintenance.

Legally required and optional standby systems must have adequate capacity to safely carry all loads that are expected to operate simultaneously.  Because optional standby systems are not critical, the user of the system can select which load(s) to connect to the system.

Additionally, both legally required standby system and optional standby system equipment must be suitable for the maximum available fault current at line terminals.  The legally required standby alternate power source can supply legally required standby and optional standby system loads under either of these conditions:

The alternate power source has adequate capacity to handle all connected loads.

Automatic selective load pickup and load shedding is provided to ensure that the legally required system takes priority over the optional system.

To protect utility workers, the backup system must have approved transfer equipment.  Legally required standby systems and optional standby systems can be on the same transfer switch — emergency systems must have their own.  On legally required systems, transfer equipment must be identified for standby use and be approved by the AHJ.

Where an outdoor generator has a readily accessible disconnecting means within sight (within 50 feet) of the structure, you don not need an additional disconnecting means for the generator feeder conductors that serve or pass through the structure.  To warn emergency response personnel of multiple electrical supply systems, both legally required and optional standby systems are required to have a sign indicating the presence of the system.  This signage must be placed at the service disconnecting means for the structure, and must indicate the physical location of the standby systems power source.  The following power source requirements apply to legally required systems, but not to optional power sources.

If the normal supply fails, legally required power must be available within 60 seconds (as opposed to 10 seconds for emergency systems).  The supply system for the legally required standby power source must be one of these seven types:

Storage batteries. These must be of suitable rating and capacity to maintain the total load for 1.5 hours, without the voltage applied to the load falling below 87.5% percent of normal.

Generator set. If prime mover-driven, a generator acceptable to the AHJ (and sized per 701.6) must have the means to automatically start the prime mover upon failure of the normal service.  Where internal combustion engines are the prime movers, you need a 2-hour on-site fuel supply.

Uninterruptible power supplies. A UPS must comply with the requirements for batteries and generators.

Separate service. An additional service installed per Article. 230 can serve as a legally required source of power, but only if it is acceptable to the AHJ.  To minimize the possibility of simultaneous interruption of the legally required standby supply, a separate service drop or lateral must be electrically and physically separated from all other service conductors.

Connection ahead of service disconnecting means. Where acceptable to the AHJ, connection ahead of (not within) the same cabinet, enclosure, or vertical switchboard section as the service disconnecting means is permitted.  To prevent simultaneous interruption of supply, the legally required standby service disconnect must be sufficiently separated from the normal service disconnection means.  See Article 230.82 for equipment permitted on the supply side of a service disconnecting means.  You cannot have more than six service disconnects, including the disconnecting means for the standby system.

Fuel cell systems. A fuel cell system meeting the requirements of Article 692 can be used, provided the system is capable of carrying the load for at least 2 hours of full demand operation.

Unit equipment. Unit equipment consisting of a battery, a battery charging means, and automatic actuation can serve to supply some legally required loads, such as lighting. Where unit equipment is used, the battery must maintain at least 87.5% of battery voltage for at least 90 minutes.

The wiring for these systems can be in raceways, cables, boxes, and cabinets with other general wiring.

You do not need to provide ground-fault protection of equipment on the alternate source of legally required standby power systems.  But you must ensure selective coordination of the overcurrent protection devices of legally required power systems with all supply-side OCPDs.  Selective coordination for optional standby systems is not a Code requirement.

If the system is separately derived, ground it per Article 250.30.  If it is not separately derived, bond it to the system grounding electrode.

When you step back and take a look at what each kind of standby system is trying to accomplish, the requirements make sense.  Article 700 applies to systems or equipment required to protect people who are in an emergency and are trying to get out, while Article 701 applies to systems or equipment needed to aid the people responding to the emergency.  Article 700 lighting provides an exit path, but Article 701 lighting illuminates fire hydrants and switchgear areas.  Article 702 systems do not protect people — they protect against financial loss.

To ensure you do not confuse what is optional with what is legally required, walk down your systems and identify which non-emergency circuits and equipment prevent danger or aid in rescuing people.  Review the list with the AHJ and/or fire marshal, making necessary additions.

References: National Electrical Code, Articles 700, 701, and 702 and Legally Required and Optional Standby Systems By Mike Holt, NEC Consultant available at http://ecmweb.com/nec/electric_legally_required_optional/index.html

Identify and discuss some of the design application requirements for Uninterruptible Power Supplies (UPS) supporting VSS: performance requirements; UPS sizing and capacities; and UPS configurations.

The fundamental purpose of a UPS is to provide an uninterruptible source of power for the equipment it protects.  An electric device plugged into the wall (or into a surge suppressor plugged into the wall) has only one source of power.  If there is a blackout, the electricity is cut and the device obviously goes off immediately.  A UPS changes this equation by providing its equipment two sources of power.

UPSs are designed so that there is one source of power that is normally used, called the primary power source, and another source that kicks in if the primary is disrupted, called the secondary power source.  The power from the wall is always one of these sources, and the battery contained within the UPS is the other.  A switch is used to control which of these sources powers the equipment at any given time.  The switch changes from the primary source to the secondary when it detects that the primary power has gone out.  It switches back from the secondary power source to the primary when it detects that the primary power source has returned.

The wall AC power is not always the primary power source and the battery the secondary. Which source is primary and which is secondary depends on the type of UPS.

Of course, the power that comes from the wall is AC, and your equipment uses AC power as well.  All batteries, however, provide DC power.  Therefore, circuitry is provided within all UPSs to convert AC power to DC to charge the battery.  A device called an inverter is also provided to change the battery’s stored DC electricity to AC to run your equipment.  T

UPSs come in many different sizes and shapes.  The size of the UPS is primarily dictated by the size of the battery; the larger the battery, the more time your equipment can run on battery power before shutting down.  Larger units not only can power equipment for more time, they can also handle a larger total demand for power.  Different UPSs have various other additional features, including warning signals, PC control software, and conditioning circuitry for the AC power source.

One of the most important features of a UPS is its capacity.  Another is its run time.  While these two concepts are related, they are not the same.  It is important to understand the difference between them, as these numbers play a critical role in UPS sizing.

The run time that a UPS provides is the number of minutes that the UPS will be able to provide power from the battery for a given load level.  Since driving more equipment requires more power to be taken from the battery, driving more load will result in shorter run time.  A UPS with a larger battery, or with an add-on battery pack, will provide longer run time for a given load size.  Run time is critically important because it tells you how long a power outage the UPS can handle before the battery runs out.  Most UPS manufacturers will provide tables that show the typical run times for a model based on the loads it has to handle.  Here is a sample table for an APC Back-UPS Pro 650 model.

| Load (VA) | Run Time (minutes) |
| --- | --- |
| 100 | 49 |
| 200 | 22 |
| 300 | 14 |
| 400 | 9.3 |
| 500 | 7.2 |
| 600 | 5.8 |

Figure 9-Run time values and loads

In figure 9 the run time values for 100, 200 and 400 VA are highlighted.  Notice that when the load is doubled, the run time is reduced not by half, but by more than half.  One key reason for this is that lead-acid batteries discharge more quickly when they are drawing more load.

After looking at that chart, a natural question might be: “If it will run a 200 VA load for 22 minutes, and a 400 VA for 9.3 minutes, how long will it run an 800 VA load for? 4 minutes? 2 minutes?”  Unfortunately, the answer to this is probably “0 minutes.”  This is where capacity enters into the picture.  The UPS has a nominal maximum capacity, usually indicated by the number in its model name.  In this example, it is 650 VA.  The UPS will probably handle a load slightly above this figure--much the way your car does not stop dead when the fuel gauge hits “E,” but going to 800 VA will probably cause the UPS to overload and shutdown when it goes on battery.  The reason for a maximum capacity figure is not just the batteries.  It is also a function of the ability of the UPS’s circuitry and even its wires to handle a particular size of load.  It is also a safety issue, as exceeding the current limit of a circuit is unsafe.

While the UPS’s capacity is rated in terms of its nominal load limit in, there is another limit that must be observed.  To understand this other limit we must understand the difference between apparent power, which is the power provided as input to a device, and actual power, which is the power the device actually uses.  For most complex devices, these are not the same.  The ratio of actual power to apparent power of a device is its power factor.  The load on a UPS cannot exceed its apparent power load limit in VA, nor can the load exceed its actual power load limit in Watts.  Many UPS manufacturers do not publish a specific wattage limit, but instead assume that the power factor of its loads will be about 60%.  If you are driving a load that has a power factor of 60%, then the apparent and actual power limits are the same.  But if the loads you are driving have a power factor higher than 60%, you cannot use the total VA limit because your watt usage will be over the wattage limit.  I

Many larger UPS models offer the ability to increase run time by adding on expansion battery packs.  These expandable units are great, especially if you are not sure of your exact load requirements when you purchase the unit.  Expanding the UPS saves money over buying another since you are only paying for extra battery and not duplicating the UPS’s other components.

So, a UPS has a limit on the loads it can power.  In fact, it has two limits: a maximum apparent power load specification (in VA) and a maximum actual power load specification (in W).  Sometimes the actual power load limit is not explicitly provided but must be computed.  If the wattage is not listed specifically, it is safe to assume that it is 60% of the VA number.  However, you should read the specifications carefully, because some UPSs use a different ratio.

The rule for sizing a UPS is simple in concept, and difficult in application: the loads you attach to the UPS cannot exceed either of its limits.  Here are a couple of examples to show how the two limits work:  Take a 650 VA UPS.  The wattage limit is not specified, so to be safe, we use 60%, which yields a limit of 390W.  This means any load we run cannot exceed either 650 VA or 390 W.  Some sample power supply loads:

Regular Power Supply, 500 VA Rating: A regular power supply with a rating of 500 VA will run fine on this UPS, because its power factor is probably about 60%, much as the UPS manufacturer assumed.  Even if the power factor is 70%, that is still 350 W, under the UPS’s limit.

Power-Factor-Corrected Power Supply, 500 VA Rating: Some power supplies have circuitry added to them that corrects the power factor to approximately 100% (sometimes called power factor 1).  In this case the power supply will have a 500 VA rating and also a 500 W rating.  This power supply will overload the UPS we are discussing here because its W rating is too high.

To figure out what a load will demand of the UPS, we need to know both its VA and W ratings.  Unfortunately, many manufacturers do not provide the information required to make a knowledgeable decision.  An upper bound of the VA requirements of a unit can be obtained by looking for its current rating, which almost all devices have on a label or plaque near their power cord.  However, these numbers are usually rather conservative.  If a device has a 2A rating, then its nominal VA requirement is 2*115=230 VA.  However, in practice, it may never actually require more than, say, 175 VA.  There is no way to know for sure unless you know how to test the device electrically, so if you want to be absolutely certain, you must be conservative and use the maximum figure of 230.

Unfortunately, ideally sizing a UPS is not easy to do.  You often have to be conservative with your numbers and purchase a bit more UPS than you really need, to make sure you have your bases covered.  Here are some tools and techniques you can use to help you with sizing:

Use A Sizing Tool: American Power Conversion has a useful UPS sizing tool on its web site. Other companies also offer sizing programs.  These tools are specifically geared towards UPS sizing, and have databases of typical real VA and W requirements of various devices. They are probably the best place to start.

Read the Recommendations: For a UPS you are considering, look at the recommendations the manufacturer makes for the unit.  Compare them to what you are going to run and use common sense.  If the manufacturer says “deal for small desktop PCs” and you are running a high-powered equipment, you are probably asking for trouble if you try to run it on that UPS.

Test the UPS: The absolute best way to size a UPS, if you can do it, is to test it.

Be Conservative: A little too much is better than a little too little when it comes to a UPS.

Once you know your UPS has enough capacity to meet the requirements of your hardware, the next matter is one of run time: how much do you need?  The most important goal of a UPS is to provide enough power to let you gracefully shut down your system.  To get enough run time to actually work through anything but the shortest blackouts, you will usually have to pay substantially more money.  To lengthen your run time, do not plug unnecessary gadgets into your UPS’s backed-up receptacles.  For example, most peripherals do not need to be plugged into a UPS.  Most UPS manufacturers provide charts that show theoretical run-time for various sizes of load.

Reference: http://www.pcguide.com/ref/power/ext/ups/func.htm

- Identify some of the key Class 1E performance characteristics for Class 1E static battery chargers and inverters supporting VSS: Input conditions; Output requirements; Surge withstand capability; and, reverse current flow prevention.

For each division of the DC power system, the battery charger supplies the steady state DC power and maintains the battery in a fully charged condition.  The battery charger itself is supplied from the AC power system of the emergency power supply.

The battery chargers should have sufficient capacity to restore the battery from a discharged condition to a minimum charged state within an acceptable period of time while at the same time satisfying the highest combined demands of the various steady state loads following an initiating loss of normal power.  If the battery charger is permitted to supply the system with the battery disconnected, the charger should have the capability to satisfy the highest combined demands, including transients.  Each battery charger should have disconnecting devices in the AC and DC circuits to enable the charger to be isolated.

Ventilation should be provided in battery rooms to maintain the concentrations of combustible gases below prescribed levels.  This ventilation system should be powered by the emergency power supply.

Each redundant battery set should be capable of meeting all required load demands and conditions, including duty cycles and electrical transients occurring in operational states and under design basis accident conditions for a specified period of time (typically two to four hours), with account taken of such factors as design margins, temperature effects, any recent discharge and deterioration with age.

Overvoltage surges can be caused by lightning strikes, electrical faults or switching phenomena.  Voltage surge suppressors or arresters should be provided to prevent surges from exceeding the allowable voltage limits set for the equipment or its insulation.

Reference: International Atomic Energy Agency, Design of Emergency Power Systems for Nuclear Power Plants, August 2004

## Demonstrate a familiarity-level knowledge of electrical safety design requirements for VSS Accident Monitoring Instrumentation (IEEE Std 497-2002; and, DOE O 420.1B and DOE G 420.1-1).

- Identify and discuss the selection criteria used for identifying the ‘type variables’ for Accident Monitoring Instrumentation.

Nuclear Regulatory Commission. Regulatory Guide 1.97 defines five types and three categories of plant variables for accident monitoring instrumentation.  A discussion of these classifications is provided below.  Each variable has been defined as to both type and category.  Plant variables are divided into types according to the purpose of the indication to the plant operator.  Any one variable may belong to more than one type.

#### Type A

Type A are those variables to be monitored that provide the primary information required to permit the Main Control Room (MCR) operators to take the specified manual actions for which no automatic control is provided and that are required for safety systems to accomplish their safety functions for design basis accident events.

Primary information is information that is essential for the direct accomplishment of the specified safety function.  It does not include those variables that are associated with contingency (or backup) action that may also be identified in written procedures or guidelines.

Type A variables are limited to those variables which are necessary (primary) to alert the MCR operator of the need to perform preplanned manual actions for safety systems to perform their safety functions, such as initiating suppression pool cooling and containment spray to permit the systems to perform safety functions for which no automatic system controls are provided.

Variables that require actions specified by the emergency procedure guidelines in response to specific operating limits have also been considered in performing the assessment documented in this chapter.

Type A variables do not include variables (1) which may indicate whether a specific safety function is being accomplished (Type B), or (2) which may indicate the need for contingency or corrective actions, resulting from the failure of the plant (Type C) or system(s) (Type D) to respond correctly when needed, or (3) which may indicate to the operator that it is desirable to change or modify the operation/alignment of systems important to safety to maintain the plant in a safe condition after plant safety has been achieved.

#### Type B

Type B are those variables that provide information to the MCR operators to indicate whether plant safety functions are being accomplished, including reactivity control, core cooling, maintaining reactor coolant system integrity, and maintaining containment integrity.

#### Type C

Type C are those variables that provide information to the MCR operators to indicate that barriers to fission product release have the potential for being breached or have been breached.  These barriers are the fuel cladding, primary coolant pressure boundary, and primary containment.  The sources of potential breach are limited to the energy sources within the cladding, coolant boundary, or containment.

#### Type D

Type D are those variables that provide information to the MCR operators to indicate the successful operation of individual safety systems or other systems important to safety.  Type D variables should provide information to permit the MCR operators to ascertain the operating status of each individual safety system and other systems important to safety to that extent necessary to determine if each system is operating or can be placed in operation to help mitigate the consequences of an accident.

#### Type E

Type E are those variables monitored to determine the magnitude of release of radioactive materials and to assess the continuation of such releases.  These variables should permit the MCR operators to monitor the effluent discharge paths and environs within the site boundary to ascertain if there have been significant releases (planned or unplanned) of radioactive materials and to continually assess such releases.  In particular, Type E variables monitor:

The planned paths for effluent release

Plant areas inside buildings where access is required to service equipment necessary to mitigate the consequences of an accident

Onsite location where unplanned releases of radioactive materials are detected.

#### Categories of Variables

The design and qualification criteria for the instrumentation used to measure the various variables are divided into three categories that provide a graded approach to instrumentation criteria, depending on importance to safety of the variables.

In general, Category 1 provides for full qualification, redundancy, and continuous real-time display and requires onsite (standby) power.  Category 2 provides for qualification but is less stringent in that it does not (of itself) include seismic qualification, redundancy, or continuous display and requires only a high-reliability power source (not necessarily standby power).  Category 3 is the least stringent.  It provides for high-quality commercial-grade equipment that requires only offsite power.

Category 1 represents the most stringent criteria and is used for key variables.  Key variables are those parameters that most directly indicate the accomplishment of a safety function.  All Type A variables are considered to be Category 1.  For Types B and C, the key variables are Category 1, while backup variables are generally Category 3.

Category 2 provides less stringent criteria and generally applies to instrumentation designated for indication of system operating status.  Most Type D variables are classified as Category 2.

Category 3 provides criteria for high quality backup and diagnostic instrumentation or for other instrumentation where the state-of-the-art will not support requirements for higher qualified instrumentation.

#### Design and Qualification Criteria

The detailed design and qualification criteria for category 1, 2 and 3 variables are provided in Regulatory. Guide 1.97 for:

Equipment qualification

Redundancy

Power sources

Channel availability

Quality assurance

Display and recording

Range

Equipment identification

Interfaces

Servicing, testing, and calibration

Human factors

Direct measurement

Reference: Information Systems Important to Safety, http://japan.nonukesasiaforum.org/lungmen/CH_07/07_05.PDF

- Identify some key performance criteria of Accident Monitoring Instrumentation.

Instrumentation shall be provided to monitor variables and systems over their anticipated ranges for normal operation, for anticipated operational occurrences, and for accident conditions as appropriate to assure adequate safety, including those variables and systems that can affect the fission process, the integrity of the reactor core, the reactor coolant pressure boundary, and the containment and its associated systems.  Appropriate controls shall be provided to maintain these variables and systems within prescribed operating ranges.

A control room shall be provided from which actions can be taken to operate the nuclear power unit safely under normal conditions and to maintain it in a safe condition under accident conditions, including loss-of-coolant accidents.  Adequate radiation protection shall be provided to permit access and occupancy of the control room under accident conditions without personnel receiving radiation exposures in excess of 5 rem whole body, or its equivalent to any part of the body, for the duration of the accident.  Equipment at appropriate locations outside the control room shall be provided (1) with a design capability for prompt hot shutdown of the reactor, including necessary instrumentation and controls to maintain the unit in a safe condition during hot shutdown, and (2) with a potential capability for subsequent cold shutdown of the reactor through the use of suitable procedures.

Means shall be provided for monitoring the reactor containment atmosphere, spaces containing components for recirculation of loss-of-coolant accident fluids, effluent discharge paths, and the plant environs for radioactivity that may be released from normal operations, including anticipated operational occurrences, and from postulated accidents.

Reference: Nuclear Regulatory Commission, Regulatory Guide 1.97, Criteria for Accident Monitoring Instrumentation for Nuclear Power Plants, June 2006

## Demonstrate a familiarity-level knowledge of electrical safety design requirements for VSS Motor Control Centers (MCC) (IEEE Std 649-1991; and, DOE O 420.1B and DOE G 420.1-1).

- Identify the three qualification alternatives for VSS MCC equipment.

The three qualification alternatives for VSS MCC equipment are testing, analysis, and operating.

- Identify the three major elements of the qualification process for VSS MCC: Equipment specification; the Qualification Program; and, the documentation requirement.

Assemblies that include protective devices and other components, such as motor starters, carry a short circuit withstand rating.  This rating reflects both the interrupting capacity of the device and its ability to protect the components from catastrophic failure for downstream faults.  If the withstand rating of a motor starter is exceeded, components such as the contactor and overload relay could fail in such a way as to burst the enclosure and present a hazard to personnel, even if the current is successfully interrupted by the protective device.

When specifying mechanical equipment which includes motor starters, the required short circuit current withstand rating must be included as a specification item.  This value should be available from the electrical engineer, who must calculate the available short circuit currents for the electrical system to properly specify equipment such as panel-boards and MCCs.  Note that adequate withstand ratings ensure only that the equipment will not fail catastrophically; damage to the contactor or overload relay may still occur, and they should be inspected following any motor or circuit fault that causes the protective device to operate.

Reference: http://findarticles.com/p/articles/mi_m0BPR/is_12_16/ai_58348313

- Discuss the Qualification Procedural requirements for VSS MCCs relating to Aging, Seismic Qualification, and Harsh Environment Events.

The basic principles, requirements, and methods for qualifying Class 1E motor control centers for both harsh and mild environment applications in nuclear power generating stations are described in IEEE Std 649-1991, Standard for Qualifying Class 1E Motor Control Centers for Nuclear Power Generating Stations.  In addition to defining specific qualification requirements for Class 1E motor control centers and their components this standard is intended to provide guidance in establishing a qualification program for demonstrating the adequacy of Class 1E motor control centers in nuclear power generating station applications.

Reference: Institute of Electrical and Electronic Engineers, IEEE Std 649-1991, Standard for Qualifying Class 1E Motor Control Centers for Nuclear Power Generating Stations. 1991

## Demonstrate a familiarity-level knowledge of electrical safety design requirements for Digital Computers supporting VSS (IEEE Std 7-4.3.2-2003, Annex E; and, DOE O 420.1B and DOE G 420.1-1).

- Discuss some of the configuration requirements for communications independence relating to communications between computers in different safety channels.

IEEE Std 7-4.3.2-2003, Criteria for Digital  Computers in Safety Systems for Nuclear Power Generating Stations, describes computer  specific requirements addressing firmware, software, and hardware alike for the development  process in an integrated approach.  This standard recommends a minimum set of functional and design requirements for computer components of a safety system employed in nuclear power generating stations.  Additionally IEEE Std 1228, Standard for Software Safety Plans provides requirements for the development of a management plan and performance of safety software activities.

References: Institute of Electrical and Electronic Engineers, IEEE Std 7-4.3.2-2003, Criteria for Digital Computers in Safety Systems for Nuclear Power Generating Stations, 2003 and DOE G 414.1-4, Safety Software Guide for Use with 10 CFR 830 Subpart A, Quality Assurance Requirements, and DOE O 414.1C, Quality Assurance.

- Discuss some of the configuration requirements for communications independence relating to communications between safety and non-safety computers.

See element “a” for a discussion regarding configuration requirements for communications independence.

## Demonstrate a familiarity-level knowledge of electrical safety design requirements for VSS Protection Systems (IEEE Std 741-1997, and 833-1988; and, DOE O 420.1B and DOE G 420.1-1).

- Identify the key general design criteria for VSS Protection Systems (see IEEE Std 741, Section 4.)

- Identify the major criteria for establishing bus voltage monitoring schemes (see IEEE Std 741, Section 5.1.2 a) - h)).

- Identify the major requirement for selecting protective devices for direct-geared valve actuator motors (IEEE Std 741, Section 5.5, first paragraph, first sentence).

Criteria that establish protection requirements for Class 1E power systems and equipment are prescribed in IEEE Std 741-1997, Standard Criteria for the Protection of Class 1E Power Systems and Equipment in Nuclear Power Generating Stations.  The purpose of and the means for obtaining protection from electrical and mechanical damage or failures that can occur within a time period that is shorter than that required for operator action are described.  Testing and surveillance requirements are included.  For information related to electrical safety design requirements for VSS protection systems see the Institute for Electrical and Electronic Engineers, IEEE Std 741, Standard Criteria for the Protection of Class 1E Power Systems and Equipment in Nuclear Power Generating Stations.

Reference: IEEE Std 741-1997, Standard Criteria for the Protection of Class 1E Power Systems and Equipment in Nuclear Power Generating Stations

## Demonstrate a familiarity-level knowledge of electrical safety design requirements for Instrumentation and Control (I&C) Equipment Grounding of VSS (IEEE Std 1050-1996; and, DOE O 420.1B and DOE G 420.1-1).

- Discuss some design considerations for electrical noise minimization: Noise sources; noise-coupling methods; and techniques for electrical noise minimization.

### Noise Sources

Electrical noise can be annoying when it causes audible or visual interference in radios and televisions.  If it interferes with a depth sounder, or a back-up camera on a motor coach, then human life may be at risk.

Noise categorization is complex, but falls into two major types, radiated and conducted. Radiated noise is propagated through the air, while conducted noise is present on power and signal lines.

The best rule is to prevent noise from escaping its source, but this is not always easy to do, and in some cases, proper filtering would cost more than a manufacturer is willing to pay.  In other cases, noise exists because no one has considered the problem.  In such circumstances, noise might be prevented with easy and inexpensive methods.

High frequency noise is easier to filter than low frequency noise.  Intermittent noise, such as that generated by motors, can sometimes be minimized by clamping power lines with diodes or tranient absorbers.

Here is a list of devices that can cause noise in some form.

Fluorescent lights ...usually high frequency.

Alternators ...high frequency noise from the diodes as they switch between conducting and blocking state.

Alternator regulators ...from 30 Hz to several kHz.

Ignition systems ...often broadband noise from the audio range up.

Motors! Pumps, trim-tabs, fans, thrusters, windlass, etc. ... transient noise as they are turned on and off.

Battery Chargers ...from 60 Hz and up, depending on type of unit.

Inverters ...same as battery chargers.

Radio/radar transmitters ...the transmitted signals can be noise to other equipment.

Computers, monitors, printers.

Radio, television, and audio gear.

Cell phones, wireless phones.

To find a noise source, turn everything off, and then turn on one device at a time until the noise appears.  Finding the source of noise is hardest when the noise is intermittent.  Is there a motor that periodically operates and generates the noise?

Once a noise source is identified, treatment can begin.  As mentioned, clamping diodes may be a simple solution, but in complex situations, the noise will have to be measured on an oscillscope or spectrum analyzer before a targeted solution can be applied.

While filtering power to each sensitive device may work, it is always better to find the source of noise and prevent it from leaving.  A filter on a noise source is always more effective than trying to filter downstream devices.

Reference: Electrical Noise Sources, http://www.amplepower.com/apps/noise/index.html

### Noise Coupling Methods

Need something here

### Noise Minimization Techniques

Below is a list of techniques to minimize electrical noise:

Keep wires as short as possible

Loop wires through ferrite cores

Add snubber R/C circuit at motor terminals

Keep controller, wires and battery enclosed in metallic body

Reference: http://www.roboteq.com/files/manuals/ax1500man17-110305.pdf

- Describe the purpose or use of, and advantages and disadvantages for: Single-point ground systems; multi-point ground systems; and floating ground systems.

### Single-Point Ground System

A true single point ground system means just that, everything is referenced to a single point and that is were everything within your shelter is tied to the external earth ground system. The external ground system could include the utility ground, a facility ring ground, tower ground and your antenna and radial ground systems.  The single point is truly a single point, typically a single bus bar or equal that is typically 4 or 6 inches by 24 inches.  All system grounds terminate to this single bus bar connecting point.  In reality each component and external source is effectively bonded to a single point, which is then effectively bonded to the facility or site external ground system.

However, a single-point ground is not suitable for handling the higher frequencies encountered in modern computing devices.  The fundamental assumption behind the principle of single-point grounding is that the velocity of light is infinite.  Any time designers need to consider the velocity of light, notably at computer speeds, the single-point ground technique does not work.  A useful rule of thumb is that a single-point ground is appropriate if the longest dimension of interest is less than a 1/20 wavelength of the highest-frequency threat.  Thus, single-point grounds are appropriate for handling EMI with audio frequencies in most cases but inappropriate and unachievable for radio frequencies used in digital electronics.

Reference: National Electrical Code Internet Connection, http://www.mikeholt.com/mojonewsarchive/GB-HTML/HTML/Single-Point-Ground~20040427.php

### Multi-Point Ground System

A multipoint ground is an alternate type of electrical installation that attempts to solve the ground loop and mains hum problem by creating many alternate paths for electrical energy to find its way back to ground.  The distinguishing characteristic of a multipoint ground is the use of many interconnected grounding conductors into a loose grid configuration.  There will be many paths between any two points in a multipoint grounding system, rather than the single path found in a star topology ground.

If installed correctly, it can maintain reference ground potential much better than a star topology in a similar application.  However it is more complicated to install and to maintain over the long term, and can be more expensive.

Star toploogy systems can be converted to multipoint systems by installing new conductors between old existing ones.  However, this should be done with care as it can inadvertently introduce noise onto signal lines during the conversion process.  The noise can be diminished over time as noisy and failed components are removed and repaired, but some isolation of high current (e.g. motors and lighting) and sensitive low current (e.g. amplifiers and radios) equipment may always be necessary.

Reference: http://en.wikipedia.org/wiki/Multipoint_Ground

### Floating Ground

A system where the system ground is not actually connected to earth is often referred to as a floating ground.

Reference: http://en.wikipedia.org/wiki/Ground_(electricity)

- Identify the IEEE Standard citing requirements for VSS I&C equipment signal cable shield grounding requirements (IEEE Std 1050-1996).

At each end the cable shield in a distant host connection shall be connected through a circuit described below to signal ground.  The circuit consists of two components connected in parallel.  (1) A 100K, 1/8 watt resistor provides a path to leak off slow accumulations of static charge.  (2) A .01 mfd, 600 V ceramic capacitor bypasses sharp noise spikes.

Exception:  In cases of severe noise, one end of the shield or the other, but not both, may have to be tied directly to ground, sacrificing the symmetry.

Refer to IEEE Std 1050-1996, Guide for Instrumentation and Control Equipment Grounding in Generating Stations for more information.

Reference: http://tools.ietf.org/html/rfc745

## Demonstrate a familiarity-level knowledge of electrical safety design requirements for VSS Motor Operated Valves (IEEE Std 1290-1996; and, DOE O 420.1B and DOE G 420.1-1).

- Identify the IEEE Standard, citing requirements for motor applications, protection, and control for motor operated valve (MOV) motor applications (IEEE Std 1290).

For information regarding MOVs see IEEE Std 1290-1996, Guide for Motor Operated Valve (MOV) Motor Application, Protection, Control, and Testing in Nuclear Power Generating Stations. 1996

Additional Reading Requirements

## Obtain a clear understanding of electrical safety requirements and practices in the following list of regulatory and consensus standards documents, including the relationship between these documents and which are “enforceable” in your site’s contractors contract.  OSHA (29 CFR 1910 and Subpart S, and 29 CFR 1926 Subparts K and V), NFPA 70E, Standard for Electrical Safety in the Workplace/Maintenance, NFPA-70B, Recommended Practice of Electrical Equipment Maintenance, DOE-HDBK-1092, DOE Electrical Safety Handbook; and 10 CFR 851, Worker Safety and Health Program.

- Describe the purpose, scope, and application of the requirements detailed in the listed standards and Orders.

### 29 CFR 1910, Subpart S

This subpart addresses electrical safety requirements that are necessary for the practical safeguarding of employees in their workplaces and is divided into four major divisions as follows:

Design safety standards for electrical systems.  These regulations are contained in Sec. Sec.  1910.302 through 1910.330.  Sections 1910.302 through 1910.308 contain design safety standards for electric utilization systems.  Included in this category are all electric equipment and installations used to provide electric power and light for employee workplaces.  Sections 1910.309 through 1910.330 are reserved for possible future design safety standards for other electrical systems.

Safety-related work practices.  These regulations will be contained in Sections 1910.331 through 1910.360.

Safety-related maintenance requirements.  These regulations will be contained in Sections 1910.361 through 1910.380.

Safety requirements for special equipment.  These regulations will be contained in Sections 1910.381 through 1910.398.

Reference: 29 CFR 1910, Occupational Safety and Health Standards, July 2006

### 29 CFR 1926, Subpart K

This subpart addresses electrical safety requirements that are necessary for the practical safeguarding of employees involved in construction work and is divided into four major divisions and applicable definitions as follows:

Installation safety requirements.  Installation safety requirements are contained in Sections 1926.402 through 1926.408.  Included in this category are electric equipment and installations used to provide electric power and light on jobsites.

Safety-related work practices.  Safety-related work practices are contained in Sections 1926.416 and 1926.417.  In addition to covering the hazards arising from the use of electricity at jobsites, these regulations also cover the hazards arising from the accidental contact, direct or indirect, by employees with all energized lines, above or below ground, passing through or near the jobsite.

Safety-related maintenance and environmental considerations.  Safety-related maintenance and environmental considerations are contained in Sections 1926.431 and 1926.432.

Safety requirements for special equipment.  Safety requirements for special equipment are contained in Section 1926.441.

Reference: 29 CFR 1926, Safety and Health Regulations for Construction, July 2006

### 29 CFR 1926, Subpart V

The occupational safety and health standards contained in this subpart V shall apply to the construction of electric transmission and distribution lines and equipment.

As used in this subpart V the term construction includes the erection of new electric transmission and distribution lines and equipment, and the alteration, conversion, and improvement of existing electric transmission and distribution lines and equipment.

Existing electric transmission and distribution lines and electrical equipment need not be modified to conform to the requirements of applicable standards in this subpart V, until such work is to be performed on such lines or equipment.

The standards set forth in this subpart V provide minimum requirements for safety and health.  Employers may require adherence to additional standards which are not in conflict with the standards contained in this subpart V.

Reference: 29 CFR 1926, Safety and Health Regulations for Construction, July 2006

### NFPA 70E

This standard addresses those electrical safety requirements for employee workplaces that are necessary for the practical safeguarding of employees in their pursuit of gainful employment. This standard covers the installation of electric conductors, electric equipment, signaling and communications conductors and equipment, and raceways for the following: (1) Public and private premises, including buildings, structures, mobile homes, recreational vehicles, and floating buildings (2) Yards, lots, parking lots, carnivals, and industrial substations FPN: For additional information concerning such installations in an industrial or multi-building complex, see ANSI C2-2002, National Electrical Safety Code. (3) Installations of conductors and equipment that connect to the supply of electricity (4) Installations used by the electric utility, such as office buildings, warehouses, garages, machine shops, and recreational buildings, that are not an integral part of a generating plant, substation, or control center.

Reference: National Fire Prevention Association, NFPA 70E, Standard for Electrical Safety in the Workplace, 2004

### NFPA 70B

This recommended practice applies to preventive maintenance for electrical, electronic, and communication systems and equipment and is not intended to duplicate or supersede instructions that manufacturers normally provide.  Systems and equipment covered are typical of those installed in industrial plants, institutional and commercial buildings, and large multifamily residential complexes.  Consumer appliances and equipment intended primarily for use in the home are not included.

Reference: National Fire Prevention Association, NFPA 70B, Recommended Practice for Electrical Equipment Maintenance, 2006

### DOE-HDBK-1092

The Electrical Safety Handbook presents the DOE safety standards for DOE field offices or facilities involved in the use of electrical energy.  It has been prepared to provide a uniform set of electrical safety guidance and information for DOE installations to effect a reduction or elimination of risks associated with the use of electrical energy.  The objectives of this handbook are to enhance electrical safety awareness and mitigate electrical hazards to employees, the public, and the environment.

This handbook provides general information to enhance understanding of DOE Orders, national codes, national standards, and local, state, and federal regulations.  Each entity should reference its contract documents and determine what legal requirements are to be followed in the area of electrical safety.  These requirements may vary from location to location.

Reference: DOE-HDBK-1092-2004, Electrical Safety, December 2004

### 10 CFR 851

This final rule, which becomes effective February 9, 2007, codifies the Department’s worker protection program requirements established in DOE O 440.1A, Worker Protection Management for DOE Federal and Contractor Employees. Consistent with the intent of Congress, DOE O 440.1A forms the basis for the rule’s substantive requirements.  The Conference Committee for the NDAA recognized that contractors currently operate under this order, which provides an adequate level of safety.

Reference: Federal Register, February 9, 2006, Department of Energy 10 CFR Parts 850 and 851 Chronic Beryllium Disease Prevention Program; Worker Safety and Health Program; Final Rule

- Discuss the graded approach process that Department line management uses to determine an appropriate level of coverage by electrical personnel.  Include in this discussion the factors that may influence the level of coverage.

The process of assuring that the level of analysis, documentation, and actions used to comply with electrical requirements are commensurate with

the relative importance to safety, safeguard, and security;

the magnitude of any hazard involved;

the life cycle stage of a facility;

the programmatic mission of a facility;

the particular characteristics of a facility;

the relative importance of radiological and non-radiological hazards; and

any other relevant factor.

Reference: DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide, September 2001

- Determine contractor compliance with the listed documents as they apply to contract design requirements and electrical system activities at a defense nuclear facility.

This is a performance-based competency.  The qualifying official will evaluate the completion of this competency.

## Demonstrate a familiarity level knowledge of DOE O 414.1C, Quality Assurance, as it pertains to electrical systems.

- Mandatory Performance Activity: Describe how electrical equipment is procured based upon its safety function and/or nuclear related activity using quality assurance criteria and appropriate national or international consensus standards.

The procurement process should ensure that items and/or services provided by suppliers meet the requirements and expectations of the end user.  The procurement process should be planned and controlled to ensure that

the end user’s requirements are accurately, completely, and clearly communicated to the supplier;

supplier, designer, and end-user requirements are met during the production phase; and

the proper product is delivered on time and maintained until use.

Procurement processes should prevent introduction of suspect/counterfeit items and provide a method to detect them before they are released for use.

The selection of procurement requirements should be commensurate with the importance of the end use of the purchased item or service.  Management controls exist for DOE procurement and subcontracts through applicable DOE Orders, the Department of Energy Acquisition Regulation in 48 CFR subchapters A through H, and the Federal Acquisition Regulation in 48 CFR 970 et. seq.

The procurement process of DOE nuclear facility contractors must include a determination of the applicability of 10 CFR 830 to the supplier or subcontractor.  If applicable, procurement documents and contracts for items and services provided to facilities covered by 10 CFR 830 should include a statement informing the supplier or subcontractor that it is subject to 10 CFR 830 and of the potential for enforcement actions under 10 CFR 820.

Specific requirements related to electrical systems include

American Society for Testing and Materials (ASTM) Committee F-18, Electrical Protective Equipment for Workers, has developed and published a consensus standard for protective grounds, ASTM Designation: F-855.  This voluntary consensus standard may be used by all federal agencies for procurement purposes.  Therefore, grounding cables, clamps, and ferrules purchased should meet all the requirements of ASTM Designation: F-855.  Aluminum cables shall not be used for personal grounds.

Procurement and use of equipment not listed by an NRTL should be reviewed by the AHJ.  The extensive testing involved in the listing process usually cannot be duplicated at the user facility, and many of the tests are destructive in nature.  The AHJ should develop an examination acceptance process to ensure appropriate confidence in the safety of the product.

References: DOE G 414.1-2A, Quality Assurance Management Guide, June, 2005; and DOE-STD-1092-2004, Electrical Safety, December 2004

- Describe what is meant by implementing quality assurance criteria using a graded approach.

A graded approach that doesn’t compromise public, employee, or facility safety or adversely impact the environment and complies with requirements, rules, and regulations must be used to implement the QAP.  The graded application of facility/activity requirements is dependent on the hazards and/or level of risk associated with the activity or SSCs under consideration.  The scope, depth, and rigor of the quality management system’s application of requirements should be determined by the use of a grading process before performing the activity.  The purpose of grading is to select the controls and verifications to be applied to various items and activities consistent with their importance to safety, cost, schedule, and success of the program.

Grading is encouraged if a single or uniform method of applying a requirement across a facility or activity does not add value or reduce risk.  The grading process provides the flexibility to design controls that best suit the facility or activity.  The grading process is not used to obtain exemptions from the requirements of the QA Rule or Order.

The grading process is used to determine the appropriate controls to address and mitigate hazards and/or risks.  This process is accomplished by deliberate quality planning and is based on activity-specific or facility-specific factors such as

the relative importance to safety, safeguards, and security;

the magnitude of any hazard or risk involved;

the life-cycle stage of a facility or activity;

impact/consequences on the programmatic mission of a facility;

the particular characteristics of a facility or activity;

the nuclear safety classification or hazard category of the item or activity;

adequacy of existing safety documentation;

the relative importance of radiological and nonradiological hazards;

complexity of products or services involved;

performance history of a facility or activity; and

any other relevant factors.

The first step in the grading process is to identify the hazards, and for the facility level their consequences and probability of a failure, before work begins.  The second step is to identify the specific requirements and controls to be applied.  The third step is to determine the depth, extent, and degree of rigor necessary in the application of the requirements and controls.  The final step is to communicate and implement the selected requirements and controls and their degree of rigor by means of documented work processes (procedures, instructions, specifications, and controls).  The logic, method of implementation, and basis for grading should be documented in the quality management system, periodically reviewed in light of changes that may have occurred, and if appropriate, revised to reflect those changes.

The graded approach must not be used to “grade quality assurance criterion to zero” which has the affect of eliminating all verifications of the requirement (“to get out of work”).  Even in the least stringent application, compliance with applicable portions of stated requirements is mandatory unless an exemption is approved through an appropriate process.

When considering the use of grading of an item or activity, it is important to consider the impact of safety on personnel, the public, and the environment.  The safety class or safety significance of the item or activity is critical to the amount of controls imposed which are necessary to assure the requisite or desired quality.

Reference: DOE G 414.1-2A, Quality Assurance Management Guide, June, 2005

Describe the types of documents related to electrical systems that should be controlled by a document control system.

Risk is a fundamental consideration in determining to what extent controls should be applied at the facility level.  The varying degrees of the controls applied should be dependent upon function, complexity, consequence of failure, reliability, repeatability of results, and economic considerations.

These controls are documented and communicated to facility/activity personnel to ensure appropriate application.  This documentation should take the form of written procedures, practices, requirements manuals, policy statements, standing orders, or other written and controlled means as deemed appropriate by facility/activity management.  The level of approval of this documentation is also based on the hazards, complexity, and/or relative risk.

Documentation specific to electrical systems include the following:

All testing methods, apparatus, and facilities shall meet the applicable ANSI/ASTM Standard.

The method used and the results of such tests shall be documented and made available for inspection.

Each employer shall document and implement lockout/tagout procedures to safeguard employees from injury while they are working on or near de-energized electric circuits and equipment.  The lockout/tagout procedures shall meet the requirement of NFPA 70E 120.2, 29 CFR 1910.147(c) to (f), 1910.269(d) and (m), 1910.333, and 1926.417.

An electrical preventive maintenance (EPM) program is defined as the system that manages routine inspections and tests and the servicing of electrical equipment so that impending troubles can be detected and reduced or eliminated.  Where designers, installers, or constructors specify, install, and construct equipment with optional auxiliary equipment, that optional equipment should be part of the EPM program.  Records of all inspections, tests, and servicing should be documented and reviewed.

Electrical equipment should be maintained in accordance with the manufacturer’s recommendations and instructions for the local operating environment.  A copy of the manufacturer’s recommendations should be documented and on file.

Areas that contain explosives that are not defined as hazardous locations (areas containing no dust, vapor, gas hazards, or exposed explosives; for example, storage magazines), shall be evaluated and documented by facility management to ensure that electrical ignition sources are minimized or shall be regarded as NEC Class II.

Maintenance checklists and schedules in compliance with OSHA, owner’s manuals, and manufacturer’s requirements for the specific equipment shall be provided as required.  Weekly, monthly, and semiannual inspections shall be conducted, and comments and condition of the inspected part shall be documented and certified.

In cable/utility management systems where cables other than those of the equipment exist, the decision should be documented that any risk posed by the situation is acceptable for the operation to be performed and to the functions of the existing cables.

Metallic cable/utility management systems that support electrical conductors shall be grounded or bonded to the equipment.  Grounding integrity should be checked by inspection by a qualified worker for all components with exposed metal parts.  This inspection should be documented.

Where cable/utility management systems are installed exclusively for electrical/electronic equipment usage and where these trays are metallic and not grounded or bonded, approved documentation shall exist stating the reason for not grounding or bonding the system.

Documentation should be developed to substantiate the acceptance of any equipment. Such documentation should include but not be limited to:

Tests performed

Conditions of acceptability

Applicable standards to which the equipment was evaluated

Limitations of approved use, if any.

References: DOE G 414.1-2A, Quality Assurance Management Guide, June, 2005; and DOE-STD-1092-2004, Electrical Safety, December 2004

- Discuss the requirements for revision and distribution of controlled documents.

The organization responsible for document control should be notified of any need to change a document as soon as that need is identified and approved, typically through the change control or work control processes.  A document change notice may be used for this purpose.  The organization responsible for document control should provide a receipt acknowledging the notification that a document should be changed.  The organization responsible for document control should take the appropriate action to update the document and record the status in the document control database.

The contractor should specifically identify in the change control process what constitutes a minor change (e.g., inconsequential, editorial corrections).  Major changes to controlled documents are any changes that are not defined as minor changes.  Major changes to controlled documents must be reviewed and approved by the document owners.  The configuration management process may specify a simpler review for minor changes.

Pending changes are changes that have been approved for which the associated documents have not yet been updated and distributed.  The organization responsible for document control should provide notice of pending changes to the controlled document users for the applicable documents.  A notice of the pending change should also be attached to, or appropriately referenced on, the affected master document, in order to alert anyone requesting a copy of the document.

Contractors must incorporate approved changes into controlled documents in a timely manner.  The contractor should control and limit the backlog of changes that have not been incorporated.  Contractors should consider incorporating small changes in batches, where appropriate.  When there is a large backlog of changes that have not been incorporated on a document, the documents may not reflect the physical facility or the approved safety basis consequently diminishing the value of the documents.  Document control procedures should specify the limit of the number of changes that may be outstanding for a document before the document is revised.  That limit may vary depending upon the type of document, document priority, complexity of the changes, and the degree of overlap of those changes.

Whenever a document is issued or superseded by a new revision, the contractor organization responsible for document control must send a copy of the new revision to each controlled document user of the document, along with a request for written receipt acknowledgment.  Contractors can facilitate the return of receipt acknowledgments by sending a receipt acknowledgment form with the revised document.  Document control procedures should specify guidelines for the maximum time between issuance of the revised controlled document and distribution.  For example:

| Level of importance of controlled documents | Maximum time before distribution |
| --- | --- |
| Most important (e.g TSRs) | 24 hours |
| Important | 72 hours |
| Least important | 7 days |

The recipients (controlled document users) should update their copy of the document (for example, by inserting changed pages), and discard any obsolete pages or copies of documents.  The recipient must return a written acknowledgment of receipt to the document control organization.  The controlled document users should periodically review controlled copies in use to ensure their accuracy and their consistency with the master copies.

The contractor should ensure that the document control process includes measures to ensure that superseded or canceled documents are replaced.  If someone requests a copy of a superseded or canceled document, the provider should clearly and distinctively mark the document as “Superseded” or “Canceled” before providing the document.

Reference: DOE-STD-1073-2003, Configuration Management, October 2003

- Discuss the determination of calibration frequency for electrical test equipment.

Frequency of calibration should be determined based on the manufacturers’ recommendations, measuring and test equipment (M&TE) usage, and M&TE historical reliability.  Consideration should be given to the amount and type of M&TE available for use compared with that needed to support periods of peak activity such as outages.  This information can help determine calibration frequency and schedule requirements that result in adequate M&TE support for facility needs.

The standards laboratory, in conjunction with each department manager responsible for M&TE, should establish and maintain a calibration schedule for the M&TE, including primary, secondary, and working standards.  Specific items may be calibrated on a prior-to-use basis rather than on a periodic basis.

The schedule should normally be divided by application departments.  The M&TE assigned to a department should be listed in calibration due date order by the unique identification number and noun name.  Calibration dates for similar M&TE should be staggered to ensure availability for day-to-day and peak needs.  The established scheduling organization should normally update and distribute the schedule to the responsible department managers on a quarterly basis.  Department managers should ensure that M&TE under their cognizance is calibrated in accordance with the master schedule.

The calibration intervals for M&TE should be established by the cognizant department managers.  The initial interval should be based on the inherent stability characteristics of the device, the rate/level and purpose of expected use, manufacturer’s recommendation, and historical data for similar equipment.  Calibration intervals may be revised based on a review of previous calibration results and maintenance history.

Revision of calibration intervals should require the approval of the cognizant department manager.  Revisions should be documented on the calibration interval change authorization form which should be filed in the maintenance history.

Reference: DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide for Use with DOE O 433.1, September 2001

- Describe the effect of using inappropriate calibration standards on electrical test equipment.

M&TE found to exceed required calibration tolerance or that has been subjected to possible damage should be identified as rejected.  When repairs are required to standards or other M&TE, they shall be re-calibrated to the original requirements prior to being returned to normal service.  When calibration/certification is performed, the as-found condition and/or minor adjustments to the M&TE should be noted as part of the equipment history information.

When M&TE is suspected or actually found to be inoperable, unreliable, defective, or out of calibration, all data recorded since the previous calibration by affected equipment should be identified through a usage record.  A prompt evaluation should be performed to determine the need for corrective action.  This evaluation shall be documented on a gross error report.  The validity of all applications and data derived since the previous calibration should be evaluated and dispositioned by the appropriate owner/operator affected.  The owner/operator of the affected equipment should establish the nature and timing of corrective actions.

Reference: DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide for Use with DOE O 433.1, September 2001

- Discuss the key elements of the procurement process for electrical systems as described in DOE O 414.1C, Quality Assurance.

The organization should ensure that procured items and services meet established requirements and perform as specified.  Prospective suppliers should be evaluated and selected on the basis of specified criteria.  The organization should ensure that approved suppliers can continue to provide acceptable items and services.

Reference: DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide for Use with DOE O 433.1, September 2001

## Demonstrate a familiarity-level of knowledge of DOE O 430.1B, Real Property Asset Management, with regard to life cycle asset management.

- Explain the Department’s role in the oversight of contractor maintenance operations.

The Department’s in the oversight of contractor maintenance operations is to ensure that safety requirements necessary for a practical safeguarding of applicable DOE facilities and personnel are being adequately implemented.  Practical safe work procedures include training of skilled and unskilled personnel who work in maintenance.  Safety measures shall protect personnel against both normal operations and emergency situations.  In addition, only qualified persons who are capable of working safely in maintenance and are familiar with the proper use of special precautionary techniques, personal protective equipment, TSRs, and operating procedures may perform work.  Maintenance management personnel perform DOE line management oversight of their assigned facilities to ensure that

the contractor is operating facilities safely and efficiently (i.e., within the boundaries of those controls invoked in the facility authorization basis);

the contractor’s management system is effectively controlling conduct of operation as related to nuclear safety;

effective lines of communication between DOE and its operating contractors are maintained during periods of normal operation, and following reportable events, in accordance with DOE Orders and requirements.

Reference: DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide for Use with DOE O 433.1, September 2001

Identify the key elements of a contractor maintenance plan as required by the DOE Orders referenced above.

DOE contractors should develop a maintenance implementation plan (MIP) for each nuclear facility under their cognizance.  Where one contractor has more than one facility on a site, the contractor may develop a consolidated plan that can accommodate the facility differences without losing effectiveness.  DOE contractors may include facility-related, non-safety equipment within the MIP.  The MIP should clearly identify and define the following minimum elements.

All SSCs included in the maintenance program (typically all those SSCs identified in the nuclear facility safety basis as documented in the DSA, Basis for Interim Operation, TSR); SSCs that are critical to mission objectives or facility operations; or SSCs that may be desirable for inclusion in the maintenance program for other reasons.  Contractors should develop a detailed master list of equipment/SSCs to be included in the maintenance program to help in selecting and scheduling preventive maintenance and to evaluate the effectiveness of the maintenance program.  The list normally is developed and controlled by or with assistance from engineering support organizations and can be used for other purposes, such as determining the safety or code classification of components.  The MIP should include both safety-related and non-safety related SSCs in the maintenance program.  Failures of non-safety-related SSCs can lead to challenges, failure or undesirable consequences to safety-related SSCs. Special tools or equipment should also be included in the MIP.  This list could be used effectively to help establish the maintenance history program and to determine the necessary parts required to maintain equipment.

Management systems used to control maintenance activities associated with the defined SSCs (these include work control, post-maintenance testing, material procurement, handling and disposal, control and calibration of M&TE).

Assignment of organizational roles and responsibilities and appropriate maintenance related training and qualification requirements.

Interfaces between the maintenance organization and other organizations (e.g., operations, engineering, quality, training, industrial health).

Facility/site mission.

System for assessing maintenance status.

Planned major activities.

Summary of maintenance backlog.

Performance indicators.

Self-assessment program.

Schedule for periodic inspection of SSCs, and equipment to determine whether deterioration or technical obsolescence that threatens performance and/or safety is taking place.

The MIP should establish maintenance priorities based on mission needs, and the priorities should be tracked directly to maintenance budget requests.  This provides a forum on maintenance priorities between DOE and the contractor operating a nuclear facility.  The maintenance priorities should be derived from or based on the DSA/BIO/TSR to preserve the

facility’s safety envelope so that the SSCs covered by the MIP are maintained in a condition suitable for their intended use.

The MIP should describe in detail the integration of the MIP with the QAP and the safety management system.

The MIP should establish a configuration management process to ensure the integrity of the identified nuclear facility SSCs using a graded approach.

The MIP should establish how an accurately documented, computerized maintenance history engineering database will be maintained locally and how certain data fields will be incorporated into the DOE corporate FIMS.  The MIP will facilitate DOE maintenance planning, performance evaluation, and prioritizing in a way that balances safety requirements, the maintenance backlog, and facility availability so that resources can be effectively allocated to address safety, programmatic, and operational considerations

The MIP should establish how performance requirements for those infrastructure elements identified as part of the nuclear safety basis will be enforced.

Reference: DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide for Use with DOE O 433.1, September, 2001

Describe configuration control and its relationship to the maintenance work control process and the maintenance history file.

### Configuration Control

The configuration management process addresses material condition and aging management (MCA).  MCA develops analytical methods and testing techniques that can be used to meet the requirements of the maintenance program.

Configuration management programs also interface with the maintenance program through the change control and document control elements, which address control of hardware and procedure changes.  The main interface is through the work control process of the maintenance program that manages and sequences maintenance activities in the field.  Another important interface exists between the preventive and predictive maintenance activities and the performance monitoring function of the assessment element.  Configuration control is maintained by ensuring that systems and equipment are restored to their original condition following maintenance.

### Maintenance History File

Assessments should ensure that

equipment repair history is used to support maintenance activities, upgrade maintenance programs, optimize equipment performance, and improve equipment reliability;

the maintenance history program defines what data are to be collected, how the data are to be recorded, and how the data are to be used;

a cost-effective equipment history program is in place for systems, equipment and components that warrant special attention based on initial cost, cost to maintain, or impact on facility operations or safety;

maintenance records are closely correlated with the current issue of the facility master equipment list;

the facility master equipment list is a compilation of system and equipment and provides an engineering database;

maintenance history records are considered in planning for corrective maintenance, modifications, and preventive maintenance, and development of facility life-cycle plans;

maintenance history records are readily available for use by supervisors, work planners, and maintenance or plant engineers;

maintenance history is periodically and systematically reviewed to identify equipment trends and persistent maintenance problems and to assess their impact on facility reliability;

equipment maintenance and repair history files contain items such as the following: equipment and component identification, maintenance records, diagnostic monitoring data, vendor information (or a reference to this information), corrective and preventive maintenance or modification information, and spare parts information;

the maintenance record is a chronological list of all maintenance repair work and materials expended on a piece of equipment or component;

equipment repair history data is used for such activities as failure analysis, conduct of maintenance assessments, preventive maintenance, predictive maintenance, outage planning, budget preparation, reviews of DOE-wide experience, and plant life extension;

vendor information obtained from suppliers is controlled and indexed for ready retrieval.

Reference: Senior Technical Safety Manager Reference Guide, April 2006

Describe the mechanisms for feedback of relevant information, such as trend analysis and instrumentation performance/reliability data, to identify necessary program modifications.

A maintenance history and trending program should be maintained to document data, provide historical information for maintenance planning, and support maintenance and performance trending of nuclear facility systems and components.  All records and documentation should be maintained according to the approved site-specific records retention and disposition schedule.

Reference: DOE O 433.1, Maintenance Management Program for DOE Nuclear Facilities, June 2001

Review a contractor preventive maintenance activity and describe the preventive maintenance factors to be considered as the activity is planned.

This is a performance-based competency.  The qualifying official will evaluate the completion of this competency.

Discuss the importance of post-maintenance testing and the elements of an effective post-maintenance testing program.

Before returning equipment to service following maintenance, the equipment should be tested to demonstrate that it is capable of performing its intended function.  This serves two purposes.  The testing should verify that the maintenance was performed correctly.  It should also prove that no problems were introduced as a result of the maintenance activities.

The maintenance work control package or maintenance procedure should specify the type and duration of post-maintenance testing required.  For some facilities, the specific requirements to prove operability of safety-related systems are identified in the TSRs.  An engineering evaluation should determine whether additional testing or different methods are required whenever the scope of work is changed, e.g., when additional work is performed to correct a previously undisclosed problem that is discovered during maintenance.  All equipment functions that may have been affected by the maintenance should be tested.

Operation of the equipment for testing should be performed by qualified operations personnel in accordance with approved procedures.  Maintenance personnel should monitor the testing. The operations supervisor is ultimately responsible for ensuring that the testing proves the operability of the equipment.

Reference: DOE O 433.1, Maintenance Management Program for DOE Nuclear Facilities, June 2001

Review the results of post-maintenance testing activities and discuss the acceptance of post-maintenance testing.

This is a performance-based competency.  The qualifying official will evaluate the completion of this competency.

Discuss the importance of maintaining a maintenance history.

A maintenance history and trending program should be maintained to document data, provide historical information for maintenance planning, and support maintenance and performance trending of facility systems and components.  The documentation of complete, detailed, and usable history will be increasingly important as plant-life extension becomes an issue.  Trending should be directed toward identifying improvements for the maintenance program and needed equipment modifications.

The maintenance history program should document SSC maintenance and performance data as a basis for improving facility reliability.  This history should assist in ensuring that root causes of failures are determined, corrected, and used in future work planning.  This may be accomplished by a thorough review and analysis of maintenance performed, diagnostic monitoring data, and industry experience reports.

Reference: DOE O 433.1, Maintenance Management Program for DOE Nuclear Facilities, June 2001

Review a maintenance history file and discuss the potential implications of repeat maintenance items.

This is a performance-based competency.  The qualifying official will evaluate the completion of this competency.

Explain the intent of a Maintenance Problem Analysis Program and discuss a maintenance problem where this program has been employed.

A problem analysis program is a system designed to help correct the causes of equipment and human error problems.  This may improve the reliability of the site by decreasing the probability of recurrence.  Examples of proven and accepted techniques for analyzing for root cause include the following:

Event and causal charts (system utilizing a block diagram to depict cause and effect)

Barrier analysis (questioning process used to determine what programmatic system or barrier may have prevented the problem)

Walk-through task analysis (step-by-step reenactment to determine the failure mode

Change analysis (looks at the problem from the standpoint of what was expected and what actually happened)

Interviews

An acceptable root cause should meet three criteria:

Its correction should prevent recurrence of the unplanned occurrence.

Its correction should be feasible.

Its correction should not adversely impact safety, reliability, or operational goals.

The most important aspect of an analysis program is to fix the problem and not merely conduct an academic, analytical thought exercise.  Therefore, after the root cause has been determined, corrective actions should be initiated to correct the deficiency and prevent recurrence.  Follow-up should be incorporated into the corrective action to ensure the fit is appropriate and the problem does not recur.

Reference: DOE O 433.1, Maintenance Management Program for DOE Nuclear Facilities, June 2001

# Selected Bibliography and Suggested Reading

10 CFR 50.34, “Licenses for Industrial Radiography and Radiation Safety Requirements for Industrial Radiographic Operations.” January 2006.

10 CFR 50.49, “Environmental Qualification of Electric Equipment Important to Safety for Nuclear Power Plants.” July 2006

10 CFR 50.82, “Termination of License.” January 2006

10 CFR 830.203, “Unreviewed Safety Question Process.” January 2006.

10 CFR 830.204, “Documented Safety Analysis.” January 2006.

10 CFR 830.205, “Technical Safety Requirements.” January 2006.

29 CFR 1910, “Occupational Safety and Health Standards.” July 2006.

29 CFR 1926, “Safety and Health Regulations for Construction.” July 2006.

American National Standards Institute. ANSI-C2, National Electrical Safety Code. 2002.

American National Standards Institute. ANSI Z136.1-2000, Guide for the Safe Use of Lasers. 2000.

Dorf, Richard C. The Electrical Engineering Handbook. 1st ed. CRC Press, 1993.

Federal Register, February 9, 2006, Department of Energy 10 CFR Parts 850 and 851 “Chronic Beryllium Disease Prevention Program; Worker Safety and Health Program; Final Rule.” February 9, 2006.

Firesmith, Donald G. A Taxonomy of Safety-Related Requirements. Software Engineering Institute, Pittsburgh: December 2003. http://www.sei.cmu.edu/community/rhas-workshop/firesmith.pdf.

Institute of Electrical and Electronic Engineers. IEEE Std 7-4.3.2-2003, Criteria for Digital  Computers in Safety Systems for Nuclear Power Generating Stations. 2003.

Institute of Electrical and Electronic Engineers. IEEE Std 141-197, IEEE Red Book, Electrical Power Distribution. 1996.

Institute of Electrical and Electronic Engineers. IEEE Std 142-1982, IEEE Green Book, Grounding. 1982.

Institute of Electrical and Electronic Engineers. IEEE Std 242-1975, IEEE Buff Book, Protection and Coordination. 1975.

Institute of Electrical and Electronic Engineers. IEEE Std 308-2001, Standard Criteria for Class 1E Power Systems for Nuclear Power Generating Stations. March 2002.

Institute of Electrical and Electronic Engineers. IEEE Std 323-2003, Standard for Qualifying Class 1E Equipment for Nuclear Power Generating Stations. January 2004.

Institute of Electrical and Electronic Engineers. IEEE Std 379-2000, Standard Application of the Single-Failure Criterion to Nuclear Power Generating Station Safety Systems. March 2001.

Institute of Electrical and Electronic Engineers. IEEE Std 384-1992, Standard Criteria for Independence of Class 1E Equipment and Circuits. December 1992.

Institute of Electrical and Electronic Engineers. IEEE Std 387-1984, Criteria for Diesel-Generator Units Applied as Standby Power Supplies for Nuclear Power Generating Stations. August 1989.

Institute of Electrical and Electronic Engineers. IEEE Std 446-1987, IEEE Orange Book, Emergency and Standby Power. 1987.

Institute of Electrical and Electronic Engineers. IEEE Std 603-1998, Standard Criteria for Digital Computers in Safety Systems of Nuclear Power Generating Stations. December 2003.

Institute of Electric and Electronic Engineers, IEEE Std 649-1991, Standard for Qualifying Class 1E Motor Control Centers for Nuclear Power Generating Stations. 1991

Institute of Electrical and Electronic Engineers. IEEE Std650-1990, Standard for Qualification of Class 1E Static Battery Chargers and Inverters for Nuclear Power Generating Stations. December 1990.

Institute of Electrical and Electronic Engineers. IEEE Std 741-1997, Standard Criteria for the Protection of Class 1E Power Systems and Equipment in Nuclear Power Generating Station. 1997.

Institute of Electrical and Electronics Engineers. IEEE Std 828-1998, Standard for Software Configuration Management Plans. 1998.

Institute of Electrical and Electronics Engineers. IEEE Std 830-1998, IEEE Recommended Practice for Software Requirements Specifications. 1998.

Institute of Electrical and Electronics Engineers. IEEE Std 944-1986, Recommended Practice for the Application and Testing of Uninterruptible Power Supplies for Power Generating Stations. Withdrawn February 2006.

Institute of Electrical and Electronics Engineers. IEEE Std 1050-1996, Guide for Instrumentation and Control Equipment Grounding in Generating Stations. 1996.

Institute of Electrical and electronics Engineers. IEEE Std 1290-1996, Guide for Motor Operated Valve (MOV) Motor Application, Protection, Control, and Testing in Nuclear Power Generating Stations. 1996.

International Atomic Energy Agency, Design of Emergency Power Systems for Nuclear Power Plants, August 2004.

Kurhaldt, Tony R. All About Circuits. Design Science License. http://www.allaboutcircuits.com/vol_1/chpt_10/8.html.

Mablekos, Van E. “The Two-Phase Induction Motor.” Section 4.10 in Electric Machine Theory for Power Engineers. New York: Harper & Row, 1980.

National Fire Protection Association. NFPA-70E, Standard for Safety in the Workplace. 2004

National Fire Prevention Association, NFPA 70B, Recommended Practice for Electrical Equipment Maintenance, 2006.

National Fire Protection Association. NFPA-780, Standard for the Installation of Lightning Protection Systems. 1997.

National Fire Protection Association. NFPA 70B, Recommended Practice for Electrical Equipment Maintenance. 2002.

National Fire Protection Association. NFPA 70E, Standard for Standard for Electrical Safety in the Workplace. 2004.

National Fire Protection Association. NFPA 72, National Fire Alarm Code. 2002.

U.S. Department of Energy. DOE Guide 414.1-2A, Quality Assurance Management Guide, June, 2005.

U.S. Department of Energy. DOE Guide 420.1-1, Nonreactor Nuclear Safety Design Criteria and Explosive Safety Criteria Guide for Use with DOE O 420.1 Facility Safety. March 2000.

U.S. Department of Energy. DOE Guide 420.1-2, Guide for the Mitigation of Natural Phenomena Hazards for DOE Nuclear Facilities and Non Nuclear Facilities. March 2000.

U.S. Department of Energy. DOE Guide 421.1-2, Implementation Guide for Use In Developing Documented Safety Analyses to Meet Subpart B of 10 CFR 830, October 2001.

U.S. Department of Energy. DOE Guide 423.1-1, Implementation Guide for Use In Developing Technical Safety Requirements, October 2001.

U.S. Department of Energy. DOE Guide 424.1-1A, Implementation Guide for Use In Addressing Unreviewed Safety Question Requirements, July 2006.

U.S. Department of Energy. DOE G 433.1-1, Nuclear Facility Maintenance Management Program Guide, September 2001.

U.S. Department of Energy. DOE Guide 450.4-1B, Integrated Safety Management System Guide for Use with Safety Management System Policies (DOE P 450.4, DOE P 450.5, and DOE P 450.6); The Functions, Responsibilities, and Authorities Manual; and The Department of Energy Acquisition Regulation, March 2001.

U.S. Department of Energy. DOE-HDBK-1011/1-92, DOE Fundamentals Handbook, Electrical Science, volumes 1-4. June 1992.

U.S. Department of Energy. DOE-HDBK-1016/1-93, DOE Fundamentals Handbook Engineering Symbology, Prints, and Drawings, volume 1 of 2. January 1993.

U.S. Department of Energy. DOE-HDBK-1092-2004 Electrical Safety. December, 2004.

U.S. Department of Energy. DOE HDBK-1188-2006, Glossary of Environment, Safety, the Health Terms. January 2006.

U.S. Department of Energy. DOE Manual 231.1-2, Occurrence Reporting and Processing of Operations Information. August 1993.

U.S. Department of Energy. DOE Order 413.3A, Program and Project Management for the Acquisition of Capital Assets, July 2006.

U.S. Department of Energy. DOE Order 414.1A Change 1, Quality Assurance, April 2004.

U.S. Department of Energy. DOE Order 420.1B, Facility Safety. December 2005.

U.S. Department of Energy. DOE Order 430.1B, Real Property Asset Management. September 2003.

U.S. Department Of Energy. DOE Order 433.1, Maintenance Management for DOE Nuclear Facilities. June 2001.

U.S. Department of Energy. DOE Order 4330.4B, Maintenance Management Program, (Canceled). February 1994.

U.S. Department of Energy. DOE Order 5480.19, Conduct of Operations Requirements for DOE Facilities. July 1990.

U.S. Department of Energy. DOE Order 5480.20A, Personnel Selection, Qualification, and Training Requirements for DOE Nuclear Facilities. July 2001.

U.S. Department of Energy. DOE-STD-1020-2002, Natural Phenomena Hazards Design and Evaluation Criteria for Department of Energy Facilities. January 2002.

U.S. Department of Energy. DOE-STD-1021-93, Natural Phenomena Hazards Performance Categorization Guidelines for Structures, Systems, and Components. July 1993.

U.S. Department of Energy. DOE-STD-1022-94, Natural Phenomena Hazards Characterization Criteria. March 1994.

U.S. Department of Energy. DOE-STD-1023-95, Natural Phenomena Hazards Assessment Criteria. March 1995.

U.S. Department of Energy. DOE-STD-1073-2003, Configuration Management. October 2003.

U.S. Department of Energy. DOE-STD-3009-94, Preparation Guide for U.S Department of Energy Nonreactor Nuclear Facility Documented Safety Analyses. July 1994.

U.S. Department of Energy. Energy Efficiency and Renewable Energy. April 2004.

U.S. Department of Energy. Problem Analysis and Risk Assessment Self-Study Guide. October 1996.

U.S. Department of Energy. Senior Technical Safety Manager, April 2006.

U.S. Department of the Army. Chapter 2 in TM 5-688, Foreign Voltages and Frequencies Guide. November 1999. http://www.usace.army.mil/inet/usace-docs/armytm/tm5-688/chap-2.pdf.

U.S. Nuclear Regulatory Commission. Regulatory Guide1.118, Periodic Testing of Electric Power and Protection Systems. April 1995.

U.S. Nuclear Regulatory Commission, Regulatory Guide 1.53, Application of the Single-Failure Criterion to Safety Systems, November 2003

U.S. Nuclear Regulatory Commission, Regulatory Guide 1.97, Criteria for Accident Monitoring Instrumentation for Nuclear Power Plants, June 2006.

Werninck, E. H. Electric Motor Handbook: Alternating Current Motors. New York: McGraw-Hill, 1978.

Electrical Systems

Qualification Standard

Reference Guide

November 2006