Application for Permit to Construct

and

Non-Attainment New Source Review Approval

AES SPARROWS POINT LNG TERMINAL PROJECT

600 Shipyard Road

Baltimore, MD 21219

Submitted To:

Maryland Department of the Environment

1800 Washington Boulevard

Baltimore, MD 21230

Submitted By:

AES Sparrows Point LNG, LLC

140 Professional Way

Lockport, NY 14094

Prepared By:

Haley & Aldrich

200 Town Centre Drive, Suite 2

Rochester, NY 14623-4264

January 2007

# Table Of Contents

Table Of Contents	i

1.0	Introduction	3

2.0	Project Description	5

2.1	Project Location	5

2.2	Facility Overview	5

2.3	LNG Terminal Emission Sources and Operating Assumptions	6

2.4	Estimated Facility Emissions	10

3.0	Air Quality Regulations Applicability and Compliance	11

3.1	Existing Air Quality	11

3.2	New Source Review Requirements	12

3.3	MDE Title V and State Operating Permit Requirements	17

3.4	New Source Performance Standards Requirements	17

3.5	National Emissions Standards for Hazardous Air Pollutants Requirements	18

3.6	National Emissions Standards for Hazardous Air Pollutants for Source Categories Requirements	18

3.7	Acid Rain Program Requirements and Clean Air Interstate Rule (CAIR)	19

3.8	MDE Emission Standards	20

3.9	EPA Chemical Accident Prevention Provisions and OSHA Process Safety Management	23

4.0	Control Technology Analysis	25

4.1	LAER and BACT Analysis for NOX Emissions from Hot Water Heaters	25

4.2	LAER and BACT Analysis for CO and VOC Emissions from Hot Water Heaters	35

4.3	LAER and BACT Analysis for Emissions from Emergency Engines	36

5.0	Air Quality Impact Analysis	42

5.1	Air Quality Modeling Analysis Scope and Objectives	42

5.2	Model Selection	43

5.3	Emissions and Source Parameters	44

5.4	Good Engineering Practice (GEP) Stack Height Analysis	45

5.5	Meteorological Data and Site Characteristics	46

5.6	Receptors and Terrain Data	47

5.7	Background Air Quality	48

5.8	Model Results	48

5.9	Cumulative Impacts Analysis	49

5.10	Cooling Tower Impact Analysis	50

Figures

  - Site Location Map, AES Sparrows Point LNG, LLC

  - General Arrangement

  - USGS Site Location Map, AES Sparrows Point LNG, LLC

  - Facility Plot Plan Overview

  - Facility Plot Plan – Fabrication Building

  - Facility Plot Plan – Tank Area

  - Facility Plot Plan – Process Area

  - BPIP Model Setup, Building/Structure Identification

  - BPIP Model Setup, 3D Building Representation

  - AERMOD Model Setup Showing Buildings, Fenceline, Plant Boundary and Near-Field Receptors

  - AERMOD Model Setup Showing Polar Receptor Grid and Domain Boundaries

Tables

  - Hot Water Heaters Emissions

  - Diesel Fire Water Pump (Fresh Water) Emissions

  - Diesel Fire Water Pump (Salt Water) Emissions

  - Standby Generator Emissions

  - Vent Stack Heater Emissions

  - LNG Tanker Ship Unloading Operations Emissions – Assumptions

  - LNG Tanker Ship Unloading Operations Emissions

  - LNG Terminal Stationary Source Emissions Summary

  - National and Maryland Ambient Air Quality Standards

  - Air Quality Control Region Attainment Status

  - Representative Ambient Background Data from Monitoring Stations

  - Stack Parameters and Emission Rates for Model Input

  - Source Groups Used In Modeling Analysis

  - Building/Structure Dimensional Data

  - Sectors and Site Characteristics Used for AERMET Input

  - Representative Ambient Background Data From Monitoring Stations

  - Summary of AERMOD Modeling Results by Scenario and Model Year

  - Summary of Maximum AERMOD Impacts By Model Scenario

  - Maryland Counties Emissions Inventory (2001)

  - Comparison of Project Direct and Indirect Emissions With County Emissions Inventory

Appendices

A	Permit Application Forms

B.	State-Wide Compliance Certification

C.	Preliminary Vendor Data

D.	CD Containing Dispersion Modeling Input/Output Files

E.	Alternatives Analysis

# Introduction

AES Sparrows Point LNG, LLC (Sparrows Point LNG) proposes to construct, own, and operate a new liquefied natural gas (LNG) import, storage, and regasification terminal (LNG Terminal) at the Sparrows Point Industrial Complex situated on the Sparrows Point peninsula east of the Port of Baltimore in Maryland.  LNG will be delivered to the LNG Terminal via ship, offloaded from the ship to shoreside storage tanks, regasified on the LNG Terminal site (Terminal Site), and transported to consumers via pipeline.  The LNG Terminal will have a regasification capacity of 1.5 billion standard cubic feet of natural gas per day (bscfd), with potential to expand to 2.25 bscfd.  Regasified natural gas will be delivered to markets in the Mid-Atlantic Region and northern portions of the South Atlantic Region through an approximately 88-mile, 30-inch outside diameter natural gas pipeline (Pipeline) to be constructed and operated by Mid-Atlantic Express, LLC (Mid-Atlantic Express).  The Pipeline will extend from the LNG Terminal to interconnections with existing natural gas pipeline systems near Eagle, Pennsylvania.  Together the LNG Terminal and Pipeline projects are referred to as the Sparrows Point Project or Project.  Both AES Sparrows Point LNG and Mid-Atlantic Express (hereinafter collectively referred to as AES) are subsidiaries of The AES Corporation.  The stationary emission sources to be located at the LNG Terminal are the subject of this application for Permit to Construct (PTC) and Nonattainment New Source Review (NNSR) Approval.

The principal components of the proposed LNG Terminal include marine terminal facilities, three full-containment onshore LNG storage tanks, a vaporization system, a vapor handling system, site utilities, administrative and support buildings, instrumentation and control systems, communications and security systems, and fire protection, hazard detection and safety systems.  Potential emissions sources subject to air permitting are combustion sources necessary for the LNG regasification and sendout and for fire protection and emergency standby power generation.  These emissions sources include four installed natural gas-fired hot water heaters, a total of eight diesel reciprocating engines used for emergency fire water pumping and standby electricity generation, and a heated vent stack, which will be used to heat boil off vapors from the LNG Terminal if a power failure renders the vapor handling systems inoperable.  Although LNG ships will not be owned or operated by AES, estimated emissions from LNG ships associated solely with LNG offloading activities were also added to potential emissions from proposed LNG Terminal stationary sources for the purpose of evaluating applicability of Prevention of Significant Deterioration (PSD) and NNSR requirements.  This analysis demonstrates that potential emissions will be less than U.S. Environmental Protection Agency (EPA) Major Stationary Source thresholds for each regulated pollutant, with the exception of ozone precursor nitrogen oxide (NOX) emissions.  Therefore, the LNG Terminal will be a major source with respect to NOX emissions in an ozone nonattainment area, and will be subject to NNSR permitting requirements.  The LNG Terminal will be considered a minor source with respect to volatile organic compounds (VOCs) and all attainment pollutants and, therefore, will not be subject to NNSR for VOC or PSD review for any attainment pollutants.

AES is considering the possibility of constructing and operating a 300 megawatt (MW) combined-cycle cogeneration power plant (Power Plant) on the Terminal Site.  The Power Plant, which would provide heat to the LNG vaporizers and generate electricity for the local utility electric system, would operate in lieu of or in conjunction with the hot water heaters, depending on the operating scenario.  The Power Plant is not included in the scope of the current permit application.  However, AES understands that if it decides to construct and operate the Power Plant, it will not be considered separate from the LNG Terminal with respect to New Source Review (NSR) requirements.  The combined emissions from the LNG Terminal and Power Plant will be used for the purpose of PSD and NNSR applicability determinations even if AES receives permits for the LNG Terminal stationary sources and subsequently submits applications for the Power Plant.  If NNSR or PSD review applies with the addition of the Power Plant, all requirements will apply to LNG Terminal and Power Plant sources.  In anticipation of the potential future addition of the Power Plant, emissions limits and controls for currently proposed LNG Terminal sources have been incorporated into the design in order to meet potentially-applicable future LAER and BACT criteria.

This document serves as AES’s formal application for the required PTCs and NNSR Approval for the proposed LNG Terminal.  Section 2.0 describes the LNG Terminal, including site location, LNG Terminal overview and detailed descriptions of the stationary sources and operating assumptions used in developing potential emissions estimates.  Section 3.0 provides a detailed analysis of potentially-applicable air quality regulatory requirements and demonstrations of compliance with applicable requirements.  Section 4.0 presents the Lowest Achievable Emission Rate (LAER) control technology demonstrations and also discusses how presently-proposed controls will meet potential future LAER and Best Available Control Technology (BACT) criteria in the event that AES decides to construct and operate the Power Plant.  Although an air quality impact evaluation is not an applicable requirement of the present permit application, a summary of the dispersion modeling analysis conducted for the FERC application for Certificate of Public Necessity and Convenience is presented in Section 5.0.  Completed application forms, detailed calculations and other documentation are provided in the appendices.

# Project Description

## Project Location

The LNG Terminal will be located on an approximately 80-acre parcel within the existing Sparrows Point Industrial Complex located in Baltimore County, Maryland.  The 80-acre Terminal Site is comprised of approximately 45 acres of upland area and the remainder is a near shore riparian rights area.  The Terminal Site previously was owned and operated by Bethlehem Steel Corporation (BSC) as part of a steel manufacturing and shipbuilding facility.  BSC divided its operations and split off the portion that dealt with shipbuilding.  AES has an option to lease the Terminal Site with the current owner of the Sparrows Point Shipyard.

The Terminal Site is situated on a promontory that extends into the Chesapeake Bay east of the Port of Baltimore as shown on Figure 2-1.  More specifically, the Terminal Site is located on the Marine Channel adjacent to the Fort McHenry channel near the confluence of the Fort McHenry Channel and the Brewerton Angle.  The boundaries of the main property where the LNG Terminal will be located, including both land-side and riparian rights area, the proposed turning basin and approach channel, are shown on Figure 2-2.  Figure 2-3 depicts the location of the Terminal Site location on a USGS topographical map.

## Facility Overview

The principal components of the proposed LNG Terminal include marine terminal access and facilities, three full-containment onshore LNG storage tanks, a vaporization system, a vapor handling system, site utilities, administrative and support buildings, instrumentation and control systems, communications and security systems, and fire protection, hazard detection and safety systems.  The LNG Terminal facilities have been sited and will be designed, constructed and operated in accordance with all applicable standards and requirements established by the U.S. Department of Transportation (USDOT) (49 CFR Parts 192 and 193), the Federal Energy Regulatory Commission (FERC) (18 CFR Parts 153 and 380) and the U.S. Coast Guard (USCG) (33 CFR Parts 105, 127, 157 and 160), as well as additional standards and regulations cited in the FERC application for Certificate of Public Necessity and Convenience.

The following facility plot plans are provided, depicting the major LNG Terminal components:

- Figure 2-4	Facility Plot Plan – Overview

- Figure 2-5	Facility Plot Plan – Fabrication Building

- Figure 2-6	Facility Plot Plan – Tank Area

- Figure 2-7	Facility Plot Plan – Process Area

The LNG Terminal design regasification/sendout capacity will be 1.5 bscfd, at a maximum sendout pressure of 2,080 pounds per square inch (psig).  It is expected to operate continuously in a baseload mode of operation, and will be designed to allow the potential addition of a fourth tank and a potential expansion in vaporization and sendout capacity of up to 2.25 bscfd.  The Terminal design includes pre-investment in features and equipment, including blanked off pipe connections, to facilitate this future expansion.  If and when the time comes to pursue this expansion, AES will perform a more detailed study on the expansion case to identify changes required to the existing LNG Terminal facilities.

## LNG Terminal Emission Sources and Operating Assumptions

Emissions from operation of the LNG Terminal would primarily involve criteria pollutants and hazardous air pollutants (HAPs) from operation of the High Temperature Fluid (HTF) heating system used to provide heat to the LNG vaporizers and LNG ship auxiliary power systems used during offloading of LNG to the LNG Terminal.  Emissions will also result from operation of emergency diesel engine powered fire water pumps, a diesel engine powered standby electricity generator and other minor auxiliary combustion equipment.  This air permit application specifically addresses emissions from the following stationary sources and activities at the LNG Terminal:

- Four natural gas-fired hot water heaters, each rated at 345 MMBtu/hr

- One 375 HP diesel engine powered fire pump (freshwater)

- Six 700 HP diesel engine powered fire pumps (seawater)

- One 2 MW diesel engine powered emergency generator,

- One natural gas-fired heated vent stack rated at 5.5 MMBtu/hr, and

- LNG ship offloading operations.

- Dredged Material Recycling Facility

It should be noted that the LNG storage tanks are not considered stationary sources of air pollution subject to permitting review.  The LNG tanks are not vented and the principal components of vaporized LNG are not regulated air pollutants.  During normal terminal operation and LNG ship unloading, a boiloff gas (BOG) compression system will be used to control the BOG pressure in the storage tanks.  As discussed in section 2.3.5, boiloff vapors will be directed to the heated vent stack for safety purposes in the event that BOG compressors are inoperative due to power failure or other emergency.

### Hot Water Heaters

Four hot water heaters are proposed for installation at the LNG Terminal to provide heat required for LNG vaporization as part of the HTF heating system.  Three of the hot water heaters would normally be operated for the equivalent of up to 8,760 hours per year at up to 100 percent rated capacity with the fourth hot water heater operated in hot standby using a heating coil.  Each hot water heater would be rated at 345 million British thermal units per hour (MMBtu/hr) maximum heat input and will be fueled exclusively with natural gas.  It was assumed that there would be two catalyst malfunctions per hot water heater per year, lasting 48 hours each, resulting in uncontrolled emissions.  Furthermore, it was assumed that each hot water heater would undergo three cold iron startups per year, each lasting one hour at an average of 15 percent load before controls were effective.  This was the operating scenario used as a basis for the estimated short-term and annual potential emissions.  Table 2-1 summarizes maximum emission rates for the hot water heaters based on these assumptions.  Criteria pollutant emissions factors were based on a review of recent BACT and LAER determinations for similar types and sizes of natural gas-fired hot water heaters, and from preliminary emissions guarantees from potential vendors.  The emissions control systems would include low-NOX burners and/or flue gas recirculation for preliminary NOX control, selective catalytic reduction (SCR) for final NOX control, and oxidation catalysts for carbon monoxide (CO) and VOC control.

### 375 HP Fire Pump (Fresh Water)

The 375 HP fire pump will be diesel engine-driven and used to provide redundancy to an electric motor-driven fresh water fire pump in the event of a fire during an electrical power failure.  This system is capable of providing two hours of design flow fire water.  The assumed worst-case operating scenario for this diesel engine fire pump is 60 hours per year to conduct periodic testing and to allow for an emergency event.  Emissions were estimated based on representative engine manufacturers’ performance and emissions data for criteria pollutants other than sulfur dioxide (SO2) and on EPA AP-42 emission factors for SO2 and hazardous air pollutants.  SO2 emissions were based on diesel fuel containing a maximum 15 parts per million (ppm) sulfur content.  Short term and annual emissions rates for this engine are summarized in Table 2-2.

The Code of Maryland Regulations (COMAR) Section 26.11.02.10 provides a list of sources exempt from permitting and approval requirements.  This list includes “stationary internal combustion engines with an output less than 500 brake horsepower (373 kilowatts) and which are not used to generate electricity for sale or for peak or load shaving”.  Because the size of this fire pump will not be above the permitting/approval threshold, this unit is exempted and a permit to construct is not being sought for it.  However, its potential emissions are included in the total facility potential emissions for purposes of determining major source status.  In addition, a condition will need to be included in the NNSR Approval restricting operation of this source to 60 hours per year.

### Six 700 HP Fire Pumps (Salt Water)

The set of six 700 HP diesel engine-driven fire pumps, installed at the water's edge, will provide additional backup fire water from the Patapsco River.  These backup pumps can provide full flow to the onshore fire water system, and can also provide tank deluge flow in the event of a tank fire.  The assumed worst-case operating scenario for these diesel engine fire pumps is 60 hours per year to conduct periodic testing and to allow for an emergency event.  Emissions were estimated based on representative engine manufacturers’ performance and emissions data for criteria pollutants other than SO2 and on EPA AP-42 emission factors for SO2 and hazardous air pollutants.  SO2 emissions were based on diesel fuel containing a maximum 15 ppm sulfur content.  Short term and annual emissions rates for this engine are summarized in Table 2-3.

### 2 MW Emergency Generator

The 2 MW diesel engine-powered standby generator set will be used in the event of a utility power failure and will be capable of providing sufficient power to maintain LNG circulation via operation of one low pressure (LP) pump and to provide for LNG Terminal lighting, all control systems, and the operation of all other necessary auxiliary systems.  The assumed worst-case operating scenario for this diesel engine generator is 60 hours per year to conduct periodic testing and to allow for an emergency event.  Emissions were estimated based on representative engine manufacturers’ performance and emissions data for criteria pollutants other than SO2 and on EPA AP-42 emission factors for SO2 and hazardous air pollutants.  SO2 emissions were based on diesel fuel containing a maximum 15 ppm sulfur content.  Short term and annual emissions rates for this engine are summarized in Table 2-4.

### Heated Vent Stack

The boiloff gas (BOG) compression system will consist of three reciprocating type BOG compressors, two of which will be used during active LNG ship unloading.  During normal terminal operation, when no LNG ships are unloading, one BOG compressor will be needed to control the BOG pressure in the storage tanks.  If the BOG compressor is inoperative due to power failure or other emergency, the boiloff vapors will be directed to the heated vent stack for safety purposes.  Because this is a safety/emergency system, air emissions from this source will be infrequent and intermittent.  The heated vent stack will be a small (5.5 MMBtu/hr) natural gas-fired combustion source and is assumed to operate no more than 50 hours per year.  Anticipated emissions from the heated vent stack were estimated to be very low based on vendor emission factors and are summarized in Table 2-5.  However, even if this unit were operated 8,760 hours per year at maximum rated capacity, the potential emissions of each pollutant would be less than 1 ton per year (TPY).  Based on its low potential to emit, this unit would be exempt from the requirement for a permit to construct under the provisions of COMAR 26.11.02.10.

### LNG Ship Offloading Operations

As discussed in Sections 1.0 and 3.1, emissions from LNG ship offloading operations have been aggregated with potential emissions from stationary sources at the LNG Terminal for purposes of determining PSD and NNSR permit applicability.  For the purposes of conservatively estimating marine vessel emissions, the estimated annual emissions from these mobile sources are based on up to 180 LNG ship arrivals of various capacity ships; three tug boats, and two security or escort boats participating in the arrival, berthing and departure of each LNG ship; and emissions during LNG offloading and idling while stationary at berth (hoteling).  AES estimates that LNG ships will arrive at the Terminal Site with a typical frequency of two to three ships per week depending on the capacity of the ship).  Each ship will remain stationary at the berth for a maximum of 24 hours, about 12 to 18 hours of which for transferring of LNG, depending on the capacity of the ship and an average unloading rate of about 11,500 cubic meters per hour.

AES obtained information concerning the type of propulsion, power generation, fuel types, operating scenarios and other parameters necessary to estimate emissions during offloading activities at the LNG Terminal.  Based on this information, the current fleet of LNG ships (182 within AES’s design range of 125,000 to 217,000 cubic meter capacity) exclusively run on conventional steam-electric power plants for both propulsion and auxiliary power and are fueled with boil-off gas or heavy fuel oil.  AES has also determined that there are currently 117 LNG ships on order or under construction within AES’s design capacity envelope for the LNG Terminal.  These consist of 61 (52 percent) that are steam powered ships and 57 (48 percent) that are powered by slow speed or medium speed diesel engines for propulsion and auxiliary power.  The diesel engines can be fueled with low sulfur distillate (1.5 percent sulfur), heavy fuel oil (2.7 percent sulfur) or dual fuel mixtures (e.g., Marine Gas Oil (MGO), typically consisting of 90 to 95 percent gas and 5 to 10 percent low sulfur oil).  Because AES will not own or operate the LNG ships that will deliver LNG to the LNG Terminal, a number of different power plant and fuel scenarios were evaluated in order to conservatively estimate the range of emissions to be expected from LNG ship movements and transfer operations.  The scenarios evaluated ranged from natural gas fired steam-electric power plants to diesel engines firing 2.7 percent sulfur heavy fuel oil.  An assumed mix of technologies and fuels was then used to estimate annual emissions, based on AES’s evaluation of the representative levels of technologies and fuels currently in use and projected to be in use in the LNG shipping industry.  Detailed assumptions used for all calculations are summarized in Table 2-6.  AES believes these are conservative assumptions; however, the assumptions may need to be refined in the future based on actual shipping assignments and/or availability, actual ship operating conditions, and trends in the industry for the various sizes of LNG ships.  The emission estimates based on these assumptions and EPA emission factors are presented in Table 2-7.

### Dredged Material Recycling Facility (DMRF)

A dredged material recycling facility (DMRF) will also be constructed and operated at the LNG Terminal construction site, involving use of hoppers, conveyors, pug mills for mixing additives, and stacking equipment.  Pug mills and the additive delivery system will be equipped with separate baghouse dust collectors to control PM10 and PM2.5 emissions.  Marine vessels and equipment used for offshore dredging activities will include a clamshell dredge or suitable alternative required by permit, in addition to tug boats, survey/work boats, crew boats and inspecting/diving vessels.  These mobile sources are not subject to stationary source permitting requirements.

AES will use the mitigation measures to minimize the fugitive dust emissions associated with transfer of the processed dredged material (PDM) once it has been processed in the DMRF.  These measures may include the application of water or dust suppressants, covering of haul trucks, use of paved roads to the extent possible, limiting vehicle speed and stabilizing disturbed areas.

The majority of materials handled in the DMRF will be high moisture-content dredged materials with little potential for dust emissions.  Dry additive filling, storage and transfer equipment will be contained in enclosed structures with baghouse dust collectors for high-efficiency dust control.  As a result, PM2.5/PM10 emissions from the DMRF will be negligible, with uncontrolled emissions currently estimated at less than 1 TPY.  Based on estimated uncontrolled PM2.5/PM10 emissions, the DMRF additive material storage, transfer, mixing and dust control equipment would be exempt from the requirement for a permit to construct under the provisions of COMAR 26.11.02.10.

## Estimated Facility Emissions

Total LNG Terminal potential emissions based on the operating scenarios and assumptions discussed herein and calculations presented in Tables 2-1 through 2-7 are summarized below and in Table 2.8.

| Potential Emissions (tons/year) |
| --- |
| Pollutant | Hot Water Heaters | Fire Pump (Fresh Water) | 6 Fire Pumps (Salt Water) | Emergency Standby Generator | Stack Vent Heater | LNG Ship Offloading | Total LNG Terminal | Major Source Threshold |
| NOX | 18.1 | 0.1 | 1.6 | 1.3 | 0.0007 | 11.84 | 32.9 | 25 |
| CO | 34.9 | 0.009 | 0.1 | 0.1 | 0.003 | 1.8 | 37.0 | 100 |
| VOC | 18.9 | 0.002 | 0.03 | 0.03 | 0.003 | 0.30 | 19.3 | 25 |
| PM-10 | 34.2 | 0.002 | 0.009 | 0.007 | 0.001 | 0.393 | 34.6 | 100 |
| SOX | 0.5 | 0.000 | 0.00 | 0.00 | 0.001 | 3.05 | 3.6 | 100 |
| Total HAPs | 8.6 | 3.1E-04 | 1.3E-03 | 9.2E-04 | 2.6E-04 | 2.9E-02 | 8.6 | 25 |

Based on total premise emissions, and as discussed in Section 3.2, the proposed LNG Terminal will be a Major Stationary Source of ozone precursor NOX emissions and will be subject to NNSR for NOX.  The LNG Terminal will not be a Major Stationary Source with respect to any other pollutant and will, therefore, not be subject to PSD review.

# Air Quality Regulations Applicability and Compliance

Emissions from operation of the LNG Terminal would be subject to applicable federal and state air quality regulations.  This section provides a detailed evaluation of applicability of specific air regulations to emissions units and demonstrations of compliance with applicable requirements.

## Existing Air Quality

### Ambient Air Quality Standards

EPA has established primary and secondary national ambient air quality standards for certain air pollutants, including CO, lead (Pb), nitrogen dioxide (NO2), ozone, particulate matter less than 10 microns (PM10), particulate matter less than 2.5 microns (PM2.5) and SO2, which are referred to under the Clean Air Act CAA as "criteria pollutants."  National Ambient Air Quality Standards (NAAQS) have been established for each of the criteria pollutants.  Standards are designated as primary or secondary.  Primary standards are set at levels designed to protect public health.  Secondary standards are set to protect welfare values such as vegetation, visibility and property values.  States are free to adopt standards more stringent than the NAAQS.  Maryland has adopted all of the NAAQS.  Table 2-9 summarizes the NAAQS as well as the corresponding Maryland Ambient Air Quality Standards.

### Ambient Air Quality Attainment Status

The LNG Terminal is proposed to be located in Baltimore County, Maryland.  Baltimore County is contained in the Metropolitan Baltimore Intrastate Air Quality Control Region (AQCR 115).  The EPA has designated AQCR 115 as being either in attainment with the NAAQS or unclassifiable/attainment for certain criteria air pollutants, including SO2, CO, and NO2 and PM10.  With respect to the one-hour ozone (O3) standard (revoked as of June 25, 2005), AQCR 115 is classified as severe-15 non-attainment.  With respect to the new 8-hour ozone standard, AQCR 115 is classified as moderate non-attainment.  For PM2.5, AQCR 115 has been classified as non-attainment.  For Total Suspended Particulate (TSP), portions of AQCR 115 that do not include the LNG Terminal have been classified as nonattainment.  Although TSP attainment designations are listed in 40 CFR 81, there no longer are TSP NAAQS and TSP-directed State Implementation Plan (SIP) programs.  EPA revised the primary and secondary NAAQS for particulate matter on July 1, 1987 by eliminating TSP as the indicator for the NAAQS and replacing it with the PM10 indicator.  Table 2-10 summarizes the attainment status for AQCR 115.

Because AQCR 115 is classified as non-attainment with respect to the old one-hour ozone standard and had 1-hour design values greater than or equal to 0.121 ppm, it is categorized as "subpart 2" non-attainment with respect to the new 8-hour ozone standard.  As such, the AQCR is subject to specific requirements that must be incorporated into SIPs for attaining the national ozone air quality standards.  In addition, Maryland is considered part of the Ozone Transport Region (OTR).  The OTR encompasses eleven northeast states and the District of Columbia, all of which have at least some areas not meeting the NAAQS for ozone.  Because ozone attainment is a region-wide problem involving interstate transport of ozone precursors, projects locating in all areas within the OTR must meet more stringent non-attainment new source review requirements.  The applicable emissions thresholds triggering major new source review in the Metropolitan Baltimore Intrastate AQCR are 25 TPY for either VOCs or NOX.  New stationary sources with the potential to emit VOC or NOX above these thresholds would be classified as Major Stationary Sources subject to more stringent NNSR requirements.

### Existing Ambient Air Quality Monitoring Data

The Maryland Department of the Environment (MDE) monitors ambient concentrations of certain criteria pollutants at a number of monitoring stations located in the vicinity of the LNG Terminal.  The monitored data, which are available from EPA’s AirData website (http://www.epa.gov/air/data/reports.html), were evaluated to determine representative air quality levels for the area around the LNG Terminal.  Table 2-11 summarizes the most recent three-year averages of the data available from monitoring stations with the most representative locations with proximity to the LNG Terminal.  The assumptions used in developing the most representative three-year average concentrations are also detailed in Table 2-11.  The monitoring data demonstrates that all monitored pollutants are meeting the NAAQS, with the exception of one-hour and 8-hour average ozone and annual average PM2.5 concentrations in Baltimore.  The monitored 24-hour average PM2.5 concentrations in Baltimore County also exceed the recently (12/18/06) promulgated revised standard (35 µg/m3); however, the Maryland SIP will need to be revised to address NSR and other requirements related to PM2.5 attainment.

## New Source Review Requirements

The NSR provisions of the CAA apply to new Major Stationary Sources or Major Modifications to Major Stationary Sources under two separate programs.  For sources located in areas designated as attaining the Ambient Air Quality Standards, with respect to a specific regulated criteria pollutant, the requirements of the PSD program (40 CFR § 52.21) apply.  For Major Stationary Sources located in areas that do not attain the Ambient Air Quality Standards, the requirements of the NNSR Program (40 CFR Parts 51 and 52) apply to each non-attainment pollutant.  The LNG Terminal will involve construction and operation of a new stationary source in Maryland.  Evaluation of the applicability of NSR regulations to these sources is discussed below.  Administration of NSR programs in Maryland is provided by MDE’s SIP-approved regulations promulgated under COMAR Section 26.11 with respect to the LNG Terminal.

As discussed in Section 1.0 and 2.3.6, for the purposes of the Major Stationary Source applicability determinations under PSD and NNSR rules, total potential emissions associated with operation of the LNG Terminal are assumed to include the combination of emissions from stationary emission units at the LNG Terminal with those emissions from LNG ships associated solely with LNG offloading activities while the LNG ships are at berth.  The offloading activities are included in the major source applicability determination because the transferring of fuels from LNG ships is directly connected to the function of the LNG Terminal.  This conservative approach was taken because this procedure is consistent with EPA guidance provided in the 1990 Draft New Source Review Workshop Manual as well as several EPA policy documents on this subject.

### PSD Requirements

MDE’s approved SIP provides the authority to issue air permits in accordance with federal PSD regulations (40 CFR § 52.21), which are designed to ensure that the air quality in current attainment areas does not significantly deteriorate beyond baseline concentration levels.  The PSD regulations specifically apply to the construction of EPA-defined Major Stationary Sources and Major Modifications to existing Major Stationary Sources in areas designated as attainment for at least one of the following criteria pollutants: SO2, NO2, PM10, CO, O3, and Pb.  In addition, pursuant to EPA’s proposed implementation of PM2.5 standards, states are in the process of developing SIP revisions that would include applicability and review criteria for PM2.5 emissions.  In the meantime, EPA guidance to the states is to utilize the PM10 requirements as a surrogate for PM2.5.  For PSD purposes, a Major Stationary Source is defined as one of 28 listed source categories with the potential to emit 100 TPY or more of any pollutant regulated under the CAA.  A non-listed Major Stationary Source is defined as a source with the potential to emit 250 TPY or more of any regulated pollutant.  PSD applies on a pollutant-specific basis at Major Stationary Sources for each pollutant with the potential to be emitted at greater than EPA-defined Significant Emission Rates: 100 TPY CO; 40 TPY NOX, SO2 or VOC; 25 TPY TSP; 15 TPY PM10; 0.6 TPY Pb.  For PM2.5, EPA has proposed to apply a Significant Emission Rate of 10 TPY of direct PM2.5 emissions and 40 TPY of precursor SO2 emissions.  If other precursors are included for determination of major source applicability to PM2.5, a 40 TPY Significant Emission Rate would be used for precursor NO2 emissions and other Significant Emission Rate thresholds may apply to precursor VOC and ammonia emissions, as determined by the state’s SIP.

Based on the attainment status of the area (see Section 3.1.2) and on projected emission levels (see Section 2.4), the LNG Terminal will not be considered a Major Stationary Source with respect to the PSD regulations and is not subject to PSD review, regardless of whether the 100 TPY or 250 TPY applicability threshold is determined to apply (i.e., potential emissions of all attainment pollutants are below 100 TPY).  However, if AES decides to construct and operate the Power Plant, it would be subject to PSD review for NO2 and CO if the 100 TPY threshold applies, but would not be subject to PSD review if the 250 TPY threshold is determined to apply in this case.  AES is in the process of contacting EPA and MDE to further evaluate PSD applicability to the Power Plant and to request a formal determination.  If AES decides to construct and operate the Power Plant, it will apply for the appropriate permits, as necessary, based on the outcome of that discussion.

If PSD review is triggered, all stationary sources at the premise must demonstrate compliance with PSD requirements for each pollutant with potential premises emissions above Significant Emission Rates.  AES understands that, if it decides to construct and operate the Power Plant, it will not be considered separate from the LNG Terminal with respect to NSR requirements.  Even if AES applies for and receives permits for the LNG Terminal stationary sources and subsequently submits applications for the Power Plant, the combined emissions from the LNG Terminal and Power Plant will be used for the purpose of PSD and NNSR applicability determinations.  If PSD review applies, all requirements will apply to LNG Terminal and Power Plant sources.

PSD review for Major Stationary Sources and Major Modifications includes the following: an assessment of the existing air quality; the use of analytic dispersion models to demonstrate compliance with the NAAQS and applicable PSD Increments; a demonstration that BACT has been applied to the subject emission sources; and an assessment of the impact of new emissions on the environmental resources such as soils and vegetation.  If the source is located within 100 kilometers (km) (62 miles) of a federal Class I area, the impacts must be evaluated at these areas based on the more stringent Class I PSD increments.  The PSD permit would contain emission limits and other operating, monitoring, record keeping, and reporting requirements.

The air quality modeling includes emissions from the proposed Major Stationary Source or Major Modification and other sources in the area to ensure protection of the NAAQS and to prevent emission increases beyond a specified amount, called a PSD Increment.  Because the LNG Terminal and associated LNG ship unloading operations, without the Power Plant, will not be a Major Stationary Source subject to PSD review, an air quality modeling demonstration is not required by MDE or EPA PSD regulations specifically for that LNG Terminal configuration.  However, if it is determined that the 100 TPY PSD applicability threshold applies to the Power Plant, the Power Plant will trigger PSD review for the Power Plant and the LNG Terminal sources, including the air quality modeling demonstrations.  In that case, the results of the air quality dispersion modeling analysis demonstrating compliance with the NAAQS and PSD Increments will be included in the PSD permit application submitted to the Maryland Public Service Commission (MPSC) for review by that agency with input from MDE (see Section 3.2.3).  If AES proceeds with the Power Plant option, the PSD permit application for the Power Plant will be submitted to MPSC.

Separate from the potentially applicable PSD modeling requirements, AES completed an air quality modeling analysis for both LNG Terminal options (with and without the Power Plant) to satisfy the FERC Staff’s interpretation of its obligation under National Environmental Policy Act (NEPA) to evaluate anticipated air quality impacts for the Project (see Section 5.0).  This modeling analysis includes an analysis of impacts from the LNG Terminal with and without the Power Plant, and includes impacts from LNG ship offloading operations.  Separate model runs were also performed to evaluate impacts of marine vessels associated with LNG ship movements in the Project Area.

The emission limits contained in the PSD permit are required to represent the BACT.  BACT is determined on a case-by-case basis, taking into account energy, environmental, and economic impacts and costs.  The LNG Terminal is not currently subject to PSD review or BACT requirements.  However, if AES elects to construct and operate the Power Plant, the LNG Terminal sources will be subject to PSD review, including BACT.  Based on a review of previous BACT and LAER determinations for other boiler and hot water heater equipment, the proposed controls and emission limits for the LNG Terminal are considered representative of BACT (see Section 4.0).

The PSD program was designed to protect air quality in areas where existing air quality was considerably better than the NAAQS.  The program established a set of increments of new air pollution that would be allowed over a baseline level for three classes of areas.  Class I areas are areas of special national or regional value from a natural, scenic, recreational, or historic perspective and include such areas as National Parks, Fish and Wildlife Service Areas and National Wilderness Areas.  In addition to restrictive Class I PSD increments for SO2, PM and NO2, select Class I areas were additionally protected through adoption of visibility protection requirements.   For a project meeting the PSD regulatory definition of a Major Stationary Source or Major Modification and with emission source(s) typically located within 100 km (62 miles) of a Class I area, an impact analysis must be performed to demonstrate that stringent Class I PSD increments will not be exceeded and that other air quality related values (AQRVs) are not adversely impacted.  The LNG Terminal is not currently subject to PSD review.  However, the nearest PSD Class I areas to the LNG Terminal site were identified as the Shenandoah National Park in Virginia (about 145 km southwest of the LNG Terminal and Power Plant) and Brigantine National Wilderness Area in southeastern New Jersey (about 193 km east of the site).  The LNG Terminal would be located more than 100 km (62 miles) from the nearest Class I area and, as such, a Class I area impact analysis would not be automatically triggered in this case.  However, as part of the PSD review process (if the Power Plant will be subject to PSD review), the MDE will likely provide information on the LNG Terminal’s estimated emissions and impacts to the Federal Land Manager responsible for overseeing the nearest Class I areas.

### Non-attainment New Source Review Requirements

The CAA established more stringent provisions for NSR of Major Stationary Sources proposed to be located in non-attainment areas.  MDE regulations implementing those provisions are codified in COMAR 26.11.17.  Because the LNG Terminal and Power Plant will be located in Baltimore and the Baltimore AQCR has been designated as nonattainment with respect to certain criteria air pollutants, the LNG Terminal is potentially subject to certain NNSR requirements if potential emissions of NOX or VOC will be greater than 25 TPY.  In addition, the MDE may establish requirements under NNSR for emissions of PM-2.5, for which the Baltimore AQCR also has been classified as non-attainment.

Based on the attainment status of the area (see 3.1.2) and on projected emission levels (see Section 2.4), the LNG Terminal will be subject to NNSR for NOX.  Applicable NNSR permitting requirements would include an emission limitation that represents LAER for the source, obtaining NOX equivalent emission reductions (offsets) from existing sources in the area in the ratio of 1.3 to 1 for sources located in Baltimore (although the one-hour standard has been rescinded at the federal level, the area continues to be subject to the severe nonattainment rules in Maryland’s approved SIP, COMAR 26.11.17.03.B(3)(a)), and an alternatives analysis to demonstrate that the benefits of the proposed source significantly outweigh the environmental and social impacts.  The control technology analysis demonstrating compliance with LAER is provided in Section 4.0.  A detailed alternatives analysis fulfilling the NNSR requirements is provided in Resource Report 10 to the FERC application for a Certificate of Public Necessity and Convenience.  A formal filing of Resource Report 10 has been submitted to FERC on January 8, 2007 of which a copy was provided to the MDE.

### State Permit to Construct Requirements

Pursuant to COMAR 26.11.02.09, all air pollution sources subject to PSD, NNSR, NSPS, and National Emissions Standards for Hazardous Air Pollutants (NESHAPS) requirements and all other sources, except those specifically exempted in COMAR 26.11.02.10, are required to apply for and obtain a permit to construct.  Maryland is authorized by EPA through its approved SIP to implement both the PSD and NNSR programs.  Therefore, in addition to the permit to construct, sources subject to PSD and/or NNSR are required to obtain additional PSD and NNSR permits, called Approvals.  The purpose of the permit to construct is to ensure that any new, modified, replaced or relocated source of air pollution complies with all applicable State and federal air quality regulatory requirements.  The NNSR and PSD Approvals are required to enforce applicable PSD and NNSR requirements.  Therefore, the four hot water heaters, six emergency fire water pumps and emergency generator at the LNG Terminal will require permits to construct.

As discussed in Sections 2.3.2 and 2.3.5, the 375 HP diesel engine fire pump and the natural gas fired vent stack heater are exempt from the necessity to apply for permits to construct.  The 375 HP diesel engine fire pump will have a rated output less than 500 brake horsepower (373 kilowatts) and will not be used to generate electricity for sale or for peak or load shaving.  Based on operation of the vent stack heater at maximum rated capacity for 8,760 hours per year, potential emissions of each pollutant would be less than 1 TPY.  Therefore, each of these minor sources meet the permit exemption criteria in COMAR 26.11.02.10.

If AES elects to construct and operate the Power Plant, which will be rated at greater than 70 MW, it will be subject to review by the MPSC.  In that case, AES will be required to apply for a Certificate of Public Convenience and Necessity from the MPSC, which includes a review of the Power Plant’s potential air impacts instead of pursuing its air permit approvals via the MDE.  The MPSC has been authorized and SIP-approved to issue PSD and NNSR Approvals, with MDE input, for all power plants in Maryland with a generating capacity greater than 70 MW.

## MDE Title V and State Operating Permit Requirements

Under MDE’s Title V Facility Permit regulations (COMAR 26.11.03), a Title V permit is required for Major Stationary Sources (as defined under COMAR 26.11.02.01).  For Title V applicability purposes, a Major Stationary Source is defined differently than a Major Stationary Source under PSD review, with potential emissions thresholds established at 10 TPY for any individual HAP, 25 TPY for any combination of HAPs, 25 TPY for NOX or VOC in Baltimore and 100 TPY for any other regulated air pollutant.  Based on the estimated potential emissions from the LNG Terminal as presented in Section 2.4, the LNG Terminal will be a Major Stationary Source subject to Title V permitting.  The owner or operator of a source that becomes subject to the requirement to obtain a Part 70 permit must submit an application not later than 12 months after the date that the source commences operations or becomes subject to the requirements for a Part 70 permit, whichever is later (COMAR 26.11.03.02.B(4)).  The purpose of the Title V operating permit is to combine, into a single document, all the State and federal air quality requirements applicable to all sources located on the same premise.  Title V does not impose new substantive requirements above and beyond the State requirements.

## New Source Performance Standards Requirements

As natural gas-fired hot water heaters with heat inputs greater than 100 MMBtu/hr, the four proposed heaters at the LNG Terminal are subject to Standards of Performance for Industrial-Commercial-Institutional Steam Generating Units (NSPS, 40 CFR Part 60, Subpart Db).  Although Subpart Db contains emissions standards and/or control requirements for SO2 and PM from boilers combusting coal, oil, wood and other fuels, it contains no SO2 or PM standards applicable to natural gas fired boilers.  The most stringent Subpart Db NOX emission standard applicable to gas fired boilers with a low heat release rate is 0.1 pounds per million British thermal unit (lb/MMBtu).  The hot water heaters associated with the LNG Terminal will be designed and operated in accordance with the applicable Subpart Db NOX emission standard.  The proposed NOX emission rate (less than 0.004 lb/MMBtu) would easily meet the applicable emission standard.  AES will also comply with the applicable monitoring, record keeping and reporting requirements consistent with Subpart Db.

If AES elects to construct and operate the Power Plant, the proposed combustion turbine generator (CTG) would have a heat input greater than 10 MMBtu/hr and would be constructed after February 18, 2005.  Therefore, the CTG and associated heat recovery steam generator (HRSG) would be subject to Standards of Performance for Stationary Combustion Turbines (Subpart KKKK), which were promulgated July 6, 2006 and are applicable to CTGs with a heat load input greater than or equal to 10 MMBtu/hr and were constructed, modified or reconstructed after February 18, 2005.  Stationary CTGs subject to Subpart KKKK are exempt from requirements of Subpart GG, which is applicable to combustion turbines constructed, modified, or reconstructed after October 3, 1977.  In addition, HRSGs subject to Subpart KKKK are exempt from the requirements in Subparts Da, Db and Dc.  Subpart KKKK sets emission limits for NOX and SO2.  For new CTGs firing natural gas at a heat input rate of greater than 850 MMBtu/hr, such as the CTG preliminarily designed for the Power Plant, the applicable NOX emission limit would be 15 ppmvd at 15 percent O2.  The proposed NOX emission limit, which will also be proposed to meet BACT and LAER, is two ppmvd at 15 percent O2 and, therefore, the CTG will easily meet the applicable limit in Subpart KKKK.  The continuous emission monitoring system (CEMS) proposed for the Power Plant would also comply with the Subpart KKKK NOX monitoring requirements.  The Subpart KKKK SO2 limit applicable to all CTGs regardless of size or fuel type is 0.58 lb/MWh gross energy output or fuel sulfur content of 0.05 percent by weight.  The proposed CTG with HRSG would be fueled exclusively with natural gas, and will meet the fuel sulfur content specification.

Subpart Kb, Standards of Performance for Volatile Organic Liquid Storage Vessels (Including Petroleum Liquid Storage Vessels) for Which Construction, Reconstruction, or Modification Commenced After July 23, 1984, was reviewed for applicability to the LNG storage tanks at the LNG Terminal.  This subpart applies to storage vessels above 75 cubic meters capacity used to store Volatile Organic Liquids (VOL).  VOL is defined as any organic liquid that can emit VOC as defined in 40 CFR § 51.100.  The principal organic compounds with the potential to be emitted only in trace amounts from LNG storage tanks are methane and ethane, both of which are specifically exempted in 40 CFR § 51.100 from the definition of VOC.  Therefore, this subpart is not applicable to the LNG storage tanks.

Subpart IIII, Standards of Performance for Stationary Compression Ignition Internal Combustion Engines, promulgated July 11, 2006, will apply to emergency fire pump engines and the emergency standby generator proposed for the LNG Terminal.  The rule requires manufacturers of such engines to meet emission standards that are phased in for the size, type of engine application and model year of the engine.  Owners and operators of covered engines are required to configure, operate and maintain the engines according to specifications and instructions provided by the engine manufacturer and to maintain records demonstrating compliance.  AES will comply with the requirements applicable to owners and operators of covered engines.

## National Emissions Standards for Hazardous Air Pollutants Requirements

The NESHAPs, codified in 40 CFR Part 61, regulate HAP emissions. Part 61 was promulgated prior to the 1990 CAAA and regulates only eight types of hazardous substances (asbestos, benzene, beryllium, coke oven emissions, inorganic arsenic, mercury, radionuclides, and vinyl chloride).  The proposed LNG Terminal and Power Plant do not fall under one of the source categories regulated by Part 61; therefore, the requirements of Part 61 are not applicable to the LNG Terminal.

## National Emissions Standards for Hazardous Air Pollutants for Source Categories Requirements

Boilers and process heaters that are located at new or existing Major Stationary Sources of HAPs must meet NESHAPs for Source Categories, Subpart DDDDD - National Emission Standards for Industrial / Commercial / Institutional Boilers and Process Heaters, commonly referred to as Boiler Maximum Achievable Control Technology (MACT) standards.  Subpart DDDDD emission limitations applicable to “large” (greater than 10 MMBtu/hr) gas fired boilers and process heaters include PM (0.03 lb/MMBtu), hydrogen chloride (0.0009 lb/MMBtu) and CO (400 ppm at three percent O2).  The hot water heaters at the LNG Terminal would be classified as a large boiler or process heater under the regulations and estimated emissions would easily comply with these limitations based on vendor data and/or EPA emissions factors as summarized in Table 2-1.  The HRSG at the potential Power Plant would be classified as a waste heat boiler, which is not subject to the regulation, because the supplemental burners to the HRSG would not be 50 percent or more of the total heat input to the HRSG based on preliminary engineering design.  Based on estimated potential emissions of federal HAPs summarized in Table 2-8, the LNG Terminal would not be classified as a Major Stationary Source of HAPs (i.e., those that have the potential to emit 10 TPY or more of a single HAP or 25 TPY or more of a combination of HAPs that are specifically listed in or pursuant to section 112(b) of the CAA).  Therefore, the proposed LNG Terminal will not be subject to Subpart DDDDD.

Other NESHAPs for Source Categories, or MACT standards, potentially applicable to LNG Terminal stationary sources include Subpart ZZZZ (NESHAP for Stationary Reciprocating Internal Combustion Engines) and Subpart YYYY (NESHAP for Stationary Combustion Turbines, if the Power Plant is constructed).  Both of these NESHAPs are only applicable to Major Stationary Sources of HAPs.  Based on estimated potential HAP emissions, neither the proposed LNG Terminal nor the Power Plant will be Major Stationary Sources of HAPs.  Therefore, these NESHAPs do not apply to the LNG Terminal.  Moreover, with regard to Subpart YYYY, based on EPA’s August 18, 2004 stay of effectiveness with regard to applicability of this NESHAP to lean premix gas-fired turbines and diffusion flame gas-fired turbines, Subpart YYYY would not apply to the CTG proposed for the Power Plant, as the proposed CTG will be a lean premix dry low-NOX design.

## Acid Rain Program Requirements and Clean Air Interstate Rule (CAIR)

The Acid Rain Program is codified in 40 CFR Parts 72 through 78.  This program aims to reduce acid rain by reduction of SO2 and NOX from utility units that have a nameplate electricity generation capacity greater than 25 MW.  A “unit” is defined as a “fossil fuel-fired combustion device” and “fossil fuel-fired” is defined as “the combustion of fossil fuel, alone or in combination with any other fuel, independent of the percentage of fossil fuel consumed in any calendar year”.  The hot water heaters at the LNG Terminal will not be used to generate electricity; however, the combined cycle Power Plant, if constructed, would have a generation capacity greater than 25 MW and will be subject to Acid Rain program requirements.  If the Power Plant is constructed, the Acid Rain permit application must be filed at least 24 months before the unit commences operation.  An affected unit is required to follow the continuous emissions monitoring requirements of 40 CFR Part 75 and to hold sufficient SO2 allowances to cover expected emissions of SO2 when operation commences.  In the event that the Power Plant is constructed, AES would apply for the Acid Rain Permits; install, certify and operate the required monitoring systems; and comply with the required emissions allowances, monitoring, and reordkeeping requirements.

The Clean Air Interstate Rule (CAIR), 40 CFR Parts 96 and 97, established a new cap and trade program for SO2 and NOX emissions across 28 eastern states and the District of Columbia.  The CAIR requires certain states, including Maryland, to achieve significant, phased reductions in annual and ozone-season NOx emissions (as a precursor to fine particulate matter (PM2.5) and ozone formation) and annual SO2 emissions (as a precursor to PM2.5 formation), consistent with state-specific emissions budgets established by EPA.  To achieve those reductions, affected states may choose to participate, to the extent applicable, in cap and trade programs for annual NOx, ozone-season NOx and annual SO2 emissions. Affected states must submit to EPA proposed revisions to its State Implementation Plan (SIP) that include the requisite NOx and SO2 emissions reductions and specify the CAIR-affected sources and control mechanisms that will be required by the state.  Alternatively, affected states may elect to adopt the CAIR Federal Implementation Plan (FIP), meaning that EPA would administer the CAIR program for that state.  Because the State of Maryland has not yet submitted its CAIR SIP to EPA for review and approval or indicated its intention to adopt the CAIR FIP, it is not yet clear how the State will comply with the rule and whether the emissions reduction requirements will apply to sources other than coal-fired electric generating units.  However, if AES proceeds with construction of the Power Plant, AES will comply with any CAIR requirements that may be applicable to the natural gas-fired units at the plant.

The Clean Air Mercury Rule (CAMR) establishes standards of performance for new and existing coal-fired electric generating units pursuant to Section 111(d) of the CAA.  CAMR sets annual caps for mercury emissions from such units and creates a market-based trading program. States were required to submit SIP revisions to EPA by November 17, 2006, to implement the obligations under CAMR.  Many states, including Maryland, failed to meet the SIP submittal deadline and it is not yet clear whether Maryland will develop a state plan to adopt the CAMR or will become subject to the CAMR FIP, which was published by EPA on December 8, 2006.  Under either scenario, the State's CAMR program is not anticipated to apply to new, natural gas-fired electric generating units, such as the units that would be installed at the Power Plant, if constructed.

## MDE Emission Standards

In addition to the MDE permit to construct, permit to operate and PSD and NNSR Approval requirements, the following state emission standards and other requirements were evaluated for applicability to the LNG Terminal sources:

- COMAR 26.11.05:  Air Pollution Episode System – This chapter requires sources designated by the Secretary or the Secretary's designee to submit standby emission reduction plans and to implement such plans if a designated level of air pollution is reached.  Designated sources primarily include coal and oil fired electric power generating facilities, coal and oil fired steam producing facilities, large manufacturing industries and refuse incinerators.  Any other source of air pollutants not specifically designated in the regulation may be required to submit standby plans, upon written request of the MDE, describing emission cutbacks to be taken if an air pollution Alert is called.  Because the LNG Terminal and Power Plant do not involve emission sources specifically designated by regulation to prepare and submit standby plans, AES would not be subject to this requirement unless specifically requested by MDE.

- COMAR 26.11.06:  General Emission Standards, Prohibitions and Restrictions – This chapter contains emissions standards and other requirements applicable to certain air pollution sources.  Specific requirements pertain to visible emissions, emissions of particulate matter, CO, SO2, VOC and fluorides, and to odors and other nuisance air pollution.  The proposed hot water heaters, diesel engines and vent stack heater at the LNG Terminal and the CTG with HRSG at the Power Plant will be designed to meet all applicable standards and operate in compliance with applicable limitations.

- COMAR 26.11.06.03.D:  Particulate Matter from Materials Handling and Construction. This regulation requires reasonable precautions to prevent particulate matter from becoming airborne due to material handling, transport, or storage, or due to construction or demolition activities, use of roads and other activities.  Reasonable precautions specified in the regulation include, but are not be limited to:

  - Use of water or chemicals for control of dust in the demolition of existing buildings or structures, construction operations, the grading of roads, or the clearing of land.

  - Application of asphalt, oil, water, or suitable chemicals on dirt roads, materials stockpiles, and other surfaces that can create airborne dusts.

  - Installation and use of hoods, fans, and dust collectors to enclose and vent the handling of dusty materials. Adequate containment methods shall be employed during sandblasting of buildings or other similar operations.

  - Covering, at all times when in motion, open-bodied vehicles transporting materials likely to create air pollution. Alternate means may be employed to achieve the same results as would covering the vehicles.

  - The paving of roadways and their maintenance in clean condition.

  - The prompt removal from paved streets of earth or other material which has been transported there by trucks or earth moving equipment or erosion by water.

AES will require its contractors to use the mitigation measures to minimize the fugitive dust emissions associated with construction of the Project.  These measures may include the application of water or dust suppressants, covering of haul trucks, use of paved roads to the extent possible, limiting vehicle speed and stabilizing disturbed areas.

- COMAR 26.11.09:  Control of Fuel-Burning Equipment, Stationary Internal Combustion Engines, and Certain Fuel-burning Installations – This chapter contains emissions standards and other requirements applicable to certain fuel-burning equipment, including boilers, vent heater, and diesel engines at the LNG Terminal, and the CTG with HRSG at the potential Power Plant.  Specific requirements pertain to visible emissions, emissions of particulate matter, SO2 and Major Stationary Sources of NOX.  The proposed combustion equipment at the LNG Terminal and Power Plant will be designed to meet all applicable standards and operate in compliance with applicable limitations.

- COMAR 26.11.15 and 26.11.16:  Toxic Air Pollutants – Fuel burning equipment as defined in COMAR 26.11.09.01, such as boilers and stationary internal combustion engines associated with the LNG Terminal and the CTG with HRSG associated with the Power Plant, are exempt from the requirements of this chapter.

- COMAR 26.11.17:  Requirements for Major New Sources and Modifications – This chapter applies to Major Stationary Sources and Major Modifications with respect to non-attainment pollutants NOX, VOC and CO.  Based on estimated potential emissions from the LNG Terminal emission units, the requirements of this chapter apply to NOX, as the LNG Terminal will be a Major Stationary Source of NOX emissions when LNG ship offloading emissions are included.  The LNG Terminal, even with offloading emissions, will not be a Major Stationary Source of VOC emissions and, therefore, will not be subject to the requirements of this chapter for VOC.  In addition, the LNG Terminal will not be located in a non-attainment area for CO.  However, based on estimated potential emissions, the LNG Terminal with the Power Plant, and including LNG offloading emissions, will be a Major Stationary Source of NOX and VOC and, therefore, will be subject to the NNSR requirements in this chapter.  The applicable requirements for sources subject to NNSR are summarized in section 9.2.3.1.2.

- COMAR 26.11.29 and 26.11.30:  NOX Reduction and Trading Program – These chapters apply to affected trading sources, which are defined as fossil fuel fired electric generating units that serve a generator with a name plate capacity greater than 25 MW or non-electric generating units that have a maximum design heat input greater than 250 MMBtu/hr.  The proposed hot water heaters at the LNG Terminal are fossil fuel fired stationary boilers with a maximum design heat input of 345 MMBtu/hr and are, therefore, classified as non-electric generating units subject to the requirements.  The CTG with HRSG at the proposed Power Plant would be a fossil fuel fired electric generating unit that would serve a generator with a name plate capacity of approximately 300 MW and will sell electricity.  Therefore, the combined cycle Power Plant would also be subject to Maryland’s NOX Reduction and Trading Program.  In general, COMAR 26.11.29 requires an affected trading source to acquire sufficient NOX allowances for the control period each year at least equal to the affected trading source’s NOX emissions for the control period.  Allowances from a “set-aside pool” are made available by the MDE to accommodate new affected trading sources or “clean air projects”, defined as a new or modified fossil fuel electric generator with state-of-the-art NOX controls demonstrated to be more efficient than existing electric generation.  An affected trading source must also install, operate, maintain, and certify a NOx CEM or other approved monitoring method in accordance with 40 CFR Part 75, Subpart H and comply with the monitoring requirements in 40 CFR Part 96, Subpart H.  COMAR 26.11.30 is referenced throughout Chapter 26.11.29 and establishes procedural requirements to implement Maryland’s NOX Reduction and Trading Program.  The proposed hot water heaters at the LNG Terminal and combined cycle Power Plant will be designed to meet all applicable standards and operate in compliance with applicable monitoring and NOX emissions trading requirements.

## EPA Chemical Accident Prevention Provisions and OSHA Process Safety Management

40 CFR Part 68, Chemical Accident Prevention Provisions, are Federal regulations designed to prevent the release of hazardous materials in the event of an accident and minimize impacts when releases do occur.  The regulation contains a list of substances and threshold quantities for determining applicability of the rule to a facility.  If a facility stores, handles or processes one or more substances on this list and at a quantity equal or greater than specified in the regulation, the facility must prepare and submit a risk management plan (RMP).  If a facility does not have a listed substance on-site, or the quantity of a listed substance is below the applicability threshold, the facility is not required to prepare an RMP.  However, it still must comply with requirements of the general duty provisions in Section 112(r)(1) of the 1990 CAAA if it has any regulated substance of other extremely hazardous substance on-site.  The general duty of the provision is as follows:

“The owners and operators of stationary sources producing, processing, handling and storing such substances have a general duty to identify hazards which may result from such releases using appropriate hazard assessment techniques, to design and maintain a safe facility taking such steps as are necessary to prevent releases, and to minimize the consequences of accidental releases which do occur.”

With the exception of natural gas constituents (e.g., methane, ethane, propane, etc.), no regulated substance would be handled or stored in quantities greater than the applicability threshold.  Natural gas pipelines are not covered if they are regulated by the USDOT or an equivalent state natural gas program certified by USDOT in accordance with 49 U.S.C § 60105.  In addition, storage of natural gas incidental to transportation (e.g., gas taken from a pipeline during non-peak periods and placed in storage, then returned to the pipeline when needed) is not covered.  Consequently, an RMP is not required for any portion of the Project.  AES would be required to maintain awareness of hazard issues and meet the goals of the above-listed general duty provisions.

The applicability of the Occupational Safety and Health Administration (OSHA) standard 29 CFR 1910.119, Process Safety Management of Highly Hazardous Chemicals (PSM), to the Project was also evaluated.  Based on standard interpretations published by OSHA in response to questions on PSM applicability to LNG facilities, OSHA has concluded that current USDOT regulations in 49 CFR Parts 192 and 193 and enforced by the Pipeline and Hazardous Materials Safety Administration cover LNG and gas transmission and distribution processes, and that OSHA is precluded from enforcing the PSM standard with respect to working conditions associated with fire and explosion hazards of these processes.  Therefore, the Pipeline and LNG Terminal, which are subject to 49 CFR Parts 192 and 193, respectively, are not subject to the PSM regulations.

# Control Technology Analysis

## LAER and BACT Analysis for NOX Emissions from Hot Water Heaters

The LNG Terminal will be subject to LAER for NOX because estimated potential emissions of NOX will be greater than the 25 TPY Major Stationary Source threshold applicable to an O3 precursor in a serious O3 nonattainment area.  LAER, as defined in 40 CFR 51.165(a)(1)(xiii) is the most stringent emissions limitation that is contained in the implementation plan of any State for such class or category of stationary source, unless the owner or operator of the proposed stationary source demonstrates that such limitations are not achievable; or the most stringent emissions limitation that is achieved in practice by such class or category of stationary sources.  This section demonstrates that the proposed NOX emissions and controls meet the requirements of LAER.  In addition, because LAER requirements are at least as stringent as BACT and BACT would potentially apply to NOX emissions from the LNG Terminal, if AES elects to construct and operate the Power Plant, the LAER analysis also satisfies the BACT demonstration for NOX.

### Estimated Emissions and Minimum Regulatory Requirements

AES is proposing a NOX emission rate of 0.004 lb/MMBtu, to be achieved with low-NOX burners and/or flue gas recirculation for preliminary NOX control and selective non-catalytic reduction (SCR) technology for final NOX control.  The remainder of this section will demonstrate that the proposed emission rate and controls meet both LAER and BACT requirements.

Table 4-1 summarizes the minimum EPA and MDE regulatory limits applicable to NOX emissions from gas-fired boiler projects:

Table 4-1 – Regulatory Limits Applicable to NOX Emissions

| Pollutant/Parameter | Regulatory Limit | Citation |
| --- | --- | --- |
| NOX | 0.20 lb/MMBtu | NSPS – 40 CFR 60.44b(a)(1) |
| NOX | 0.20 lb/MMBtu | COMAR § 26.11.09.08(B)(1)(c) |

There are no other specific EPA or MDE emissions standards applicable to NOX emissions from combustion sources.

### Identification of NOX Control Technologies

Based on a review of currently permitted boilers identified in the EPA’s RACT/BACT/LAER Clearinghouse (RBLC), California Air Resources Board Statewide BACT Clearinghouse, and a literature review of NOX controls for gas-fired boilers and heaters, the following NOX control technologies were identified as potentially applicable to the hot water (HW) heaters:

- Low Excess Air (LEA)

- Overfire Air (OA)

- Flue Gas Recirculation (FGR)

- Low-NOX Burners (LNB)

- Selective Catalytic Reduction (SCR)

- Selective Non-Catalytic Reduction (SNCR)

The following subsections provide brief overviews of these technologies.

#### Low Excess Air

When fuel is combusted, the fuel molecules combine with oxygen molecules and release energy in the form of heat.  In order to ensure that all of the fuel is combusted, more oxygen is supplied to the combustion chamber than necessary; this is known as excess air.  With LEA systems, less excess air is supplied to the burners than normal.  This reduces the temperature of the flame, and thus lowers the amount of thermal NOX created.  Additionally, more of the fuel-bound NOX becomes nitrogen gas, further reducing NOX levels.  LEA requires continuous monitoring of oxygen levels in the fuel gas to ensure that oxygen levels are within a narrow range.

#### Overfire Air

In this method of NOX control, the initial combustion is performed with less than the required amount of oxygen at the burners, then the remaining required air is added shortly downstream.  This staged combustion process reduces thermal NOX by lowering the flame temperature, and keeps the oxygen levels low and reduces mixing to minimize fuel NOX.  However, this tends to result in more incomplete combustion, resulting in higher CO and hydrocarbon emissions.

#### Flue Gas Recirculation

In flue gas recirculation, a portion of the cooled flue gas is combined with the fresh air entering the combustion zone.  Since most of the oxygen in the flue gas has been used in the original combustion, recirculating a portion of the flue gas reduces the oxygen available to the combustion process.  This reduces the temperature and lowers thermal NOX.  Typically, 5 percent to 20 percent of the gas is recirculated.

#### Low-NOX Burners

Low-NOX burners work under the same principle as overfire air, except that the staging is performed at the burner rather than later in the combustion chamber.  This staging can be achieved as either staged air or staged fuel.  Each of these technologies requires two combustion zones.

#### Selective Catalytic Reduction (SCR)

SCR is a flue-gas treatment technology for reducing NOX that involves injection of ammonia (NH3), a reducing agent, into the flue gas downstream of the boilers and then passing the gas through a catalyst bed.  It is one of the most effective ways to control NOX with a control efficiency up to about 90 percent.  In the SCR process, ammonia injected into the exhaust gas reacts with nitrogen oxides and oxygen to form nitrogen and water by the following reactions:

4NO + 4NH3 +O2 → 4N2 + 6H2O			(1)

6NO + 4NH3 → 5N2 + 6H2O				(2)

2NO2 + 4NH3 + O2 → 3N2 + 6H2O			(3)

6NO2 + 8NH3 → 7N2 + 12H2O			(4)

NO + NO2 + 2NH3 → 2N2 + 3H2O			(5)

The reactions take place on the surface of a catalyst.  The function of the catalyst is to effectively lower the activation energy of the NOX decomposition reaction and accelerate the reduction of NOX by ammonia to nitrogen gas and water.  Several different catalyst compositions having different properties are available. The catalyst also has a low activity level for other potentially competing reactions such as ammonia or sulfur dioxide oxidation.  The reaction of NOX and ammonia is temperature dependent, and each catalyst has its own operating range, or "temperature window".

The upper temperature boundary is a function of the physical properties of the catalyst used and different catalysts cover the range from 500˚F to over 1000˚F.  In addition, at temperatures greater than 900˚F, the ammonia is reported to thermally decompose to form NOX.  This decomposition does not appear to be a significant problem up to at least 960˚F.

Control of ammonia injection is an important parameter for an SCR system.  Ammonia is injected in proportion to the amount of NOX in the gas stream.  A molar ratio of 1.0 to 1.3 is typically used, depending upon the degree of control and final effluent NOX concentration required.  NOX is measured either upstream of the system (feed-forward controls) or downstream of the system (feedback controls), depending upon the supplier's system, and multiplied by a gas flow signal to adjust the ammonia injection rate.  Some systems are equipped with an ammonia analyzer downstream of the SCR system so that escape of ammonia ("ammonia slip") can be monitored.  These analyzers are usually part of a feedback control system that will reduce the ammonia injection rate in the event of unacceptable slip.

Sulfur content of the fuel can be a concern for systems that employ SCR.  If burning pipeline quality natural gas, the low sulfur content (less than 2 grains per 100 SCF) should allow for a reasonable catalyst life.  However, higher sulfur contents can cause the catalyst systems to promote partial oxidation of sulfur dioxide (from trace sulfur in gas) to sulfur trioxide (SO3), which combines with water to form sulfuric acid.  At lower temperatures, SO3 and sulfuric acid may react with excess ammonia to form ammonium salts.  These ammonium salts may be emitted from the stack as increased emissions of PM10 and PM2.5.  Sulfates and nitrates emitted from the stack are also precursors to atmospheric formation of PM10 and PM2.5.  Under some circumstances, fouling may eventually lead to increased system pressure drop over time and decreased heat transfer efficiencies.  Fortunately, ammonium salts may be removed by water washing, although this process requires an outage to allow cooling, washing and restart of the system.

The SCR process in general is subject to catalyst deactivation over time.  Catalyst deactivation occurs through two primary mechanisms: physical deactivation and chemical poisoning.  Physical deactivation is the result either of prolonged exposure to excessive temperatures or masking of the catalyst due to entrainment of particulate from ambient air or internal contaminants.  Chemical poisoning is caused by the irreversible reaction of the catalyst with a contaminant in the gas stream and is a permanent condition.  Catalyst suppliers typically only guarantee a 3-year lifetime for very low emission level, high performance catalyst systems.

The potential environmental impacts associated with the use of SCR are summarized below:

- Some unreacted ammonia would be emitted to the atmosphere as ammonia slip; ammonia is a PM10 and PM2.5 precursor; and

- There are safety issues associated with the transportation, handling, and storage of aqueous ammonia.  Aqueous ammonia is typically used in lieu of anhydrous ammonia to alleviate these concerns.

#### Selective Non-Catalytic Reduction

In the SNCR process, either ammonia or urea is injected into the post-combustion zone of the furnace to react directly with the NOX in the flue gas.  This process does not include a catalyst, and thus the temperature of the gas must be higher than that required for SCR.  Required temperatures generally range between 1,600˚F to 2,000˚F with residence times of one second or more; however, effective reduction has been achieved in some units with temperatures as low as 800˚F when additional proprietary flue gas additives are utilized.  Below these temperatures, the reaction rate of ammonia and NOX to nitrogen gas and water slows to ineffective levels, resulting in both high NOX emission levels and ammonia emissions.

Molar ammonia injection rates must be carefully controlled so that there is enough ammonia to effectively reduce NOX levels, but not so much that significant levels of ammonia are emitted from the stack.  In some cases, an SCR is installed downstream of the SNCR installation to capture excess ammonia/urea slip and remaining NOX.  Reduction of NOX by SNCR can approach 70 percent control efficiencies.

### Identification of Most Stringent SIP Limitation in Any State

The first step in a LAER analysis requires identification of the most stringent emissions limitation that is contained in the SIP of any State for such class or category of stationary source.  States that contain the most severe O3 nonattainment areas typically contain the most stringent NOX limits in their SIPs.  Therefore, the NOX control rules potentially applicable to steam generating units and power plants fired with natural gas were reviewed and summarized for the following states and/or Air Quality Control Management Districts (AQMD) comprising the major O3 nonattainment areas in the US:

Table 4-2 – NOX SIP Limitations In Other Nonattainment States

| State or AQMD | Regulatory Limit | Citation |
| --- | --- | --- |
| Bay Area AQMD, CA | 30 ppmvd @ 3% O2 for gaseous fuel-fired electric power steam generating boiler < 1,500 MMBtu/hr (equivalent to 0.04 lb/MMBtu) | BAAQMD Regulation 9, Rule 11, 9-11-305 |
| San Joaquin Valley Unified AQMD | 9 ppmvd @ 3% O2 (0.011 lb/MMBtu) for standard option; 6 ppmvd @ 3% O2 (0.007 lb/MMBtu) for enhanced option | SJVUAQMD Rule 4306, Boilers, Steam Generators and Process Heaters – Phase 3 |
| Texas Commission on Environmental Quality | 0.030 lb/MMBtu | Chapter 117 – Control of Air Pollution from Nitrogen Compounds §117.106 |
| New Jersey Department of Environmental Protection | 0.20 lb/MMBtu for gas-fired boilers serving electric generating units | New Jersey Administrative Code, Title 7:27-19.4 |
| Massachusetts Department of Environmental Protection | 0.20 lb/MMBtu, for large boilers (100+ MMBtu/hr) burning only gas | 310 CMR 7.19 – Reasonably Available Control Technology for Sources of Nitrogen Oxides |
| New York State Department of Environmental Conservation | 0.20 lb/MMBtu for large or very large boilers burning gas only | 6NYCRR, Chapter III, Part 227: Stationary Combustion Installations, Subpart 227-2 - Reasonably Available Control Technology (RACT) for Oxides of Nitrogen (NOx) |
| Connecticut Department of Environmental Protection | 0.20 lb/MMBtu for a gas-fired boiler rated at 5 MMBtu/hr or more at a Major Stationary Source of NOX | RCSA 22a-174-22 Control of Nitrogen Oxides Emissions |
| Pennsylvania Department of Environmental Protection | 0.10 lb/MMBtu for a gas-fired boiler rated between 100 and 250 MMBtu/hr; 0.17 lb/MMBtu for a boiler rated at or above 250 MMBtu/hr | Title 25 of the PA Code, Subpart C, Article III Air Resources § 129.201. Additional NOX Requirements for Boilers |
| Delaware Department of Natural Resources and Environmental Control | 0.20 lb/MMBtu for gas-fired fuel-burning equipment rated at 100 MMBtu/hr or more located at a Major Stationary Source of NOX | Regulation 12 – Control of Nitrogen Oxides Emissions |
| Illinois Environmental Protection Agency | 0.20 lb/MMBtu for new gas-fired fuel-burning sources rated at 250 MMBtu/hr or more | Title 35, Illinois Administrative Code, Subtitle B, Chapter I, Subchapter C, Part 217 – Nitrogen Oxides Emissions |

The most stringent NOX emission limitation applicable to gas-fired boilers identified from this review of SIPs comprising the most severe O3 nonattainment areas was 0.007 lb/MMBtu (6 ppmvd @ 3 percent O2).  The AES proposed NOX emission limit for the HW heaters is 0.004 lb/MMBtu (3 ppmvd @ 3 percent O2), which is more stringent than the most stringent SIP limitation found.

### Most Stringent Emission Limitation Achieved In Practice

The next step in a LAER analysis requires the identification of the most stringent emission limitation achieved in practice for the same class or category of stationary source proposed.  The same procedure used for identifying the “top” case for pollutants subject to BACT was used to identify the most stringent NOX limit achieved in practice for a large gas-fired boiler.  Specifically, the following sources were used to identify the most stringent emission limitation:

- Review of EPA's RACT/BACT/LAER Clearinghouse; and

- Review of the California Air Resources Board Statewide BACT Clearinghouse.

Information compiled from the data gathering efforts pertaining to NOX controls and permit limits for large gas-fired boilers are summarized in Table 4-3.  The most stringent NOX emission rate identified is 0.004 lb/MMBtu.  This emission rate is associated with a permit issued in 2002 for four 350 MMBtu/hr boilers located at Sunoco, Inc.’s Eagle Point Refinery in New Jersey.  The emission rate was achieved with the combination of low-NOX burners, flue gas recirculation and SCR, which is the same control strategy proposed here for the AES HW heaters.

Table 4-3 – Summary of NOX Control Technology Determinations and Permit Limits for Large Gas-fired Boilers

| Project Name | Location | Size | Fuel description | Date initially permitted / In-service date | Nitrogen Oxides | Ammonia Slip |
| --- | --- | --- | --- | --- | --- | --- |
|  | City | State | MW total | MMBtu /hr each unit |  |  | Limit (lb/ MMBtu) | Avg. Period | Controls | Limit (lb/ MMBtu) |
| Arizona Clean Fuels Yuma | Tacna | AZ | 101 | 346.0 | Natural Gas or Refinery Fuel Gas | 4/14/2005 | 0.0125 | 3-hour rolling average | LNB, SCR | 0.0019 |
| Arizona Clean Fuels Yuma | Tacna | AZ | 91 | 311.0 | Refinery Fuel Gas or Natural Gas | 4/14/2005 | 0.0125 | 3-hour average | LNB, SCR | 0.0019 |
| Arizona Clean Fuels Yuma | Tacna | AZ | 96 | 328.0 | Refinery Fuel Gas or Natural Gas | 4/14/2005 | 0.0125 | 3-hour average | LNB, SCR | 0.0019 |
| Arizona Clean Fuels Yuma | Tacna | AZ | 245 | 419.0 | Natural Gas | 4/14/2005 | 0.0125 | 3-hour average | FGR, LNB | N/A |
| Genentech, Inc. | South San Francisco | CA | 28 | 97 | Natural Gas | permit date not listed, startup date 6-14-2006 | 0.0109 | Three 30-min sampling periods | ULNB | N/A |
| Amerada Hess - Sea Robin Gas Processing Plant | Venice | LA | 106 | 363.0 | Natural Gas | 9/8/2005 | 0.04 | Annual average | FGR, LNB | N/A |
| BP Cherry Point Refinery | Blaine | WA | 106 | 363.0 | Natural Gas | 4/20/2005 | 0.028 | calculated | FGR, ULNB | N/A |
| AES Huntington Beach | Huntington Beach | CA | 225 (output) | 2088 | Natural Gas | 7/27/2004 | 0.0061 | 1-hour | LNB, FGR, SCR | 0.0022 |
| Sunoco Inc. | Franklin Furnace | OH | 82 | 281.0 | Natural Gas | 7/27/2004 | 0.08 |  | LNB, FGR | N/A |
| Cargill - Blair Plant | Blair | NE | 81 | 276.7 | Natural Gas | 6/22/2004 | 0.05 | 30-day average | LNB, induced FGR @ 16% | N/A |
| Midamerican Energy Company | Council Bluffs | IA | 126 | 429.4 | Natural Gas | 6/17/2003 | 0.14 |  | LNB | N/A |
| Sunoco Inc., Eagle Point Refinery | Westville | NJ |  | 350 | Refinery Fuel Gas or Jet A Fuel | 2002 | 0.004 |  | LNB, FGR, SCR | ?? |
| Dow Texas Operations Freeport | Freeport | TX | 448 | 382.0 | Natural Gas, and Gas Mix | 11/26/2002 | 0.02 |  | LNB, SCR | 0.004 |
| VA Power - Possum Point | Glen Allen | VA | 29 | 99 | Natural Gas | 11/18/2002 | 0.036 |  | LNB, low-NOx fuel | N/A |
| Weyerhaeuser Company | Pine Hill | AL | 88 | 300.0 | Natural Gas | 11/15/2002 | 0.05 |  | LNB | N/A |
| Huntsman Polymers - Odessa Petrochemical Plant | Odessa | TX | 108 | 370.0 | Natural Gas | 10/24/2002 | 0.05 |  | Only gaseous fuels, DLNC, FGR | N/A |
| Huntsman Polymers - Odessa Petrochemical Plant | Odessa | TX | 94 | 320.0 | Natural Gas | 10/24/2002 | 0.12 | calculated | None | N/A |
| Conoco - Lake Charles Refinery | Westlake | LA | 78 | 268.0 | Gaseous Fuel/Gaseous Fuel Mixtures | 9/20/2002 | 0.06 |  | LNB, external FGR | N/A |
| Conoco - Lake Charles Refinery | Westlake | LA | 122 | 418.0 | Gaseous Fuel/Gaseous Fuel Mixtures | 9/20/2002 | 0.03 | calculated | ULNB | N/A |
| ExxonMobil - Baton Rouge Refinery | Baton Rouge | LA | 105 | 360.0 | Gaseous Fuel/Gaseous Fuel Mixtures | 4/26/2002 | 0.04 | calculated | ULNB | N/A |
| Liberty Generating Station | Linden | NJ | 225 | 256.0 | Natural Gas | 3/28/2002 | 0.2 |  | SCR |  |
| Liberty Generating Station | Linden | NJ | 59 | 200 | Natural Gas | 3/28/2002 | 0.036 |  | SCR |  |
| Lyondell - Citgo Refining, LP | Houston | TX | 66 | 226.4 | Gaseous Fuel/Gaseous Fuel Mixtures | 3/14/2002 | 0.036 | calculated | SCR | 0.004 |
| Lyondell - Citgo Refining, LP | Houston | TX | 107 | 366.8 | Gaseous Fuel/Gaseous Fuel Mixtures | 3/14/2002 | 0.08 | calculated | None | N/A |
| Agritechnology Montana LLC | Great Falls | MT | 105 | 358.0 | Natural Gas | 11/6/2001 | 0.08 |  | FGR, LNB | N/A |
| FPL Energy Marcus Hook, L.P. | Marcus Hook | PA | 1845 | 1575 | Natural Gas | 5/4/2001 | 0.05 |  | GCP | N/A |
| Grays Ferry Cogen Partnership | Philadelphia | PA | 328 | 1119 | Natural Gas | 3/21/2001 | 0.1 |  | LNB | N/A |
| Kal Kan Foods, Inc. | Los Angeles | CA | 23 | 78.6 | Natural Gas | 6/28/1995 | 0.0109 | 15-min | LNB, SCR | 0.009 |
| Darling International, Inc. | Los Angeles | CA | 32 | 110 | Natural Gas or Propane | 12/7/1993 | operating: 0.0109 during startup: 0.0486 | 15-min | LNB, FGR, SCR | 0.009 |

### LAER and BACT Proposal for NOX Emissions

Based on the results of this analysis, a NOX permit limit of 0.004 lb/MMBtu is proposed as LAER for the HW heaters at the LNG Terminal.  AES proposes to achieve this emission rate with the combination of LNB and/or FGR and SCR.  The 0.004 lb/MMBtu emission rate meets EPA’s LAER criteria by being more stringent than the most stringent emission limit contained in any State SIP and it is equivalent to the most stringent emission rate achieved in practice for a large gas-fired boiler.  If AES elects to construct and operate the Power Plant, NOX emissions from the HW heaters may potentially be subject to BACT in addition to LAER requirements.  In that case, becayse LAER is, by definition, more stringent than BACT, the proposed NOX limit is also demonstrated as BACT.

## LAER and BACT Analysis for CO and VOC Emissions from Hot Water Heaters

As discussed in Section 2.4, the LNG Terminal as currently proposed will be a Major Stationary Source only for NOX emissions and will not be subject to NNSR for VOC or PSD review for any attainment pollutant.  However, in the event that AES elects to construct and operate the Power Plant at the Terminal Site, the entire LNG Terminal, including the sources that are the subject of this permit application package, could potentially be classified as a Major Stationary Source for NOX, VOC and CO emissions.  In that case, all LNG Terminal with Power Plant emission sources will be subject to NNSR for NOX and VOC and PSD review for NO2 and CO.  Accordingly, LAER determinations would need to be made for NOX and VOC and BACT determinations would need to be made for NO2 and CO.  Because by definition, LAER is more stringent than BACT, the LAER determination proposed for NOX in this application would meet the BACT requirements for NO2.  In addition, oxidation catalysts for control of CO and VOC emissions from the HW heaters are currently proposed in order to meet potentially-applicable future LAER criteria for VOC and BACT criteria for CO.  This section provides documentation in support of this determination.

### Identification of CO Control Technologies

CO is formed as a result of incomplete combustion of fuel.  Providing adequate fuel residence time and high temperature in the combustion device to ensure complete combustion can minimize CO emissions.  However, these combustion techniques can sometimes increase NOX emissions.  Conversely, a low NOX emission rate achieved by flame temperature control can result in higher CO emissions.  Therefore, a compromise must be reached whereby the flame temperature reduction is set to achieve the lowest NOX emission rate possible while maintaining CO emission rates at acceptable levels.

There are two basic techniques for controlling CO emissions from combustion units:  good combustion practices and add-on oxidation catalysts.  “Good combustion practices” is the predominant control technique used for minimizing CO emissions from natural gas-fired boilers and heaters, although more recent installations have included the use of oxidation catalysts.

Good combustion practices are intended to control the parameters that affect the formation of CO.  Optimizing the excess air, flame temperature, residence time at flame temperature, combustion zone design, and turbulence result in reduced CO formation.  Combustion controls have no additional environmental impacts, do not result in increased emissions of other pollutants, and incur no additional cost for the combustion equipment.

A CO oxidation catalyst is an add-on control option in which the catalyst is placed in the exhaust stream generally in the range of 700°F to 1,100°F.  At lower temperatures, CO conversion efficiency falls off rapidly.  Above 1200°F catalyst sintering may occur, thus causing permanent damage to the catalyst.  Within the context of a BACT analysis, a CO oxidation catalyst is considered the “top” control technology for CO emissions from fossil fuel fired sources.

AES proposes to install an oxidation catalyst on each of the four HW heaters to reduce CO emissions to achieve emission rates that will satisfy BACT requirements.  The oxidation catalyst will reduce CO emissions to a level of 10 ppmvd, which is equivalent to 0.0074 lb/MMBtu.  Based on a review of recent determinations listed in EPA’s RBLC, as documented in Table 4-4, this is consistent with the low rates required of recently permitted large boilers and water heaters.

### Identification of VOC Control Technologies

VOC emissions are also formed as a result of incomplete combustion of fuel.  The same principles that apply to CO control also apply to VOC control (although the quantity of VOC generated is smaller than CO).  Formation of VOC can be minimized by providing adequate fuel residence time and high temperatures, but these conditions can increase NOX emissions.  Because the same types of controls are effective at reducing VOC emissions as CO emissions, the controls described in the BACT analysis for CO are relevant for VOC control as well.  As such, the control proposed for CO – an oxidation catalyst – will reduce the concentration of VOC to 10 ppmvd @ 3% O2, which is equivalent to 0.0042 lb/MMBtu (as methane).

VOC emission rates and controls from recently permitted units were reviewed (see Table 4-5).  The proposed emissions rate of 0.0042 lb/MMBtu and use of an oxidation catalyst is consistent with the lowest VOC levels achieved.

## LAER and BACT Analysis for Emissions from Emergency Engines

AES is proposing to install one 375 HP and six 700 HP diesel engine emergency fire pumps and a 2 MW diesel engine emergency generator to provide fire protection and auxiliary backup power, respectively, to the LNG Terminal in the event that a fire or electricity transmission line outage occurs during a power interuption.  These engines are expected to operate for less than 60 hours per year only for emergency situations and engine testing purposes.  Based on manufacturer’s data, at 60 hours per year of operation, total potential emissions of NOX from the eight emergency engines will be less than 3 TPY and CO will be limited to 0.22 TPY.  All other pollutants will be emitted at much less than 1 TPY.

Control techniques for diesel engines are primarily directed at NOX and CO emissions as they are the primary pollutants from these engines.  Available controls for diesel engines include parametric controls, such as adjustment of ignition timing, air-to-fuel ratio and derating, and post-combustion controls, such as SCR and nonselective catalytic reduction (NSCR).  These controls are applied in base-load applications where engines are operated primarily at high capacity for extended periods of time for industrial and power generation purposes.  However, based upon a review of EPA’s RBLC and other sources, no specific controls were identified for diesel engines operating less than 100 hours per year only for emergency operation purposes.  Cost-effectiveness, evaluated on a cost per ton of pollutant controlled, would be unreasonably high for any of the add-on controls in this application.  In addition, add-on controls such as SCR are not technically feasible in applications requiring quick start-ups and short operating durations.

In summary, no specific controls are proposed for the diesel emergency fire pumps and generator.  Limiting the diesel engines to 60 hours per year of operation only for emergency and engine testing purposes is proposed to meet BACT and LAER requirements.

Table 4-4 - Summary of CO Control Technology Determinations and Permit Limits for Large Gas-fired Boilers

| Project Name | State | Size | Fuel description | Date initially permitted / In-service date | Nitrogen Oxides |
| --- | --- | --- | --- | --- | --- |
|  |  | MW total | MMBtu /hr each unit |  |  | Limit (lb/ MMBtu) | Avg. Period | Controls |
| Genentech, Inc. | CA | 28 | 97 | Natural Gas | permit date not listed, startup date 6-14-2006 | 0.0370 | three 30-min sampling periods | ULNB |
| BP Cherry Point Refinery | WA | 106 | 363.0 | Natural Gas | 4/20/2005 | 0.05 |  | GCP |
| Arizona Clean Fuels Yuma | AZ | 101 | 346.0 | Natural Gas or Refinery Fuel Gas | 4/14/2005 | 0.04 | 3-hr rolling average | None |
| Arizona Clean Fuels Yuma | AZ | 91 | 311.0 | Refinery Fuel Gas or Natural Gas | 4/14/2005 | 0.04 | 3-hr rolling average | None |
| Arizona Clean Fuels Yuma | AZ | 96 | 328.0 | Refinery Fuel Gas or Natural Gas | 4/14/2005 | 0.04 | 3-hr rolling average | None |
| Arizona Clean Fuels Yuma | AZ | 245 | 419.0 | Natural Gas | 4/14/2005 | 0.016 | 3-hr rolling average | None |
| AES Huntington Beach | CA | 225 (output) | 2088 | Natural Gas | 7/27/2004 | 0.0037 | 1-hr (source test) 24-hr (CEMS) | oxidation catalyst |
| Sunoco Inc. | OH | 82 | 281.0 | Natural Gas | 7/27/2004 | 0.076 |  | None |
| Cargill - Blair Plant | NE | 81 | 276.7 | Natural Gas | 6/22/2004 | 0.14 |  | GCP |
| Midamerican Energy Company | IA | 126 | 429.4 | Natural Gas | 6/17/2003 | 0.084 |  | GCP |
| VA Power - Possum Point | VA | 29 | 99 | Natural Gas | 11/18/2002 | 0.15 |  | GCP |
| Weyerhaeuser Company | AL | 88 | 300.0 | Natural Gas | 11/15/2002 | 0.1 |  | None |
| Huntsman Polymers - Odessa Petrochemical Plant | TX | 108 | 370.0 | Natural Gas | 10/24/2002 | 0.065 |  | GCP |
| Huntsman Polymers - Odessa Petrochemical Plant | TX | 94 | 320.0 | Natural Gas | 10/24/2002 | 0.084 |  | None |
| Liberty Generating Station | NJ | 225 | 256.0 | Natural Gas | 3/28/2002 | 0.0956 |  | CO Catalyst |
| Liberty Generating Station | NJ | 59 | 200 | Natural Gas | 3/28/2002 | 0.087 |  | CO Catalyst |
| Agritechnology Montana LLC | MT | 105 | 358.0 | Natural Gas | 11/6/2001 | 0.05 |  | GCP |
| FPL Energy Marcus Hook, L.P. | PA | 1845 | 1575 | Natural Gas | 5/4/2001 | 0.075 |  | GCP |
| Grays Ferry Cogen Partnership | PA | 328 | 1119 | Natural Gas | 3/21/2001 | 0.04 |  | GCP |
| Kal Kan Foods, Inc. | CA | 23 | 78.6 | Natural Gas | 6/28/1995 | 0.2960 | 15-min | SCR |
| Darling International, Inc. | CA | 32 | 110 | Natural Gas or Propane | 12/7/1993 | 0.0740 | 15-min | "add-on" but no description |

Table 4-5 - Summary of VOC Control Technology Determinations and Permit Limits for Large Gas-fired Boilers

| Project Name | State | Size | Fuel description | Date initially permitted / In-service date | Nitrogen Oxides |
| --- | --- | --- | --- | --- | --- |
|  |  | MW total | MMBtu /hr each unit |  |  | Limit (lb/ MMBtu) | Avg. Period | Controls |
| Sunoco Inc. | OH | 82 | 281.0 | Natural Gas | 7/27/2004 | 0.005 |  | None |
| Mid-American Energy Company | IA | 126 | 429.4 | Natural Gas | 6/17/2003 | 0.0055 |  | GCP |
| VA Power - Possum Point | VA | 29 | 99 | Natural Gas | 11/18/2002 | 0.004 |  | GCP |
| Weyerhaeuser Company | AL | 88 | 300.0 | Natural Gas | 11/15/2002 | 0.01 |  | None |
| Huntsman Polymers - Odessa Petrochemical Plant | TX | 108 | 370.0 | Natural Gas | 10/24/2002 | 0.004 |  | GCP |
| Huntsman Polymers - Odessa Petrochemical Plant | TX | 94 | 320.0 | Natural Gas | 10/24/2002 | 0.007 |  | None |
| Liberty Generating Station | NJ | 225 | 256.0 | Natural Gas | 3/28/2002 | 0.2 |  | CO Catalyst |
| Liberty Generating Station | NJ | 59 | 200 | Natural Gas | 3/28/2002 | 0.036 |  | CO Catalyst |
| FPL Energy Marcus Hook, L.P. | PA | 1845 | 1575 | Natural Gas | 5/4/2001 | 0.004 |  | None |
| Grays Ferry Cogen Partnership | PA | 328 | 1119 | Natural Gas | 3/21/2001 | 0.005 |  | GCP |

# Air Quality Impact Analysis

Although PSD review is not applicable to the proposed LNG Terminal, an air quality modeling analysis was performed as part of the FERC application for Certificate of Public Necessity and Convenience to satisfy the FERC Staff’s interpretation of its obligation under NEPA to evaluate potential air quality impacts associated with the Project.  This modeling analysis includes an evaluation of impacts from the LNG Terminal with and without the potential future Power Plant, and a cumulative analysis of impacts from the LNG Terminal, including LNG ship offloading operations.  Separate model runs were also performed to evaluate the combined effects of the LNG Terminal and Power Plant scenarios with LNG ship offloading, hoteling operations and marine vessels associated with LNG ship movements in the vicinity of the LNG Terminal and along the LNG ship transit route, specifically assist tugs and USCG security and patrol boats within the security zone.  The modeling assumptions, procedures and results are summarized in this section.  A compact disk containing all modeling input and output files is also provided in Appendix D.  In the event that AES decides to construct and operate the Power Plant and will be required to perform an air quality impact analysis satisfying all requirements for PSD review, AES will perform the required PSD modeling analyses and submit a detailed modeling report as part of the permit application to the MPSC and MDE.

## Air Quality Modeling Analysis Scope and Objectives

Atmospheric dispersion modeling was performed to evaluate impacts to air quality due to operation of the LNG Terminal.  The modeling was conducted in accordance with objectives and procedures to satisfy NEPA impact assessment criteria, as discussed in several teleconferences with the FERC Staff.  In addition, modeling guidance and meteorological input data were obtained through consultation with MDNR’s subcontractor, Environmental Resources Management, Inc. (ERM), responsible for review of air quality impact analyses under MPSC’s consolidated licensing program for power plants.

Based on the consultation with the FERC Staff, three distinct scenarios were modeled for each of the LNG Terminal operating phase options (i.e., with and without the Power Plant):

(Option 1) Without Power Plant:

- LNG Terminal emission sources only

- LNG Terminal emission sources plus LNG ship offloading emissions

- LNG Terminal emission sources, LNG ship offloading plus all other marine vessels within the security zone

(Option 2) With Power Plant:

- LNG Terminal and Power Plant emission sources only

- LNG Terminal and Power Plant emission sources plus LNG ship offloading emissions

- LNG Terminal and Power Plant emission sources, LNG ship offloading plus all other marine vessels within the security zone

The scenarios were identified in this manner consistent with FERC Staff’s interpretation of its obligation under NEPA to evaluate potential impacts from both primary and secondary emission sources associated with the LNG Terminal.  FERC Staff further advised that the secondary mobile emission sources included in the modeling should be geographically limited from the turning basin to the berth and include emissions from all LNG ship transit, maneuvering, and hoteling operations and assist tugs, security and patrol vessel operations in this restricted area.  Because the USCG has not yet determined the preliminary extent of the security zone, it was assumed for the purposes of the modeling analysis that it would be defined by a minimum radius of 500 yards from the LNG ship berth.  In addition, the USCG will establish a security zone around each LNG ship while it is in transit.  For purposes of the modeling analysis and determining the LNG Terminal “fenceline” for restricted public access, this security zone was conservatively assumed to extend 500 yards from each side of the LNG ship.  If the security zone ultimately established by the USCG is greater than these assumptions, it would reduce the impacts at LNG Terminal fenceline receptors.  Similarly, if the security zone ultimately established by the USCG is less than these assumptions, it would increase the impacts at fenceline receptors.

Further following FERC Staff guidance to comply with NEPA impact assessment requirements, the modeled impacts were first compared to EPA PSD Significant Impact Levels (SILs).  If maximum predicted impacts are predicted to be less than the applicable SILs, FERC Staff presumes that the source will not cause or significantly contribute to a PSD Increment or NAAQS violation and no further impact assessment is required.  If the predicted impacts are greater than SILs, then maximum impacts are added to representative ambient background concentrations and evaluated for compliance with the NAAQS.  In addition, if predicted impacts are greater than SILs, FERC Staff has advised AES that it must complete a qualitative cumulative impact analysis by comparing potential emissions from the Project and other new or reasonably foreseeable projects in the region with regional emission inventories.

## Model Selection

AERMOD (Version 04300), incorporating Plume Rise Model Enhancement (PRIME) downwash algorithms was used in the refined modeling analyses for simple and elevated terrain.  The AERMOD model was run using the Lakes Environmental ISC-AERMOD View (version 5.4.0) interface for EPA’s ISC and AERMOD models.  AERMOD is an EPA-approved refined dispersion model for evaluating impacts of land-based stationary sources.  AERMOD with PRME is one of the listed refined dispersion models in EPA’s Guideline on Air Quality Models (40 CFR Part 51 Appendix W, November 2005) that are required to be used for SIP revisions for existing sources and for NSR and PSD programs.

AERMOD with PRIME (Plume Rise Model Enhancement) includes improved building downwash algorithms capable of modeling receptors in both the near-building wake (cavity) and far-building wake regions.  The PRIME algorithm takes into account the distance from each building or structure to potentially affected sources in that building’s region of influence.  The inclusion of the cavity predictions within AERMOD removes a modeling discontinuity that existed with AERMOD without the PRIME algorithm and obviates the need for additional cavity impact analysis using the SCREEN3 or other calculation procedures.

Default AERMOD control options used in the modeling analysis consistent with EPA recommendations include the following:

- Final plume rise at all receptors

- Stack-tip downwash

- Buoyancy-induced dispersion

- Calm wind processing routine

- Default wind profile exponents

- Default vertical potential temperature gradients

## Emissions and Source Parameters

The emissions and operating scenarios of all sources included in the modeling analysis are described in Section 2.0.  The specific primary and secondary (mobile marine vessel) emission sources associated with the LNG Terminal, LNG ships and nonjurisdictional Power Plant are summarized as follows:

LNG Terminal

- Four hot water heaters

- One Fresh water emergency diesel engine fire pump

- Six salt water emergency diesel engine fire pumps

- One emergency diesel engine standby generator

- One heated vent stack

- LNG ship offloading operations

Marine Vessels Associated with LNG Ships

- LNG ship hoteling operations at berth and in security zone

- Three assist tug boats in security zone

- Two security and patrol boats in security zone

Non-Jurisdictional Power Plant

- One combined cycle combustion turbine with heat recovery steam generator (CTG/HRSG)

- One cooling tower

Detailed assumptions and calculations used to develop emission rates, operating scenarios and other stack parameters are provided for each of the emission sources in Tables 2-1 through 2.7.  Table 5-1 summarizes the emissions and source parameters used for AERMOD input.

Different source groups were set up in the model in order to predict impacts for each of the modeling scenarios identified in Section 5.1 for each of the LNG Terminal options (with and without the Power Plant).  These source groups are identified in Table 5-2.  The source identification numbers (IDs) listed in the table correspond to the stack numbers identified in Table 5-1.  Additional notes and conservative assumptions used in the modeling are also summarized in Table 5-2.  For example, worst-case operating assumptions for the HW heaters and CTG assume air pollution control system malfunction conditions in one of the hot water heaters for short-term average emission rates and startup conditions are factored into the annual emission rates.  With respect to the CTG/HRSG, the worst-case short-term emission rates from the two CTG manufacturers under consideration were used as model input.  In addition, worst-case emissions are based on continuous operation of the CTG and HRSG at 100 percent load at an ambient temperature of -7ºF.  In the event that AES decides to construct and operate the Power Plant and it is determined to be subject to PSD review, an analysis of impacts over a range of operating loads and ambient temperatures will be conducted as part of the PSD modeling analysis in order to verify the worst-case impact scenario.

## Good Engineering Practice (GEP) Stack Height Analysis

Building and structure dimensional data for the GEP stack height, cavity and downwash analyses are summarized in Table 5-3.  The dimensional data for all significant buildings/structures as well as the layout and orientations on site are based on the site plan and general arrangement plans presented in Figures 2-4 through 2-7 and also in Resource Report 13, Engineering and Design Manual, of the FERC application for Certificate of Public Necessity and Convenience.  In addition, typical dimensions of LNG ships for input to the models were obtained from plan and elevation drawings and photographs of a range of actual LNG ships currently in use.  For purposes of the modeling analyses, two LNG ships were assumed to be at berth at the same time, one in the process of offloading and the other hoteling.  To cover the range of sizes of LNG ships that could be accommodated at the LNG Terminal, one ship was assumed to be a 138,000 cubic meter capacity and the other was assumed to be 210,000 cubic meter capacity.  In addition, for modeling purposes, an additional position for a 210,000 cubic meter LNG ship in the tuning basin was assumed for one of the two ships at the terminal.  The additional position was assumed so that maximum potential emissions from the assist tugs and security and patrol boats operating during the berthing process could be conservatively modeled accounting for the downwash, cavity and wake effects that would result while an LNG ship is at that location.

The buildings and structures were processed using the EPA Building Profile Input Program (BPIP, version 04274) to determine GEP stack heights as well as direction-specific building heights and widths for each 10-degree azimuth direction for each source included in the modeling analysis.  BPIP input and output files are included in the modeling compact disk provided in Appendix D.  Figure 5-1 depicts the BPIP model setup for the identified significant buildings or structures on site.  Figure 5-2 is a three-dimensional representation of the significant buildings and structures.

GEP stack height calculations were performed with the BPIP program based on the building/structure dimensions and the methodology described in EPA’s Guideline for Determination of Good Engineering Practice Stack Height (Technical Support Document for the Stack Height Regulations (June 1985).  The GEP stack height calculated for all stacks, with the exception of the assist tugs and security and patrol vessels was approximately 130 meters (427 feet), with some variation due to differences in stack and building/structure base elevations.  The significant structures affecting the GEP stack height for each of these stacks were the LNG storage tanks, each with a height of 51.65 meters (169.5 feet).  The GEP stack height calculated for the assist tugs and security and patrol vessels was approximately 94 meters (308 feet), based on the dimensions of the LNG ship in the turning basin.  Each of the proposed stack heights is less than the calculated GEP stack heights and the stacks are also located within the 5L zone of influence from the significant structures.  Therefore, downwash and cavity zone impact analyses, incorporated in the AERMOD with PRIME model, were performed based on the dimensions of the controlling structures.

## Meteorological Data and Site Characteristics

For refined modeling, the Guideline on Air Quality Models recommends one year of on-site data or 5 years of off-site representative data.  For this modeling analysis, 5 consecutive years of meteorological data were provided by MPSC’s air quality consultant (ERM) from the closest and most representative National Weather Service (NWS) stations to the LNG Terminal site.  Surface data from NWS Station # 93721 (Baltimore Washington International Airport - BWI) and upper air data from NWS Station # 93734 (Sterling, Virginia), both for the years 1990 to 1994 were selected for input to AERMET, a meteorological pre-processor program used in conjunction with AERMOD.  BWI is located approximately 15 km (9.3 miles) southwest of the Terminal Site.  AES concurs with ERM in considering this station to have surface meteorological data and land use characteristics that are representative of the Terminal Site.  Selection of BWI surface data is justified on the basis of spatial and climatological (temporal) representativeness as well as the ability of the selected site parameters to characterize the transport and dispersion conditions in the area of concern.  The representativeness of the data is demonstrated based on: (1) The proximity of the meteorological monitoring site to the area under consideration (BWI is within the modeling domain and only 15 km from the emission sources); (2) the similarity in the complexity of the terrain (both BWI and the area surrounding the LNG Terminal have relatively flat terrain and have similar urban land use); (3) the exposure of the meteorological monitoring site; and (4) the period of time during which data are collected.

ERM processed the raw data with AERMET (Version 04300), the meteorological preprocessor for AERMOD.  In accordance with EPA guidance (AERMOD Implementation Guide, September 27, 2005), ERM developed the season and sector specific surface inputs (albedo, Bowen ratio, and roughness length) through the use of an in-house software program that assigned these parameters based on land use within a 3 km area surrounding the BWI airport divided into 12 equally-spaced sectors.  Land use information was extracted from USGS Composite Theme Grid (CTG) files, and parameter values were assigned based on Tables 4-1 through 4-3 presented in the AERMOD user's guide.  The site characteristics by sector and season developed with this approach are summarized in Table 5-4.  Land use surrounding BWI is predominately characterized as urban.  Therefore, the urban dispersion option was used for the AERMOD modeling and the default value of 1.0 was used for the urban roughness length.  In addition, all land-based stationary sources associated with the LNG Terminal were listed as urban sources.

## Receptors and Terrain Data

A non-uniform polar grid receptor network was initially set up in AERMOD using rings of receptors spaced at 10 degree intervals on 36 radials originating at the approximate center of the LNG Terminal emission sources.  A total of 19 receptor rings were defined at the following distances in meters from the origin:

- 0 – 2 km with 100 meter spacing

- 2 – 5 km with 500 meter spacing

- 5 – 10 km with 1,000 meter spacing

- 10 – 16 km with 2,000 meter spacing

The extent of the receptor network was believed to be sufficient to identify the significant impact area with sufficient resolution.  In order to import terrain elevations associated with each of the receptors, the polar grid was converted into discrete Cartesian receptors.

The portion of the LNG Terminal located on land will be fenced and not accessible to the general public.  In addition, the general public will be restricted access to areas over water surrounding the LNG ships at berth and while in transit.  As discussed in Section 5.1., the USCG has not yet determined the preliminary extent of the excluded security zone.  However, for the purposes of the modeling analysis, it was assumed that it would be defined by a minimum radius of 500 yards from the LNG ship berth.  In addition, the USCG will establish a security zone around each LNG ship while it is in transit.  For purposes of the modeling analysis and determining the LNG Terminal “fenceline” for restricted public access, this security zone was conservatively assumed to extend 500 yards from each side of the LNG ship.  If the security zone ultimately established by the USCG is greater than these assumptions, it would reduce the impacts at fenceline receptors.  Similarly, if the security zone ultimately established by the USCG is less than these assumptions, it would increase the impacts at fenceline receptors.

A total of 56 discrete receptors were placed along the proposed “fenceline”, including 26 primary receptors at each node of the fenceline polygon and 30 receptors at intermediate points between nodes.  Discrete Cartesian receptors located within the plant boundary were eliminated since the property will not be accessible by the general public.  Figure 5-3 depicts the near-field receptors, fenceline and plant boundary receptors with those within the plant boundary eliminated.  Figure 5-4 depicts the entire receptor network within the modeling domain boundaries.

Terrain elevations at each of the receptor points were specified by importing 7.5 minute USGS Digital Elevation Model (DEM) data into ISC-AERMOD View interface.  The DEM data was obtained from www.webgis.com.  UTM Zone 18 (NAD27) was used as the common reference for model setup.  The method used to select the elevation for each receptor involved importing the highest elevation from within a bounding polygon, where the bounding polygon is defined by half the distance to adjacent receptor grid nodes.

## Background Air Quality

Modeled pollutant concentrations are added to background air quality data to evaluate compliance with NAAQS.  Background air quality data are conservatively used to account for pollutant concentrations that are otherwise not accounted for in single-source or multiple-source modeling analyses.  Representative background concentrations were obtained from the average of the most recent available three years of monitoring data (2003-2005) from the three monitoring sites nearest to the LNG Terminal site.  Table 5-5 summarizes the background ambient data and the monitoring sites determined to be most representative of the LNG Terminal modeling domain in AQCR 115.

## Model Results

The AERMOD model was used to predict maximum ambient air quality impacts for each of the scenarios identified in Section 5.1 for the LNG Terminal with and without the Power Plant.  Model results are summarized for each of the scenarios in Table 5-6.  Following FERC guidance, maximum impacts were first compared to EPA SILs.  If impacts were estimated to exceed the respective SILs, representative ambient background concentrations were then added to modeled impacts and the total concentrations were compared to NAAQS.  As summarized in Table 5-6, estimated impacts from the LNG Terminal stationary sources with or without the Power Plant are less than respective SILs for SO2, CO and Pb.  When LNG ship offloading emissions are added, only CO and Pb impacts are less than the respective SILs.  When secondary (marine vessel) sources are added to the modeling scenarios, only Pb impacts are lower than the SIL.  However, when representative ambient background concentrations are added to modeled impacts, compliance with all applicable NAAQS is demonstrated for all pollutants currently included in Maryland’s SIP, as shown in Tables 5-6 and 5-7.

It should be noted that the offsite areas where maximum modeled impacts are predicted to exceed the SILs occur in close proximity to the LNG Terminal.  Even with the worst-case scenario involving all LNG Terminal and Power Plant sources, LNG ship offloading and marine vessels, the maximum distances to SILs were all within 1,500 meters from the approximate center of the land-based LNG Terminal sources (within 1,250 meters from the property line) for all pollutants except CO and within 3,000 meters from the center (1,800 meters from the property line) for CO.  CO impacts above SILs were exclusively due to estimated emissions from outboard gasoline engines used in security and patrol boats, which have relatively high CO emission factors relative to all other modeled sources.

It should also be noted that representative 24-hour and annual average PM2.5 ambient background concentrations currently exceed the applicable AAQS and that AQCR 115 has been designated nonattainment for PM2.5.  AES understands that Maryland is currently developing a SIP revision to address the NNSR requirements applicable to the annual average standard.  However, due to the recent final rule revising the PM2.5 24-hour standard from 65 to 35 µg/m3 (effective December 18, 2006), nonattainment designations with respect to the 24-hour standard are pending as are further SIP revisions to incorporate NNSR requirements for the revised PM2.5 24-hour standard.  In addition, an EPA final rule on implementation of the PM2.5 standards during the transition period while SIPs are under development is still pending.  Therefore, AES understands that demonstration of compliance with the NAAQS currently does not include PM2.5 impacts.

## Cumulative Impacts Analysis

Based of guidance provided by the FERC through consultation, AES understands that NEPA requires a qualitative cumulative impact analysis if predicted impacts are greater than SILs.  AES further understands that additional guidance for performing such an analysis is pending as some of the details are being worked out with EPA and affected states.  Other similar projects have performed qualitative cumulative impact analyses by comparing potential direct and indirect emissions from the Project under review and other new or reasonably foreseeable projects in the region with regional emission inventories.  Based on discussion with the FERC, AES understands that the FERC is considering using the predicted significant impact area (offsite areas where maximum modeled impacts are predicted to exceed the SILs) to define the region for identifying other new and reasonably foreseeable projects to be included in the analysis.  Pending further guidance, AES also understands that a reasonable approach for assessing the regional significance of cumulative emissions is to compare them to a preliminary threshold equivalent to 10 percent of the county-wide emission inventory.  A project would not be considered regionally significant if the cumulative emissions were predicted to be less than 10 percent of the existing county inventory.

As discussed in Section 5.8, the worst-case significant impact area based on the modeling results for the scenario involving all primary and secondary emission sources extends less than 3,000 meters for CO and less than 1,500 meters for all other pollutants from the approximate LNG Terminal center point.  Furthermore, the modeled significant impact area for CO occurs entirely over water to the west of the LNG Terminal site and the significant impact area for other pollutants occurs over the Sparrows Point Industrial Complex to the east of the LNG Terminal property lines.  AES has not identified any new or reasonably foreseeable projects located in these significant impact areas determined by the modeling.  Therefore, potential emissions from the Project alone were compared to the most recent available Baltimore County emission inventory (2001) data available from EPA (http://www.epa.gov/air/data/geosel.html).  The Baltimore County emission inventory is summarized in Table 5-8 and the comparison of Project direct and indirect emissions to the County inventory is summarized in Table 5-9.  The analysis shows that worst-case Project emissions (including the LNG Terminal, Power Plant, LNG offloading and indirect emissions associated with the Project in Maryland) are estimated to be much less than 10 percent of the Baltimore County emission inventory for all pollutants, with the exception of ammonia.  Maximum ammonia emissions, due primarily to worst-case ammonia slip emissions from the Power Plant SCR system used to control NOX emissions, are estimated to be 11.8 percent of the Baltimore County ammonia emissions inventory.  Based on this analysis, worst-case direct and indirect emissions from the LNG Terminal are not considered regionally significant because the significant impact areas are predicted to be close to the LNG Terminal, no other new or reasonably foreseeable sources are expected to be located within the small significant impact area, and total LNG Terminal direct and indirect emissions would be a small percentage of the Baltimore County emissions inventory.

## Cooling Tower Impact Analysis

If AES decides to construct and operate the Power Plant, a mechanical draft evaporative cooling tower will be used to remove waste heat from the steam condenser cooling water when the Power Plant is operated without LNG sendout (conservatively expected to be less than 33 percent of the time if the Power Plant is constructed and operated).  Mechanical draft cooling towers can produce environmental impacts due to the liquid water plume coming directly from the tower (known as “drift”), as well as from the secondary liquid water formation caused by the condensation of water vapor (“fogging”).  These impacts include:  local shading of the sun due to a visible plume, fogging at ground level and ice build-up, and deposition of dissolved salt particles.

A detailed modeling analysis of cooling tower impacts was performed to evaluate the potential for these impacts from operation of the LNG Terminal using the Seasonal/Annual Cooling Tower Impact (SACTI) model (Version 09-01-86).  The SACTI model was funded by the Electric Power Research Institute (EPRI).  It is based on studies conducted by Argonne National Laboratory that evaluated the theory and performance of over 30 cooling tower plume and drift models.  The SACTI model was used for this analysis because it is a validated cooling tower plume and drift model that has been widely used in preparing environmental assessments of cooling towers for regulatory purposes.  The SACTI model uses cooling tower design and operational data along with hourly meteorological data to predict the probable impact of cooling tower plumes.

The results of the analysis are summarized in Table 5-9 and the input and output files are included on the compact disk in Appendix D.  In summary, the Power Plant cooling tower was evaluated for adverse environmental impacts using the SACTI model.  Based on this analysis, no adverse off-site environmental effects are expected.

Table 5-10 – Summary of Cooling Tower Impact Analysis Results

| Cooling Tower Impact Description | Estimated Impacts (units based on 5 years of hourly meteorology) | Estimated Location and Extent of Impacts |
| --- | --- | --- |
| Plume Fogging | 7.2 hours per year | Predominantly within 600 to meters west-south-west of the cooling tower. |
| Rime Icing | 0 hours per year | No icing is expected to occur. |
| Salt Deposition | Maximum 7,231 kg/km2-month on site | Predominantly within 100 meters of tower and on site. |
| Plume Shadowing | Maximum 200 hours/5-years | Predominantly within 200 meters west-north-west of tower and on site. |
| Plume Visibility | Plume typically visible on site when cooling tower is operating (max. 33% of time only if Power Plant is operated) | Visible plume predominantly located onsite with dimensions less than 100 meters in length, 20 to 30 meters in height and 10-15 meters in radius. |

Figures

Tables

Appendix A

Permit Application Forms

Appendix B

State-Wide Compliance Certification

COMPLIANCE CERTIFICATION

As required under COMAR 26.11.17.03B.(1), I hereby certify that all existing major stationary sources owned or operated by AES Sparrows Point LNG, LLC, a wholly owned subsidiary of The AES Corporation, in the State of Maryland are in compliance with all applicable emission limitations or are in compliance with an approved federally enforceable plan for compliance.

Signed,

_______________________________________

_______________________________________

(Title)

______________________

(Date)

Appendix C

Preliminary Vendor Data

Appendix D

CD Containing Dispersion Modeling Input and Output Files

List of Model Input and Output Files

| Input Files: | Output Files: | Description |
| --- | --- | --- |
| AERMOD Refined Modeling Files |
| SPNO90.ADI | SPNO90.ADO | NOX, annual average, 1990 |
| SPNO91.ADI | SPNO91.ADO | NOX, annual average, 1991 |
| SPNO92.ADI | SPNO92.ADO | NOX, annual average, 1992 |
| SPNO93.ADI | SPNO93.ADO | NOX, annual average, 1993 |
| SPNO94.ADI | SPNO94.ADO | NOX, annual average, 1994 |
| SPSO390.ADI | SPSO390.ADO | SO2, 3-hr average, 1990 |
| SPSO391.ADI | SPSO391.ADO | SO2, 3-hr average, 1991 |
| SPSO392.ADI | SPSO392.ADO | SO2, 3-hr average, 1992 |
| SPSO393.ADI | SPSO393.ADO | SO2, 3-hr average, 1993 |
| SPSO394.ADI | SPSO394.ADO | SO2, 3-hr average, 1994 |
| SPSO2490.ADI | SPSO2490.ADO | SO2, 24-hr average, 1990 |
| SPSO2491.ADI | SPSO2491.ADO | SO2, 24-hr average, 1991 |
| SPSO2492.ADI | SPSO2492.ADO | SO2, 24-hr average, 1992 |
| SPSO2493.ADI | SPSO2493.ADO | SO2, 24-hr average, 1993 |
| SPSO2494.ADI | SPSO2494.ADO | SO2, 24-hr average, 1994 |
| SPSOA90.ADI | SPSOA90.ADO | SO2, annual average, 1990 |
| SPSOA91.ADI | SPSOA91.ADO | SO2, annual average, 1991 |
| SPSOA92.ADI | SPSOA92.ADO | SO2, annual average, 1992 |
| SPSOA93.ADI | SPSOA93.ADO | SO2, annual average, 1993 |
| SPSOA94.ADI | SPSOA94.ADO | SO2, annual average, 1994 |
| SPPMA90.ADI | SPPMA90.ADO | PM, annual average, 1990 |
| SPPMA91.ADI | SPPMA91.ADO | PM, annual average, 1991 |
| SPPMA92.ADI | SPPMA92.ADO | PM, annual average, 1992 |
| SPPMA93.ADI | SPPMA93.ADO | PM, annual average, 1993 |
| SPPMA94.ADI | SPPMA94.ADO | PM, annual average, 1994 |
| SPPM2490.ADI | SPPM2490.ADO | PM, 24-hr average, 1990 |
| SPPM2491.ADI | SPPM2491.ADO | PM, 24-hr average, 1991 |
| SPPM2492.ADI | SPPM2492.ADO | PM, 24-hr average, 1992 |
| SPPM2493.ADI | SPPM2493.ADO | PM, 24-hr average, 1993 |
| SPPM2494.ADI | SPPM2494.ADO | PM, 24-hr average, 1994 |
| SPCO190.ADI | SPCO190.ADO | CO, 1-hr average, 1990 |
| SPCO191.ADI | SPCO191.ADO | CO, 1-hr average, 1991 |
| SPCO192.ADI | SPCO192.ADO | CO, 1-hr average, 1992 |
| SPCO193.ADI | SPCO193.ADO | CO, 1-hr average, 1993 |
| SPCO194.ADI | SPCO194.ADO | CO, 1-hr average, 1994 |
| SPCO890.ADI | SPCO890.ADO | CO, 8-hr average, 1990 |
| SPCO891.ADI | SPCO891.ADO | CO, 8-hr average, 1991 |
| SPCO892.ADI | SPCO892.ADO | CO, 8-hr average, 1992 |
| SPCO893.ADI | SPCO893.ADO | CO, 8-hr average, 1993 |
| SPCO894.ADI | SPCO894.ADO | CO, 8-hr average, 1994 |
| SPPb2490.ADI | SPPb2490.ADO | Pb, 24-hr average, 1990 |
| SPPb2491.ADI | SPPb2491.ADO | Pb, 24-hr average, 1991 |
| SPPb2492.ADI | SPPb2492.ADO | Pb, 24-hr average, 1992 |
| SPPb2493.ADI | SPPb2493.ADO | Pb, 24-hr average, 1993 |
| SPPb2494.ADI | SPPb2494.ADO | Pb, 24-hr average, 1994 |
| BPIP Prime Files: |
| SP******.BPI | SP******.PRO | BPIP Input and Output Files For AERMOD Prime Refined Runs |
| SACTI Files: |
| Mult**.out | Tables**.out | SACTI model input and output files. |
| Prep**.out |  |  |

Appendix E

Alternatives Analysis

Resource Report 10 has been formally filed with FERC on January 8, 2007 of which a copy was provided to the MDE because MDE is a cooperating agency.

# Footnotes

The LNG Terminal will be designed to allow the potential addition of a fourth tank and a potential expansion in vaporization and sendout capacity of up to 2.25 bscfd.  The Terminal design includes pre-investment in features and equipment, including blanked off pipe connections, to facilitate this future expansion.  If and when the time comes to pursue this expansion, AES will perform a more detailed study on the expansion case to identify changes required to the existing LNG Terminal facilities.  AES does not anticipate that the potential Terminal expansion will result in modifications to stationary sources proposed with this air permit application or additional stationary sources.

AES expects two to three ships per week will arrive at the LNG Terminal, which equates to approximately 100 to 150 ships per year.  Modeling 180 ship arrivals is therefore conservative.

AES will attempt to negotiate LNG terminaling contracts under which tankers will operate preferably with natural gas and alternately with low sulfur marine diesel while stationary at the LNG Terminal, in order to minimize emissions and air quality impacts.  At this time, AES cannot predict the success it will have in negotiating such contracts.  Accordingly, the conservative assumptions outlined above and in more detail in Table 9-6 are even more appropriate at this time.

It should be noted that, effective December 18, 2006, EPA revised the 24-hour PM2.5 NAAQS from 65 to 35 µg/m3 and revoked the 24-hour PM10 NAAQS.  Therefore, revised nonattainment designations are pending based on review of monitored PM2.5 24-hour ambient data in comparison to the revised NAAQS.

Letter from John Calcagni, EPA AQMD to Ken Waid, January 8, 1990 re: clarification on questions concerning “secondary emissions” as defined in 40 CFR 52.21(b); Letter from Charles Sheehan, EPA Regional Counsel to Michael Cathey, October 28, 2003.

The 28 listed source categories subject to PSD review for which a 100 TPY applicability threshold would apply include fossil fuel boilers (or combination of them) totaling more than 250 million Btu per hour heat input and fossil fuel-fired steam electric plants of more than 250 million Btu per hour heat input.  AES has not yet determined through consultation with MDE whether these source categories potentially would include the CTG with auxiliary fired HRSG and four hot water heaters.  However, AES has determined that recent PSD applicability determinations have not treated similar sources at LNG terminals as falling within one of the 28 listed source categories.  For example, the FERC Draft Environmental Impact Statement (DEIS) for the Broadwater Energy floating LNG storage and regasification unit (November 2006) was assumed not to be one of the listed 28 source categories and, on that basis, a 250 TPY applicability threshold was applied.  Similarly, the DEIS for the Gulf LNG Energy Project discusses a May 1, 2006 applicability determination issued by the Mississippi Department of Environmental Quality indicating that the proposed LNG terminal would not be treated as one of the 28 listed source categories.  On that basis, the terminal would not trigger PSD review as long as the potential to emit for all stationary sources at the terminal would not exceed 250 TPY for any attainment criteria pollutant.

While berthing of two ships at one time is contemplated in the design of the LNG Terminal, offloading of cargo will only be possible from one ship at a time.