Phase II of the cooling project.

Phase II-1 :  End of July (pursued in the cooling group).

Post review studies  :

Further analysis of existing data

Re-measure existing structures (key-measurements) with mixtures and full power - change compressor (ATLAS COPCO)

Further studies of thermodynamic parameters of mixtures.

Design and make input/output heat-exchanger and regulator scheme in single stave setup (to be modified)

Optimization of dimensions and specifications for SCT and PIXELs. Design criteria for structures. Thermal gradients.

Cable cooling layout (Services WG)

First layout in the crack region, material-distributions and estimates (Services WG)

Costing of phase II and final system.

Define new thermal test-structures for detailed measurements and system measurements to be developed by the SCT and PIXELs. Work-packages.

Special meeting needed in July to conclude this ?

Implication of TRT ASIC power increase.

Phase II-2 : End of 1999

Item 1 : Develop and conclude TRT electronics layout cooling for increased power by September.

Item 2 : Construct structures for the detailed cooling engineering test and the system tests, including heat-exchangers. Discussion and definitions in the SCT/PIXEL communities.

Timescale for these structures September (structures for detailed studies) to December 1999 (for system structures).

Item 3 : Detailed measurements of simple structures for optimization, heat-exchangers, performance, engineering and structure parameters. Can partly be performed using the existing cooling facilities at CERN and similar facilities in other institutes. Results by November 1999 (linked to SCT structure PRR).

Item 4 : Detailed studies of thermal contacts to the modules and thermal performance of the modules. This is mostly an engineering study but it will connect to and should use the cooling plant for parts of the studies (single tube setup). Responsibility of the SCT and PIXEL engineering groups.

Results by November 1999 (linked to SCT structure PRR).

Item 5 : Design of TRT and SCT/PIXEL cable cooling plant (monophase +16) by October.

Phase II-3 : Time-scale middle/end of 2000.

System performance.

Work out detailed specifications and costing.

Prepare larger system (5-10kW) for system aspect studies, by the end of the year.

A system for mixtures or C3F8 has been shown by M.Bosteels (transparencies) with individual control of the cooling circuits.  Such a system can be developed before January 2000.

A thermal shield prototype is needed.

A request for space in bat. 186 with the correct height differences, infrastructure and dimensions has been submitted.

Systematic measurements using this cooling plant to cool structures start at CERN in January 2000.

To address : system performance and control, stability, faults, start/stop, operational issues, structure performance, etc.

General on-going activities throughout the whole period:

Item 1 : Irradiation of all components in the cooling systems.

Responsibility of the LHC cooling coordinator (A.Smith).

Item 2 : Material compatibility studies of everything which can come in contact with the liquids.

ID and SCT, PIXEL engineering responsibility.

Item 3 :

Development of a DCS system based on Bridgeview and CAN for  measurements and monitoring of the thermal structures

Interlock systems

Analog control of Fluid Mass Flow and Boiling Pressure.

Responsibility of ID cooling group and DCS groups.