From:	Joel H. Schultz

To:	Dale Meade, Phil Heitzenroeder

Subject:	Update of Cryogenic Refrigerator Sizing and Costing for FIRE* 2.14 m Reference with Self-Consistent Scenario

Date:	August 11, 2003

NSO No WBS7_081103_UpdateCryoRefrigSizeCostFIRE-2003.doc

Introduction

The FIRE cryoplant and nitrogen distribution system provides liquid nitrogen to the TF and PF magnet systems to  recool the magnets after pulses and for cooldown from room temperature. The magnet system is flushed out with helium, immediately before each pulse, in order to prevent the formation of radioactive N13.  This memorandum describes the magnet cooling circuit, the overall cryoplant topology, the cryogenic loads, and the sizes of the cryoplant components.  It has been updated from previous refrigerator descriptions to be consistent with losses in reference 2.14 m design and baseline and extended experimental plans that are consistent with constraints on total fusion energy and recool times.

I. Magnet Cooling Circuit

The magnets are cooled by circulating liquid nitrogen through cooling lines (TF), and radial flow through magnet interpancake space  (CS and PF coils). Liquid nitrogen is blown out and replaced by pressurized helium, before pulses, in order to eliminate the creation of N13 through neutron irradiation.  A negligible amount of N13 is still formed in the shielded nitrogen atmosphere of the nuclear island, but it is sufficiently low that no nitrogen holdup system is now required.

The TF inside and outside legs are cooled separately by cooling lines that are fed through adjacent gun-drilled holes in each of the TF coil turns. One set of lines turns inwards and cools the TF inside leg and the inner halves of the upper and lower legs, the other the outside leg and the outer halves. The line inlet and outlet points are located at the high and low points of the profile to facilitate draining of liquid nitrogen prior to a pulse.

The central solenoid and poloidal field coils are cooled radially between double pancakes.  As in CIT, the flow direction is from the outside to the inside to prevent outer layer heating and turn-turn delamination. A can around the outside of the Central Solenoid acts as a distribution header.  The pancakes are individually insulated, but there is no ground wrap around the entire coil, because of the need for radial flow.

II. Load Assessment

Cryogenic loads, requiring the circulation of liquid nitrogen, include the following:

1) Radiation from the inner vacuum vessel warm surface to the inner magnet surface

2)	Radiation from the outer magnet surface to the cryostat walls and the ducts

3) Radiation from the transfer lines to its cryostat walls

4)	Conduction through cold mass supports

5) Joule heating of the TF and PF coils

6) Neutron and gamma heating of the TF and PF coils during pulses

7) Heat conduction and Joule heating in the high-current leads

8)	Cold mass cooldown from room temperature

9) Removal of nuclear after heat

The load parameters that are most relevant to assessing these loads are accumulated in Table I. The dominant load is the ohmic dissipation of the TF coil.

Table I- Key Cryogenic Load Parameters

# (baseline/extended)

| Parameter | Units | Value |
| --- | --- | --- |
| Ediss, TF | (GJ) | 16.14 |
| Ediss, PF | (GJ) | 6.84 |
| Ncircuits |  | 8 |
| ntransfer lines |  | 3 |
| L,xfer line | (m) | 200 |
| tdwell, max | (s) | 4500 |
| Npulses, full-power |  | 3000/6000 |
| Npulses, total |  | 30,000/ 60,000 |
| Max pulses/storage |  | 40 |
| Max pulses/week |  | 100 |
| Max no. RT cooldowns |  | 50 |
| Storage tank drawdown |  | 0.8 |
| Storage tank boiloff |  | 0.1 |
| J/cooldown | (GJ) | 110 |
| J/cooldowns, lifetime | (GJ) | 5,500 |
| Pradiation, in | (kW) | 59.0 |
| Pradiation, outside | (kW) | 7.48 |
| Pconduction | (kW) | 3.145 |
| P,xfer lines | (kW) | 15 |
| Pleads, TF | (kW) | 10.4 |
| Pleads, PF | (kW) | 11.1 |
| Pdiss, TF | (MW) | 3.59 |
| Pdiss, PF | (MW) | 1.52 |
| Pdiss, total | (MW) | 5.19 |
| Pleads, total | (kW) | 21.52 |
| Pidle | (kW) | 95.4 |
| Ptotal, 1 recool | (MW) | 5.21 |
| lN2 flow, full-power recool | (kg/s) | 26 |
| Volume, lifetime, total lN2 | (Mgal) | 310/475 |
| lN2 usage/pulse, max | (kgal) | 30.7 |
| lN2 Storage tank requirement | (kgal) | 881/1,087 |

The nitrogen storage tanks are sized for a two-day supply of nitrogen for the worst case of DT, H-mode extended operation.  The energy needed for cooldown from room temperature was calculated to be equal to 13.4 days of idling losses. Therefore, the magnet system is kept cold overnight and weekends and only warmed up to room temperature during maintenance periods.  There 50 room temperature cooldowns during the machine life.  Heaters are used on the vent lines to prevent condensation plumes of liquid nitrogen.

III.	Cryoplant Topology

The overall cryoplant design of FIRE was originally based on those of CIT and BPX. Major design features include the following:

- Large liquid nitrogen storage tanks and fill stations are used, instead of a closed-cycle nitrogen refrigerator. However, in FY99, FIRE agreed with CIT, BPX, and Alcator that truck deliveries from a commercial air liquefaction plant must be most economical, because of the pulsed nature of the load. This was reviewed in FY00 and both BOC/AIRCO and Air Liquide recommended the construction of dedicated on-site or near-site nitrogen plants.  The design still includes on-site liquid nitrogen storage.

- FIRE uses the Alcator C-Mod method of one pump and individual regulator valves for each flow circuit. This provides close to optimized cooldown and has proven to be very reliable.

- A subcooler is used, as in the BPX and CIT designs, in order to provide 80 K liquid nitrogen to the coils.  The boiling temperature of nitrogen at 10 atmospheres is 105 K. The expensive secondary circuit of CIT is eliminated by BPX and FIRE.

- The amount of radioactive nitrogen-13 generated in FIRE is small, because of the smaller volume of unshielded nitrogen inventory.  The FY99 cryogenic system provided one day’s holdup for nitrogen-13, which has a half-life of ten minutes.  Even without holdup, the discharge of nitrogen-13 would be within allowables for sites such as ORNL or Savannah River, with large distances to the site boundaries.  The present design purges the coils with helium before operation, eliminating any need for nitrogen holdup.

Design Tradeoff

Five options were considered for the FIRE cryogenic refrigeration system, as illustrated in Figures 1-4:

- Option 1a: Temporary Storage of all Irradiated Gas after Pulse with an Open Secondary

- Option 1b: Separate holdup streams for highly-irradiated nitrogen and recool gas after Pulse with Open Secondary

- Option 2: Open Nitrogen Loop with Helium Purge before a pulse

- Option 3: Magnet cooling by a closed-loop secondary nitrogen circuit

- Option 4: Magnet cooling by a closed-loop secondary helium circuit

The schematic of a sixth option, a helium refrigerator with closed-loop primary and secondary circuits, has been developed, as shown in Figure 5, but not yet sized and costed.  This option is the only one that avoids the cost of replacing large amounts of nitrogen vented into the atmosphere, but would also have the highest capital cost.

| Figure 1: Option 1: Temporary Storage of Irradiated Gas after Pulse, Open Secondary | Figure 2: Option 2: Open Nitrogen Loop with Helium Purge |
| --- | --- |
| Figure 3: Option 3-Closed-loop Secondary N2 Circuit (BPX/CIT) | Figure 4: Option 4: Closed-Loop Helium Secondary |

Figure 5: Fire Magnet Refrigerator with closed-cycle helium primary and secondary circuits

The relative costs of the original five options are compared in Table II:

Table II: Relative Costs of Five Refrigerator Topology Options

| Refrigerator Option | PACE, min | PACE, max | Total |
| --- | --- | --- | --- |
| 1a Open N2, Holdup all N2 | 9.04 | 12.2 | 16.7 |
| 1b Separate holdup streams | 5.51 | 8.64 | 11.8 |
| 2 Open N2, He purge | 5.46 | 8.59 | 11.8 |
| 3 Closed-loop lN2 Secondary | 5.97 | 9.1 | 14.6 |
| 4 Closed-loop He Secondary | 13 | 16.1 | 22.1 |

The performance tradeoffs are summarized as numerical rankings in Table III:

Table III: Cost/Performance Rankings of five refrigeration system options

| Refrigerator Option | Cost | N13 Generated/Released | Recool Time |
| --- | --- | --- | --- |
| 1a Open N2, Holdup all N2 | 4 | 3 | 2 |
| 1b Separate holdup streams | 2 | 4 | 5 |
| 2 Open N2, He purge | 1 | 2 | 2 |
| 3 Closed-loop lN2 Secondary | 3 | 5 | 1 |
| 4 Closed-loop He Secondary | 5 | 1 | 4 |

Option 2 was selected as the new reference design, because it had the best overall combination of low cost, radioactivity, and recool time, as shown in Table III.  Parameters have been updated to correspond to the CY2002 FIRE* reference design at Ro=2.14 m and are reported in Section V.

##### IV.. Cost Algorithm

New pricing information was solicited on the cost of vacuum-jacketed piping, unjacketed piping, elbows, and valves.  A new set of cryogenic equipment costing equations were derived on the basis of the data base and are listed in Table IV.  Although impressively large at first glance, the data base is still not adequate.  In particular, we haven't obtained good recent pricing on large cold boxes, nitrogen gas bags, heaters or blowers.  However, because of the need to begin comparing different design options, an interim set of costing equations was derived, based on previous cost studies.  This will be updated as new information becomes available.

Table IV: Cryogenic Equipment Costing Equations

| Component | Equation | Notes |
| --- | --- | --- |
| Pump/Compressor | $273/gpm | Liquid nitrogen, Barber-Nichols quote |
| Cold Box | $4500/To (Q)0.7 | Slack formula, ratioed to BPX subcooler cost x 1.5 for inflation, Q is in W; To is the outlet temperature |
| Vacuum jacketed pipe | $164 Di ($/m) | Di=Inner diameter in inches,PHPK quote |
| Unjacketed pipe | $73/m (Dt) | Dt=Inner diameter thickness product in inches, Stainless Tubular Products |
| Valves Throttle Shutoff Relief | $267 Di2.27 $180 Di2.27 $140Di2.27 | PHPK quote; relative prices from BPX; Di in inches. |
| Controller | $150 k-Hardware; $250 k-Labor | 40 % deflation since BPX |
| Blower | $300/hp | BPX x 1.5 for inflation |
| Nitrogen heaters | $250/kW | Scaled from intepretation of BPX, x 1.5 for inflation |
| Filters | $500/gpm | Scaled from BPX, x 1.5 for inflation |
| Storage Bag | $30/m3 | Robinson's eqn. x 1.5 for inflation |
| Storage Tank (vacuum insulated) | $8/gal (250 MAWP) $5/gal (40 MAWP) | Taylor-Wharton quotes |
| Local I&C | $400 k | 40 % deflation since BPX |
| Contingency | 16 % of PACE subtotal | Ratioed from BPX |
| Assembly, Installation & Test | 18 % of PACE total + contingency | Ratioed from BPX |

The cryogenic load for all options is summarized in Table I:

# V. Sizing of the Design Options

A sizing workbook was developed for the four design options with five worksheets.  The first (reference) option of storing the radioactive gas after a shot for three hours between shots was subdivided into an Option A, in which all of the nitrogen used in one shot, including that used for recooling, is stored temporarily, and an Option B, in which the magnets are purged both before and after a shot, and only the purged gases are stored.  Option 2, described below in more detail, is sized in Worksheet 3 of the Workbook “Mag Refrig Design Extended Ops - 2.14 m.xls”.

## Sizing of Option2: Open Nitrogen Loop with a Helium Purge

If the liquid nitrogen were purged by helium before a pulse, then essentially no radioactive gas would be generated by the pulse.  Any imperfectly shielded nitrogen atmosphere in the cell is not considered here.  There would then also be no need to purge the magnet vapor after a shot and recool could begin immediately with no temporary storage.  The disadvantage is that pressurized helium storage and a helium-nitrogen heat exchanger have to be added to the cryogenic system.  There is also a modest amount of helium that is vented and has to be purchased.  Option 2 is illustrated by Figure 6 and sized in Table V.

Figure 6: Open Nitrogen Loop with Helium Purge

The sizes of the cryogenic refrigerator components in Option 2 are listed in Table V.

Table V: Component Sizes of Option 2 with an Open Nitrogen Loop, Helium Purge, and without Temporary Storage

| Parameter | Units | Baseline | Extended |
| --- | --- | --- | --- |
| lN2 Storage tank requirement | (kgal) | 880.7 | 1087.4 |
| nstorage tank 12" shutoff valves |  | 4 | 4 |
| Nitrogen Supply to Magnets |  |  |  |
| Lcold nitrogen piping | (m) | 200 | 200 |
| L 8" lN2 vacuum-jacketed pipe | (m) | 100 | 100 |
| Average nitrogen pumping reqmnt | (kg/s) | 20.9 | 20.9 |
| Peak nitrogen pumping reqmnt | (kg/s) | 30.3 | 41.7 |
| nRegulator valves to magnets |  | 3 | 3 |
| Dregulator valves to magnets | (in) | 10 | 10 |
| nfilters |  | 4 | 4 |
| Total gpm, premagnet filters | (gpm) | 819 | 819 |
| no 12" shutoff valves |  | 6 | 6 |
| Purge Requirements |  |  |  |
| Flush cycles |  | 20 | 22 |
| Flush length | (m) | 50 | 50 |
| Di, flushed pipes | (in) | 12 | 12 |
| V, total flushed volume | (m^3) | 4.65 | 4.65 |
| M, He gas purges | (kg) | 985 | 985 |
| nshots/Pressurized He tank capacity |  | 20 | 20 |
| Volume, 18 atm pressure vessel,supply | (m^3) | 6800 | 6800 |
| Di, shutoff valve, He purge stream | (in) | 12 | 12 |
| L,addit'l pipe, separate flush exhaust | (m) | 100 | 100 |
| Di, regulator valve, He purge stream | (in) | 12 | 12 |
| Total flush time | (s) | 600 | 600 |
| Average mass flow, flush stream | (kg/s) | 1.642 | 1.642 |
| Q,He-lN2 heat exchanger | (W) | 1908 | 1908 |
| Blower capacity | (kg/s) | 156.5 | 156.5 |
| Blower power | (hp) | 1795 | 1795 |
| Lexhaust pipes | (m) | 200 | 200 |
| Di, exhaust pipe | (in) | 16 | 16 |
| no x Di,vent valves | (in) | 2 x 12 | 2 x 12 |
| Peak mass flow through gas storage line | (kg/s) | 41.72 | 41.72 |
| Heater power | (kW) | 8915 | 8915 |

VI. Costing of the Design Options

Having sized the individual components and proposed a set of costing equations, it is now possible to compare the costs of the five design options.  Each option was costed according to the costing rules in Table IV.  The cost of Option 2 is given in Table VI, below.

Table VI: Cost of Option 2 with an Open Nitrogen Loop, Helium Purge, and without Temporary Storage

| Parameter | Units | 2.0 m Design | Baseline | Extended |
| --- | --- | --- | --- | --- |
| Subcooler | (k$) | 1007.7 | 2008.7 | 2013.4 |
| lN2 Storage tank | (k$) | 4211.8 | 4403.6 | 5437.2 |
| Dstorage tank shutoff valves | (k$) | 202.8 | 202.8 | 202.8 |
| L 8" lN2 vacuum-jacketed pipe | (k$) | 196.8 | 196.8 | 196.8 |
| Nitrogen pump | (k$) | 96.4 | 223.7 | 228.6 |
| Regulator valves to magnets | (k$) | 149.2 | 149.2 | 149.2 |
| Presubcooler filter | (k$) | 176.5 | 409.7 | 418.7 |
| Premagnet filter | (k$) | 176.5 | 409.7 | 418.7 |
| Dmisc shutoff valves | (k$) | 304.2 | 304.2 | 304.2 |
| 18 atm pressure vessel | (k$) | 89.8 | 448.8 | 471.2 |
| Shutoff valve, He purge stream | (k$) | 50.7 | 50.7 | 50.7 |
| Addit'l pipe, separate flush exhaust | (k$) | 32.9 | 32.9 | 32.9 |
| Regulator valve, He purge stream | (k$) | 75.2 | 75.2 | 75.2 |
| He-lN2 heat exchanger | (k$) | 24.7 | 40.2 | 40.2 |
| Blower | (k$) | 556.7 | 538.4 | 538.1 |
| Cold exhaust pipe | (k$) | 58.4 | 58.4 | 58.4 |
| Warm exhaust pipe | (k$) | 58.4 | 58.4 | 58.4 |
| Vent valves | (k$) | 101.4 | 101.4 | 101.4 |
| Nitrogen exhaust heater | (k$) | 1920.1 | 3462.2 | 3515.4 |
| Instrumentation and Control |  | 759.2 | 1054.0 | 1144.9 |
| PACE, subtotal | (M$) | 10.25 | 14.23 | 15.46 |
| Contingency | (M$) | 1.64 | 2.28 | 2.47 |
| PACE+Contingency | (M$) | 11.89 | 16.51 | 17.93 |
| Assembly, Installation & Test | (M$) | 2.14 | 2.97 | 3.23 |
| Grand Total | (M$) | 14.03 | 19.48 | 21.16 |

Although the total nitrogen consumption in the present baseline is actually less than in the 2.00 m design, the refrigerator is more expensive, because recool has been accelerated from 3 hours to ¼ -1¼ hours, depending on pulse length.  The incremental cost of extended operation is surprisingly similar to that of baseline operations.  The main reason for this is that recool ability “clamps” the refrigerator power over a single shot, day, or week.  The operations are extended primarily by increasing the operating weeks, which increases nitrogen consumption, but not refrigerator power or even local storage requirements.  Idling losses are also the same for baseline and extended operations.

Although Option 2 requires a helium cold box and temporary helium storage, their cost is relatively low, since the helium isn't needed for magnet heat removal, but merely for purging the nitrogen volume.

.

The closed-loop helium secondary is the most expensive of the five options considered, because of the requirement for a cold box, compressor, and helium storage tank that is adequate for magnet cooldown.

VII. Cost of Nitrogen

The cost of the cryogenic refrigeration system remains small in comparison with the cost of nitrogen over the course of the project.  The energy dissipation in the TF coils was calculated by P. Titus over a range of fields and flat-top times, while PF energy was scaled from the 6.0 GJ dissipation in a single simulation.  The lifetime ohmic dissipation is based on self-consistent experimental plan with 3,000 full-field and current shots, 30,000 lifetime shots and 6500 GJ of fusion power for baseline operation and double these numbers for extended operation.  Titus has shown a broad range of tradeoffs between nitrogen and power supply requirements vs. cooldown time.  We adopted the minimum power consumption scenario, starting each pulse at 80 K.  This study calculates the change in cost, due to increasing the size of FIRE from Ro=2.0 m to Ro=2.14 m and using a self-consistent scenario.

In 2001, BOC gave pricing for a 10 year lease and a 15 year lease.  This was then updated in 2003 for nitrogen use up to four times that of the previous design, an overly conservative intepretation of the extended operations needs for the larger, 2.14 m machine.  The quotes were scaled to the self-consistent design, and an interpretation of the nitrogen cost estimates is listed in Table VII:

Table VII: Nitrogen Cost Estimates

| Total Cost | Units | Previous | 2.14 m FIRE Self-Consistent Baseline | 2.14 m FIRE Self-Consistent Extended |
| --- | --- | --- | --- | --- |
| 10 Year Commitment | (M$) | 143 | 57.7 | 88.4 |
| 15 Year Commitment | (M$) | 107/118.5 | 43.3 | 66.3 |

The penalty for purchasing more nitrogen/year over 10 years seems high, but is based on a quote of 20 cents/100 cu ft of liquid nitrogen for a 10 year lease and 15 cents/100 cubic feet for 15 years.  In 2003, I received a new quote from BOC.  It remained at 20 cents/100 cu ft for a 10 year lease and 15 cents/100 cubic feet for 15 years.  The explanation was that inflation was exactly balanced by a quantity discount.  Unfortunately, the specifications were given to them when it was believed that extended operation would consume four times as much nitrogen as baseline, 2.0 m.  It, therefore, seems probable that the most recent quotation is too optimistic.  If the cost were 25 cents/100 cu ft, then nitrogen for the baseline would cost $72 M over the life the machine, while extended operations would cost $110.5 M.  I expressed incredulity that the price for the same amount of nitrogen over 10 years should be higher than that over 15 years to two different BOC representatives, both Marc Berlinger, the interface, and Jim Flaherty, who prepared the estimate.  They insisted that this was the case and Berlinger actually cited “return on investment” and “mortgage rates.”  I tried to explain that getting less money in a longer period of time can’t be as good as getting more money in a shorter period and that one actually pays more on a 15 year mortgage than a 10 year mortgage, even if the monthly payments or even the interest rate are less, but to no avail.  So while I remain suspicious, I have to assume that this is the actual  result from BOC’s costing spreadsheets.  The reason for the second cost for the 15 year lease/2.0 m FIRE is that the price/100 cubic feet is a constant, down to 75 % of nominal usage.  After that it would be flat, so that BOC/AIRCO would collect $8.5 M/year, even if the facility never ran.  Presumably, since the nitrogen requirements are now smaller, the minimum cost would be less than $8.5 M/year, but it may still be the cost driver, increasing the lifetime nitrogen cost to something above $100 M over the actual sixteen year experimental plan.

A second estimate is (hopefully) being prepared by Air Products.  They have questioned me extensively about the actual operating plan, so hopefully the fluctuations in load will be taken correctly into account in the costing.  They also have the latest, lower estimates of lifetime nitrogen usage.

VII. Conclusions

Sizing and costing of the reference option, an open lN2 system with a helium purge, has been updated to include a more extensive inventory of losses in the 2.14 m machine and more self-consistent experimental plan for both baseline and extended operations.

A methodology was developed for comparing different refrigerator design options.  Three of the five options were relatively inexpensive and difference between their costs within the uncertainties of the costing exercise.  These were 1) Open N2 system with a helium purge, 2) Open N2 with a nitrogen purge and two exhaust lines, and 3) Closed-loop lN2 Secondary.

The open N2 system with a helium purge also had high-rankings in low generation and release of N13 and recool time, although the difference between all of the sytems may be relatively small in both categories.

The closed-loop lN2 secondary costing is probably optimistic, since it doesn't include an emergency nitrogen holdup system. A more expensive closed-loop helium refrigerator concept has been developed, but not sized or costed.  It’s main advantage would be that of eliminating high nitrogen costs.  It would also eliminate any generation of radioactive N13 and permit “IGNITOR-style” subcooling.

Option  2 was selected, Open N2 with a helium purge.  If the relatively low liquid nitrogen costs from a dedicated plant can’t be confirmed for nonsteady-state operation, the closed-cycle helium system is being developed as a backup design.

Costs of the cryogenic refrigeration system were updated for the FIRE* Option, the CY2002 reference design, and the CY2003 baseline and extended operations experimental plans.  The overall cost of the cryogenic system increased from to $14 M to $19.5 M for baseline operation and $21.2 M for extended operation.  Recool time constraints prevented extended operation from being significantly more expensive than baseline.

The cost of liquid nitrogen has been reconfirmed by a new budgetary estimate, albeit with identifiable sources of possible error.  We are attempting to obtain a second, independent estimate.  The cost of nitrogen has decreased, because of the fixed number of pulses in the baseline and the reduced average power, integrated over all discharges.

# Footnotes

NSO No WBS7_000526_ Sizing and Costing of Cryogenic Refrigerator Options.doc, Joel H. Schultz, "Sizing and Costing of Cryogenic Refrigerator Options," May 26, 2000; NSO No WBS7_121401_UpdateCryoRefrigSizeCostFIRE*.doc, Joel H. Schultz, “Update of Cryogenic Refrigerator Sizing and Costing for FIRE* 2.14 m Reference Machine,” December 14, 2001

NSO No WBS7_0709_Extended_ Operations_Plan_Rev3, Joel H. Schultz, “Schedule and Shot-counts for FIRE Baseline and Extended Operations, Rev. 3,” July 9, 2003

R.B. Fleming and G.D. Martin, "Liquid nitrogen cooling for the Compact Ignition Tokamak," Knoxville, SOFE 13, 1989

R.B. Fleming and G.D. Martin, “System Description, Cryogenic System, WBS Q: BPX Design Description Document,” Feb 13, 1991

H. Khater, Sec. 5.8, FIRE FY 01 Engineering Report Update