From:	Joel H. Schultz

To:	Phil Heitzenroeder, Richard J. Thome

Subject:	Update of Cryogenic Refrigerator Sizing and Costing for FIRE* 2.14 m Reference Machine

Date:	December 14, 2001

Firewire:NSO No WBS7_121401_UpdateCryoRefrigSizeCostFIRE*.doc

Introduction

The FIRE cryoplant and nitrogen distribution system provides liquid nitrogen to the TF and PF magnet systems to  recool the magnets after pulses and for cooldown from room temperature. The magnet system is flushed out with helium, immediately before each pulse, in order to prevent the formation of radioactive N13.  This chapter describes the magnet cooling circuit, the overall cryoplant topology, the cryogenic loads, and the sizes of the cryoplant components.

I. Magnet Cooling Circuit

The magnets are cooled by circulating liquid nitrogen through cooling lines (TF), and radial flow through magnet interpancake space  (CS and PF coils). Liquid nitrogen is blown out and replaced by pressurized helium, before pulses, in order to eliminate the creation of N13 through neutron irradiation.  A negligible amount of N13 is still formed in the shielded nitrogen atmosphere of the nuclear island, but it is sufficiently low that no nitrogen holdup system is now required (See Sect. 5.10).

The TF inside and outside legs are cooled separately by cooling lines that are fed through adjacent gun-drilled holes in each of the TF coil turns. One set of lines turns inwards and cools the TF inside leg and the inner halves of the upper and lower legs, the other the outside leg and the outer halves. The line inlet and outlet points are located at the high and low points of the profile to facilitate draining of liquid nitrogen prior to a pulse.

The central solenoid and poloidal field coils are cooled radially between double pancakes.  As in CIT, the flow direction is from the outside to the inside to prevent outer layer heating and turn-turn delamination. A can around the outside of the Central Solenoid acts as a distribution header.  The pancakes are individually insulated, but there is no ground wrap around the entire coil, because of the need for radial flow.

II. Load Assessment

Cryogenic loads, requiring the circulation of liquid nitrogen, include the following:

1) Radiation from the inner vacuum vessel warm surface to the inner magnet surface

2)	Radiation from the outer magnet surface to the cryostat walls and the ducts

3) Radiation from the transfer lines to its cryostat walls

4)	Conduction through cold mass supports

5) Joule heating of the TF and PF coils during full-power and 2/3 power pulses

6) Neutron and gamma heating of the TF and PF coils during pulses

7) Heat conduction and Joule heating in the high-current leads

8)	Cold mass cooldown from room temperature

9) Removal of nuclear after heat

The load parameters that are most relevant to assessing these loads are accumulated in Table I. The dominant load is the ohmic dissipation of the TF coil.

Table I- Key Cryogenic Load Parameters

| Parameter | Units | Value |
| --- | --- | --- |
| Ediss, TF | (MJ) | 16.14 |
| Ediss, PF | (MJ) | 6.84 |
| ncircuits |  | 8 |
| ntransfer lines |  | 3 |
| L,xfer line | (m) | 200 |
| tdwell | (s) | 10,800 |
| Npulses, full-power |  | 3000 |
| Npulses, 2/3 current |  | 30,000 |
| Max pulses/storage |  | 8 |
| Max pulses/week |  | 20 |
| Max no. RT cooldowns |  | 50 |
| Storage tank drawdown |  | 0.8 |
| Storage tank boiloff |  | 0.1 |
| J/cooldown | (GJ) | 110 |
| J/cooldowns, lifetime | (GJ) | 5,500 |
| Pradiation, in | (kW) | 59.0 |
| Pradiation, outside | (kW) | 7.48 |
| Pconduction | (kW) | 3.145 |
| P,xfer lines | (kW) | 15 |
| Pleads, TF | (kW) | 10.4 |
| Pleads, PF | (kW) | 11.1 |
| Pdiss, TF | (MW) | 1.49 |
| Pdiss, PF | (MW) | 0.633 |
| Pdiss, total | (MW) | 2.21 |
| Pleads, total | (kW) | 21.52 |
| Pidle | (kW) | 95.4 |
| Ptotal | (MW) | 2.234 |
| lN2 flow, Total | (kg/s) | 15.13 |
| Volume, lifetime, total lN2 | (gal) | 8.78 x 108 |
| lN2 usage/pulse | (kgal) | 53.49 |
| lN2 Storage tank requirement | (kgal) | 594.4 |

The nitrogen storage tanks are sized for a two-day supply of nitrogen at 4 shots/day.  The energy needed for cooldown from room temperature was calculated to be equal to 12 days of idling losses.  Therefore, the magnet system is kept cold over the weekend and there are only 50 room temperature cooldowns during the machine life. The refrigerator is not sized for daily cooldown from room temperature. The magnets are kept cold overnight and weekends, and only warmed up to room temperature during maintenance periods.  Despite the increase in the peak temperature to 370 K at the end of a pulse, the energy required for cooldown is nearly five times higher than that for recool, and it would take 12 days for heat leakages to warm the magnets to room temperature.  Heaters are used on vent lines to prevent condensation plumes of liquid nitrogen.

III.	Cryoplant Topology

The overall cryoplant design of FIRE was originally based on those of CIT and BPX. Major design features include the following:

- Large liquid nitrogen storage tanks and fill stations are used, instead of a closed-cycle nitrogen refrigerator. However, in FY99, FIRE agreed with CIT, BPX, and Alcator that truck deliverires from a commercial air liquefaction plant must be most economical, because of the pulsed nature of the load. This was reviewed in FY00 and both BOC/AIRCO and Air Liquide recommended the construction of dedicated on-site or near-site nitrogen plants.  The design still includes on-site liquid nitrogen storage.

- FIRE uses the Alcator C-Mod method of one pump and individual regulator valves for each flow circuit. This provides close to optimized cooldown and has proven to be very reliable.

- A subcooler is used, as in the BPX and CIT designs, in order to provide 80 K liquid nitrogen to the coils.  The boiling temperature of nitrogen at 10 atmospheres is 105 K.

- The secondary circuit of CIT is eliminated by BPX and FIRE. The amount of radioactive nitrogen-13 generated in FIRE is small, because of the much smaller volume of unshielded nitrogen inventory. Even without holdup, the nitrogen-13 discharge would be within allowables for most site boundaries. The cryogenic system provides one day’s holdup for nitrogen-13, which has a half-life of ten minutes.

| Figure 1: Option 1: Temporary Storage of Irradiated Gas after Pulse, Open Secondary | Figure 2: Option 2: Open Nitrogen Loop with Helium Purge |
| --- | --- |
| Figure 3: Option 3-Closed-loop Secondary N2 Circuit (BPX/CIT) | Figure 4: Option 4: Closed-Loop Helium Secondary |

The relative costs of the five options are compared in Table II:

Table II: Relative Costs of Five Refrigerator Topology Options

| Refrigerator Option | PACE, min | PACE, max | Total |
| --- | --- | --- | --- |
| 1a Open N2, Holdup all N2 | 9.04 | 12.2 | 16.7 |
| 1b Separate holdup streams | 5.51 | 8.64 | 11.8 |
| 2 Open N2, He purge | 5.46 | 8.59 | 11.8 |
| 3 Closed-loop lN2 Secondary | 5.97 | 9.1 | 14.6 |
| 4 Closed-loop He Secondary | 13 | 16.1 | 22.1 |

The performance tradeoffs are summarized as numerical rankings in Table III:

Table III: Cost/Performance Rankings of five refrigeration system options

| Refrigerator Option | Cost | N13 Generated/Released | Recool Time |
| --- | --- | --- | --- |
| 1a Open N2, Holdup all N2 | 4 | 3 | 2 |
| 1b Separate holdup streams | 2 | 4 | 5 |
| 2 Open N2, He purge | 1 | 2 | 2 |
| 3 Closed-loop lN2 Secondary | 3 | 5 | 1 |
| 4 Closed-loop He Secondary | 5 | 1 | 4 |

Option 2 was selected as the new reference design, because it had the best overall combination of low cost, radioactivity, and recool time, as shown in Table III.  All parameters have been updated to correspond to the CY2002 FIRE* reference design at Ro=2.14 m.

##### IV.. Cost Algorithm

New pricing information was solicited on the cost of vacuum-jacketed piping, unjacketed piping, elbows, and valves.  A new set of cryogenic equipment costing equations were derived on the basis of the data base and are listed in Table IV.  Although impressively large at first glance,  the data base is still not adequate.  In particular, we haven't obtained good recent pricing on large cold boxes, nitrogen gas bags, heaters or blowers.  However, because of the need to begin comparing different design options, an interim set of costing equations was derived, based on previous cost studies.  This will be updated as new information becomes available.

Table IV: Cryogenic Equipment Costing Equations

| Component | Equation | Notes |
| --- | --- | --- |
| Pump/Compressor | $273/gpm | Liquid nitrogen, Barber-Nichols quote |
| Cold Box | $4500/To (Q)0.7 | Slack formula, ratioed to BPX subcooler cost x 1.5 for inflation, Q is in W; To is the outlet temperature |
| Vacuum jacketed pipe | $164 Di ($/m) | Di=Inner diameter in inches,PHPK quote |
| Unjacketed pipe | $73/m (Dt) | Dt=Inner diameter thickness product in inches, Stainless Tubular Products |
| Valves Throttle Shutoff Relief | $267 Di2.27 $180 Di2.27 $140Di2.27 | PHPK quote; relative prices from BPX; Di in inches. |
| Controller | $150 k-Hardware $250 k-Labor | 40 % deflation since BPX |
| Blower | $300/hp | BPX x 1.5 for inflation |
| Nitrogen heaters | $250/kW | Scaled from intepretation of BPX, x 1.5 for inflation |
| Filters | $500/gpm | Scaled from interpretation of BPX, x 1.5 for inflation |
| Storage Bag | $30/m3 | Robinson's eqn. x 1.5 for inflation |
| Storage Tank (vacuum insulated) | $8/gal (250 MAWP) $5/gal (40 MAWP) | Taylor-Wharton quotes |
| Local I&C | $400 k | 40 % deflation since BPX |
| Contingency | 16 % of PACE subtotal | Ratioed from BPX |
| Assembly, Installation & Test | 18 % of PACE total + contingency | Ratioed from BPX |

The cryogenic load for all options is summarized in Table I:

# V. Sizing of the Design Options

A sizing workbook was developed for the four design options with five worksheets.  The first (reference) option of storing the radioactive gas after a shot for three hours between shots was subdivided into an Option A, in which all of the nitrogen used in one shot, including that used for recooling, is stored temporarily, and an Option B, in which the magnets are purged both before and after a shot, and only the purged gases are stored.  Option 2, described below in more detail, is sized in Worksheet 3 of the Workbook “Mag Refrig Design Scaled to 2.14 m.xls”.

## Sizing of Option2: Open Nitrogen Loop with a Helium Purge

If the liquid nitrogen were purged by helium before a pulse, then essentially no radioactive gas would be generated by the pulse.  Any imperfectly shielded nitrogen atmosphere in the cel is not considered here.  There would then also be no need to purge the magnet vapor after a shot and recool could begin immediately with no temporary storage.  The disadvantage is that pressurized helium storage and a helium-nitrogen heat exchanger have to be added to the cryogenic system.  There is also a modest amount of helium that is vented and has be to be purchased.  Option 2 is illustrated by Figure 5 and sized in Table V.

Figure 2: Open Nitrogen Loop with Helium Purge

The sizes of the cryogenic refrigerator components in Option 2 are listed in Table V.

Table V: Component Sizes of Option 2 with an Open Nitrogen Loop, Helium Purge, and without Temporary Storage

| Units | Parameter | Value |
| --- | --- | --- |
| (kgal) | lN2 Storage tank requirement | 594.4 |
|  | nstorage tank shutoff valves | 4 |
| (in) | Dstorage tank shutoff valves | 12 |
|  | Nitrogen Supply to Magnets |  |
| (m) | Lcold nitrogen piping | 200 |
| (m) | L 8" lN2 vacuum-jacketed pipe | 100 |
| (kg/s) | Average nitrogen pumping reqmnt | 15.13 |
|  | Peak/average pumping ratio | 2 |
| (kg/s) | Peak nitrogen pumping reqmnt | 30.26 |
| (gpm) | Peak nitrogen pumping reqmnt | 594.4 |
|  | nRegulator valves to magnets | 3 |
| (in) | Dregulator valves to magnets | 10 |
|  | nfilters | 4 |
| (gpm) | Total gpm, premagnet filters | 594.4 |
|  | nMisc 12" shutoff valves | 6 |
| (in) | Dmisc shutoff valves | 12 |
|  | Purge requirements |  |
|  | Equivalent flush cycles | 4 |
| (m) | Flush length | 50 |
| (in) | Di, flushed pipes | 12 |
| (m^3) | V, flushed pipes | 3.6483 |
| (m^3) | V, magnet channels, headers | 1 |
| (m^3) | V, total flushed volume | 4.6483 |
| (m^3) | V, all flush cycles | 18.59 |
| (kg) | M, He gas purges | 197.088 |
|  | nshots/Pressurized He tank capacity | 4 |
| (m^3) | Volume, 18 atm pressure vessel,supply | 271.845 |
| (in) | Di, shutoff valve, He purge stream | 12 |
| (m) | L,addit'l pipe, separate flush exhaust | 100 |
| (in) | Di, regulator valve, He purge stream | 12 |
| (s) | Total flush time | 600 |
| (kg/s) | Average mass flow, flush stream | 0.32848 |
| (W) | Q,He-lN2 heat exchanger | 1908.3 |
| (kW) | Average heater power, flush stream | 0 |
| (in) | Di,addit'l pipe, separate flush exhaust | 12 |
| (in) | t,addit'l pipe, separate flush exhaust | 0.375 |
| (s) | Emptying time before shot | 600 |
| (kg/s) | Blower capacity | 272.4 |
| (hp) | Blower power | 3,120 |
| (m) | Lcold exhaust pipe | 100 |
| (m) | Lwarm exhaust pipe | 100 |
| (in) | Dicold exhaust pipe | 16 |
| (in) | Diwarm exhaust pipe | 16 |
| (in) | n,vent valves x Di,vent valves | 2x12 |
| (kg/s) | Peak mass flow through gas storage line | 30.26 |
| (kW) | Heater power | 64.66 |

VI. Costing of the Design Options

Having sized the individual components and proposed a set of costing equations, it is now possible to compare the costs of the five design options.  Each option was costed according to the costing rules in Table IV.  The cost of Option 2 is given in Table VI, below.

Table VI: Cost of Option 2 with an Open Nitrogen Loop, Helium Purge, and without Temporary Storage

| Units | Parameter | Value | Unit Cost | Cost |
| --- | --- | --- | --- | --- |
|  |  |  |  | (k$) |
| (kW) | Subcooler Heat removed from 1o stream | 1081 | 4500 | 1107.18 |
| (kgal) | lN2 Storage tank requirement | 594.3 | 5000 | 2971.8 |
| (in) | Dstorage tank shutoff valves | 12 | 180 | 202.8 |
| (m) | L 8" lN2 vacuum-jacketed pipe | 100 | 164 | 131.2 |
| (m) | L 8" lN2 vacuum-jacketed pipe | 100 | 164 | 196.8 |
| (gpm) | Peak nitrogen pumping reqmnt | 594.4 | 273 | 162.3 |
| (in) | Dregulator valves to magnets | 10 | 267 | 149.2 |
| (gpm) | Total gpm, presubcooler filter | 594.3 | 500 | 297.18 |
| (gpm) | Total gpm, premagnet filters | 594.3 | 500 | 297.18 |
| (in) | Dmisc shutoff valves | 12 | 180 | 304.2 |
| (kgal) | Volume, 18 atm pressure vessel | 71.8 | 5000 | 359 |
| (in) | Di, shutoff valve, He purge stream | 12 | 180 | 50.7 |
| (m) | L,addit'l pipe, separate flush exhaust | 100 | 73 | 32.85 |
| (in) | Di, regulator valve, He purge stream | 12 | 267 | 75.2 |
| (W) | Q,He-lN2 heat exchanger | 1908 | 10000 | 24.74 |
| (hp) | Blower power | 3120 | 300 | 937 |
| (in) | Dicold exhaust pipe | 16 | 73 | 58.4 |
| (in) | Diwarm exhaust pipe | 16 | 73 | 58.4 |
| (in) | Di,vent valves | 12 | 180 | 101.4 |
| (kW) | Heater power | 6466 | 250 | 3233 |
|  | Instrumentation and Control |  | 400 | 400 |
| (M$) | PACE, subtotal, min |  |  | 6.08 |
| (M$) | PACE, subtotal, max |  |  | 9.58 |
| (M$) | Contingency |  | 0.16 | 1.53 |
| (M$) | PACE+Contingency |  |  | 11.1 |
| (M$) | Assembly, Installation & Test |  | 0.18 | 2.00 |
| (M$) | Grand Total |  |  | 13.1 |

Although Option 2 requires a helium cold box and temporary helium storage, their cost is relatively low, since the helium isn't needed for magnet heat removal, but merely for purging the nitrogen volume.

.

The closed-loop helium secondary is the most expensive of the five options, because of the requirement for a cold box, compressor, and helium storage tank that is adequate for magnet cooldown.

The minimum value assumes that nitrogen vendor provides all of the liquid nitrogen storage tanks and the pipes and valves to the entrance of the reactor cell.  The maximum value assumes that these are purchased by the project.

The minimum value assumes that nitrogen vendor provides all of the liquid nitrogen storage tanks and the pipes and valves to the entrance of the reactor cell.  The maximum value assumes that these are purchased by the project.  The cost and cost/performance comparisons of the five options are given above in Tables II and III.

VII. Cost of Nitrogen

The cost of the cryogenic refrigeration system remains small in comparison with the cost of nitrogen over the course of the project.  The energy dissipation in the TF coils is known to be 14.1 GJ in a single simulation and 6.0 GJ in the PF coils.  Scaled energy dissipation in the TF coil is based only on P. Titus’ observation that overall dissipation seems to track hot spot temperature over a variety of paths to that hot spot temperature.  The lifetime ohmic dissipation is based on the specification of 3000 full-power shots and 30,000 shots at 2/3 of peak current, along with an assumption that the partial power shots averaged 4/9 the dissipation of the full-power shots.  Titus has shown a broad range of tradeoffs between nitrogen and power supply requirements vs. cooldown time.  We retain the previous assumption of 4/9 dissipation for this study, although it’s somewhat arbitrary, because we don’t have any better logic and don’t want to confuse independent effects.  This study is focused on calculating the change in cost, due to increasing the size of FIRE from Ro=2.0 m to Ro=2.14 m.

BOC gave pricing for a 10 year lease and a 15 year lease, as listed and scaled  in Table VII:

Table VII: Nitrogen Cost Estimates

| Total Cost | Units | 2.0 m FIRE | 2.14 m FIRE |
| --- | --- | --- | --- |
| 10 Year Commitment | (M$) | 143 | 163 |
| 15 Year Commitment | (M$) | 107/118.5 | 123 |

The penalty for purchasing more nitrogen/year over 10 years seems ridiculously high, but is based on a quote of 20 cents/100 cu ft of liquid nitrogen for a 10 year lease and 15 cents/100 cubic feet for 15 years.  It’s always possible that the BOC representative didn’t understand that it was a fixed total, but that’s what I got.  Also, the reason for the second cost for the 15 year lease/2.0 m FIRE is that the price/100 cubic feet is a constant, down to 75 % of nominal usage.  After that it would be flat, so that BOC/AIRCO would collect $8.5 M/year, even if the facility never ran.

VII. Conclusions

A methodology has been developed for comparing different refigerator design options.

Three of the five options were relatively inexpensive and difference between their costs within the uncertainties of the costing exercise.  These were 1) Open N2 system with a helium purge, 2) Open N2 with a nitrogen purge and two exhaust lines, and 3) Closed-loop lN2 Secondary.

The open N2 system with a helium purge also had high-rankings in low generation and release of N13 and recool time, although the difference between all of the sytems may be relatively small in both categories.

The closed-loop lN2 secondary costing is probably optimistic, since it doesn't include an emergency nitrogen holdup system.

Option  2 was selected, Open N2 with a helium purge, the new reference design with Option 1a, Open N2, N2 purge, and  separate holdup as the backup design.

The costs of the cryogenic refrigeration system were updated for the FIRE* Option, the CY2002 reference design.  The overall cost of the cryogenic system increased 11 % from to $11.8 M to $13.1 M, scaling a little less rapidly than the 14 % increase in the size of the TF magnets.

The cost of liquid nitrogen is scaled linearly with the losses and increases by 14 %, ignoring anomalies in available costing information.

# Footnotes

R.B. Fleming and G.D. Martin, "Liquid nitrogen cooling for the Compact Ignition Tokamak," Knoxville, SOFE 13, 1989

R.B. Fleming and G.D. Martin, “System Description, Cryogenic System, WBS Q: BPX Design Description Document,” Feb 13, 1991

H. Khater, Sec. 5.8, this report