July 22, 1994

Contract # TW0592

SPECIAL SPECIFICATION

SECTION 15175

CLEAN ROOM CEILING SYSTEM

Page

PART 1 - GENERAL

1.01 Description.	2

1.02Related Work	3

1.03Quality Assurance.	4

1.04References.	4

1.05Submittals..	5

1.06 Delivery, Storage, and Handling.	5

PART 2 - PRODUCTS

2.01Acceptable Manufacturers and Contractors.	8

2.02 Clean Room Ceiling Grid Module Design Requirements.	8

2.03 Ceiling Grid Module System.	10

2.04 Auxiliary Ceiling Grid Components.	11

2.05 Lighting Systems.	15

2.06 Configuration.	17

PART 3 - EXECUTION

3.01 Installation/Application/Erection.	18

3.02 Penetrations.	19

3.03 Field Quality Control.	19

SPECIAL SPECIFICATION

SECTION 15175

CLEAN ROOM CEILING SYSTEM

PART 1 - GENERAL

1.01   DESCRIPTION

A.  	This section covers the work necessary to fabricate, furnish, and supervise the erection of the Sandia National Laboratory (SNL) Building 870 clean room ceiling system.  Work shall include the following:

1.  	Ceiling filtration system with high efficiency particulate air (HEPA) filters, support grid modules, flush mounted lights, sprinkler penetrations, and intermediate supports.

2. 	In-place testing of all components of the filter ceiling system as described in Paragraph 3.03.

B.  	In the event of conflict regarding the clean room ceiling system, requirements between this Section and any other section, the provisions of this Section shall govern.

C.  	The Clean Room Ceiling System Contractor shall be fully responsible for a leak free filter/ceiling system.

1.  	An independent Clean Room Certification Contractor will be employed under Section 15055 upon completion of work to certify the facility at Class 100 and 1,000 on 0.50 one-millionth-of-a-meter (micron) at "as-built" condition.  Certification will be based on Class 100 on 0.50 micron. (No more than 100 particles per cubic foot (ft3) of 0.50 micron or larger particulate.) and Class 1,000 on 0.5 micron (No more than 1,000 particles per ft.3 of 0.5 micron or larger particulate.).

2.  	All rework and retesting shall be at the Clean Room Ceiling System Contractor's expense and no cost to SNL.

D.  	System Description

1.  	Ceiling grid modules shall be factory assembled and painted containing inverted channel filter support grid, sprinkler penetrations, flush mounted linear fluorescent light fixtures, internal lamp reflectors, single point termination for lighting terminal boxes, provisions for connection to adjacent ceiling grid modules, air flow diffusion elements, provisions for an overhead support system with threaded rods, and provisions for connections to adjacent ceiling grid modules.

2.  	HEPA filter modules shall be provided by the manufacturer from among pre-approved filter manufacturers, arranged to be compatible with the specific channel grid.

3.  	The air handling units are remotely located.

4.  	The Drawings detail size and grid orientation for ceiling grid modules.

5.  	Perimeter filler panels shall be provided by manufacturer as required.  Blank ceiling filler panels shall be provided as indicated and required on the Drawings.

6.  	The Specifications and the Drawings describe the criteria and features required for the ceiling.  The manufacturer may submit pricing options, accessories, or other features that would enhance the installation, cost, or performance in SNL's best interest.

E.  	Bids

1.  	The ceiling manufacturer shall state in the base bid which of the approved filter manufacturers has been included in the base bid for the entire modular ceiling grid.

2.  	The ceiling manufacturer shall state in an alternate bid the price for each of the other approved filter manufacturers.  SNL retains the right to select one of the alternative manufactures as desired for standardization of its site filter inventory.

1.02   RELATED WORK

A.  	Section 01300

B. 	Section 15010

C.  	Section 15023

D.  	Section 15501-S

E.  	Section 15055

1.03   QUALITY ASSURANCE

A.  	The materials and methods of construction for the clean room modular ceiling system and accessories hereinafter specified shall comply with the current editions (unless specifically indicated otherwise), of the practices, methods, or standards prepared by the applicable technical societies and associations listed in Section 15023 of these specifications.

B.  	SNL or its representative shall maintain the right to tour the clean room ceiling manufacturer's plant anytime that fabrication is being performed on components intended for this project.

C.  	The manufacturer shall notify SNL when production is finished on the components.  Anytime after that date, SNL may exercise the option, giving 24-hours advance notice, to tour the plant and inspect for component assembly, painting, cleaning, or packaging to ensure that quality control has been maintained.

D.  	All wiring shall conform to the requirements of the National Electrical Code and the Standards for Safety of Underwriters' Laboratories, Inc. (UL).

E.  	All electrical components shall be UL listed and labeled.  Filters shall be FM approved.

1.04   REFERENCES

A.  	Institute of Environmental Sciences (IES), IES-RP-CC006 Recommended Practices for testing Clean Rooms

B. 	 Uniform Building Code (UBC)

C.  	American Iron and Steel Institute (AISI), "Specifications for the Design of Cold-Formed Steel"

D.  	National Electrical Code (NEC)

E.  	Underwriter's Laboratories (UL), "Standards for Safety"

F.  	American National Standards Institute (ANSI), ANSI C82.1

G.  	Federal Communications Commission (FCC)

H.  	Code of Federal Regulations (CFR), CFR47 Part 18

I.  	American Society for Testing and Materials (ASTM), ASTM C636

J.  	Federal Standard 209E, "Airborne Particulate Cleanliness Class for Clean Rooms and Clean Zones"

1.05   SUBMITTALS

A.  	Make submittals according to this Section, Section 15010, and Section 01300.

B.  	Submit product information showing compliance with this Section for review prior to manufacturing.  Include the following:

1.  	Shop and erection drawings showing all types, profiles, sizes, gauges, finishes, dimensions, components, fittings., fasteners, welds, positions, spacing, openings, connections, welding processes, etc., for the fabrication and erection of the clean room ceiling grid system.

2.  	Structural drawings and calculations showing support member sizing, member connections details, sway bracing provisions, and size and location of loads imposed on the structure.

3.  	Electrical lighting calculations that show room cavity ratio, reflectance (ceiling/wall/floor), coefficient of utilization, lamp lumen depreciation, luminaire dirt depreciation, and average maintained foot candle levels based on the use of white lamps throughout.  Drawing showing ballast locations, manufacturer and catalog number of all components, and wiring diagram for each plenum.  Schematic drawings showing wiring between terminal cabinet/ballast enclosure to lamp-holders.  Manufacturers catalog sheets shall also be submitted.

4.  	A copy of all welder's certifications and welding procedures for review prior to any welding.

C. 	Required with the Bid

1.  	A list of five successfully operating installations similar in capacity, application, and equipment type within the continental United States.  Minimum service time on these installations shall be 2 years.

2.  	Cross-sectioned drawing showing the configuration of components, access panels (where necessary), and outside dimensions.

3.  	Detailed information on structural, mechanical, electrical, and other services necessary to evaluate installation requirements.

1.06   DELIVERY, STORAGE, AND HANDLING

A.  	It shall be the requirement of the manufacturer to provide at their facility a controlled area for the purpose of final cleaning and packaging of equipment.  This area shall be at least Class 10,000 per Federal Standard 209E.

B.  	By "clean" it is meant that all housing and equipment components will be thoroughly cleaned of all oils, grease, lubricants, dirt, and dust prior to assembly.

C.  	After assembly and test, but prior to shipment, all interior surfaces and equipment shall be wiped down with approved cleaner and vacuumed (HEPA type only).

D.  	Visual inspection without magnification shall be conducted over 100 percent of the surface.

E. 	Low-shedding materials shall be used for wipe cleaning.

1.  	Approved types

a. 	Touch-and-Go polyurethane foam, Sills & Assoc.

b. 	Texwipe cloths, Texwipe Company.

c. 	Nylon Tricot 1068 cloths, Laminaire Company.

d. 	Miracle Wipe, International Clean Products.

F.  	As preparation for shipment, all openings shall be sealed against dust, dirt, or moisture and weather protected.  Provide coverings that will remain intact during shipment.  Immediately after cleaning, the units shall be shrink wrapped with clean, acceptable plastic then double bagged and sealed with 4-millimeter plastic.  These units must also be protected with plywood exterior to the plastic, and strapped tight with a suitable method.  All components attached to the unit must also be protected in a similar manner.  All equipment must be protected from contamination during the manufacturing process through start-up procedures and SNL acceptance.

G.  	Filters

1.  	The filters shall be separately packaged.  Each filter module shall be wrapped in two protective polyethylene bags and packaged in an individual carton.  Protective sleeves shall be inserted between the filter module and the carton walls.  The packaging shall be such that sufficient protection of the bare media will be provided.  Each carton and each filter module shall display the manufacturer's label on the 2-foot end, oriented to read from the clean room side, indicating the model number, serial number, efficiency at maximum penetrating particle size, rated airflow, total pressure drop, and test results for the individual module.  A shock sticker will be attached to each pallet of filter cartons.

2.  	Filter packing cartons shall be loaded on shipping pallets with all labels oriented to one end of the load.  Filter cartons shall be placed on the long side arranged three across and three high.  Provide hardboard protective sheet along both long sides of the pallet.  Strap the entire pallet, then cover with protective polyethylene wrap.  Attach the shock sticker to each pallet where it is readily visible.

3.  	Pallets shall not be stacked for shipment.  All filter pallets shall be shipped via dedicated air-ride enclosed van directly  from the filter manufacturer to the job-site.

4.  	A representative of the manufacturer shall be present to supervise the unloading, inspection, handling, and storage of filters upon receipt of the job-site.

5.  	Filters shall not be uncrated until they are ready for final inspection and installation.

6.  	Immediately upon receipt, each carton shall be visually inspected by SNL for shipping damage, such as crushed corners or sides, broken shock sticker, punctures or any other deformation which would indicate possible damage to filter media, frame, gasket or any part of the filter unit.  Any deformed cartons shall be opened and the extent or damage shall be accessed.

7.  	Obviously damaged filters shall be segregated from undamaged cartons and returned to the factory.

8.  	All filters with deformed cartons, and all filters from pallets with broken shock stickers, shall be segregated for field bench testing by the manufacturer.

9.  	After visual inspection of cartons, filters shall be placed in storage location where they may remain until they are ready for testing and installation as directed by SNL's representative.  MINIMAL handling and moving of filters is essential.  Care must be taken to eliminate dropping of cartons, vibration, excessive movement, and rough handling.

10. 	Filters and ceiling grid modules awaiting installation shall be stored in accordance with the manufacturer's instructions.

H.  	Units must be shipped in a flat bed closed truck (rag top) or approved alternate.

I.  	SNL may inspect the cleaning, packaging, and shipping procedures of all plenum module units and randomly selected ceiling grid module units to ensure compliance.  The SNL shall also have the right to randomly select units for inspection at various intervals, without notification to the manufacturer.  All units must pass engineer's inspection prior to SNL's acceptance.  Units not meeting acceptance cleanliness, packaging, and shipping specifications during any of the above mentioned processes will not be acceptable, and shall be brought to acceptance within specifications immediately at no additional cost.

PART 2 - PRODUCTS

2.01   ACCEPTABLE MANUFACTURERS AND CONTRACTORS

A.  	Ceiling Grid Module Manufacturers

1.  	Flanders

2.  Pace Clean-Pak

3.  Daw Technologies, Inc.

4.  Clestra Co.

B.  	HEPA Filter Module Manufacturers

1.  Flanders

2.  American Air Filter

3.  Filtra

C.  	Clean Room Certification Contractors

1.  Biocon - Raleigh, N.C.

2.  Clean Room Sciences - Phoenix, Arizona.

3.  Dryden Engineering - Santa Clara, CA.

4.  Air Filtration Management - Bethlehem, PA.

2.02   CLEAN ROOM CEILING GRID MODULE DESIGN REQUIREMENTS

A.  	Vertical Design and Deflection Requirements

1.  	Applied Dead Load:  Actual weight of ceiling grid module (25 pounds-per-square-foot minimum), sprinklers, lighting, ballasts, conduit, terminal boxes, and fire protection piping.

2. 	Deflection:  1/8-inch maximum under full dead load.

3.  	Hangers:  Each 2-foot (ft) by 4-ft grid section of the grid system shall be supported from the overhead superstructure by four 3/8-in. threaded rods.  Each rod shall be connected at one end to turnbuckles.  The turnbuckles shall be attached to tapped bosses in the castings of the grid system.  The turnbuckle assembly in the overhead structure shall permit final leveling of the grid.

B.  	System and bracing designs shall be in conformance with UBC and AISI "Specifications for the Design of Cold-Formed Steel."  Lateral seismic loads shall be based on UBC using Z = 0.22, I = 1.25, and Cp = 1.5.

C.  	System design shall accommodate construction tolerances, deflection of building structural members, and clearances of intended openings.

D.  	Fire Sprinkler head placement shall be based on coverage as specified on the Drawings.

E.  	Lighting Design Requirements

1.  	Flush mounted fluorescent lighting system shall be furnished as specified herein and lamps located as shown on the drawings (electrical).  The lighting level shall be maintained at 150 footcandle.

F.  	Manufacturing Tolerances

1.  	HEPA Filter Module

a. 		Dimensions of Module: +0, -1/8 in., measured across the length and width of each module.

b. 		Squareness of Module:  +1/8 in., -1/8 in., measured across both diagonals of each module.

c. 		Pleat Straightness:  +1/16 in., -1/16 in., measured across the width perpendicular to the long side filter frame.

d. 		Pleat Depth:  +1/16 in., -1/16 in., measured through the pack.

e. 		Pleat Flatness:  +1/16 in., -1/16 in., measured at the leaving edge.

f. 		Pleat Pitch:  +1/16 in., -1/16 in., measured at the leaving edge.

g. 		Total Pleats:  +1 pleat from the average usable pleats of all filters in the ceiling.

h. 		Frame Flatness:  +1/8 in., -1/8 in., of one corner from its diagonally-opposite corner.

2.03   CEILING GRID MODULE SYSTEM

A.  	Ceiling Grid Module

1.  	The ceiling grid system shall consist of extruded aluminum channels.  The filter support grid shall consist of full module length runner extrusion welded to a perimeter extrusion frame sized to fit clean room design.  Cross members shall be welded to runner extrusions for a completely welded filter support frame and filter support grid.  No factory caulking/sealing shall be permitted to provide airtight grid construction.  Grid shall be caulked with an approved adhesive as necessary only to complete field joints in partial grids.  The ceiling support grid shall be structurally constructed to remain dimensionally stable and retain the necessary sealing requirements when the permissible hanging load is suspended from the grid.  The support grid shall be capable of withstanding 2-in. water gage (wg) of static pressure without deflection.

2.  	The grid portion of the ceiling support lattice shall be supported from an overhead support system with threaded rods as required, connected to threaded support points.  After the grid system has been completely sealed, it shall be water tested and be proven watertight.  The channel grid shall be arranged so that filters and other system components can be handled from below the grid system.

3.  	All metallic members shall be corrosion resistant materials and have finished coating of white powder coat epoxy finish.

4.  	The grid system shall be configured to provide a flush means of attaching automation systems, enclosures, and wall head tracks.

5.  	The sealant used in the grid channels shall be odor free, self-sealing, two-part biomed urethane base polymer and shall remain in place under static pressure of 10-in. wg.  Sealant shall not be fluid at temperature below 250-degrees Fahrenheit.  The sealant shall be field installed.

6.  	The grid system shall include sprinkler penetrations in the framing system at all sprinkler head locations as required by the Fire Protection Contractor with provision for airtight seals and escutcheons.

7.  	The ceiling grid module manufacturer shall coordinate with the Fire Protection Contractor to determine the placement of sprinkler heads for each area.

8.  	Sealer plugs, clips, or covers shall be furnished for field installation over all openings in the ceiling assembly left after mounting of all accessories.  Reveals to be sealed included air gap next to light fixture frame/lens, sprinkler heads, utility hangers, and empty grid channels.

9.  	The ceiling grid shall be arranged as indicated on the Drawings.

2.04   AUXILIARY CEILING GRID COMPONENTS

A.  	Blank Ceiling Filler Panels

1.  	Blank ceiling filler panels shall be constructed of aluminum with welded corners, designed to affect an airtight seal in the channel grid and shall function the same as the filter module skirt.  Both sides of the blank panel shall have a white powder coat epoxy finish.

2.  	Hold-down clips shall be used for positive seal of blank panel knife edge into the gel sealant.  Clip shall be suitable to resist positive pressure gradient on bottom clean room face of panel.

B.  	Perimeter In-Fill System

1.  	Provide acceptable perimeter in-fill system as required on Drawings to affect an airtight seal in ceiling channel grid.  In-fill system shall be constructed of aluminum panel with welded corners and shall function the same as the filter module skirt.  Both sides of panel shall have a white powder coat epoxy finish.

2.  	Hold-down clips shall be used for positive seal of panel knife edge into the gel sealant.  Clip shall be suitable to resist positive pressure gradient on bottom clean room face of panel.

C.  	HEPA Filters

1.  	The filters used in this system shall be replaceable, factory built modules consisting of extruded anodized aluminum cartridge frame with integral knife edge, secure corner assemblies, pleated media with uniform separation system, and perforated aluminum face screen.

2.  	Filters shall be nominal 24 in. by 48 in., by 4-in. deep or size as shown on the Drawings.

3.  	The cartridges shall be constructed of materials that have been qualified under U.L. Class I testing and shall be nominally 4-in. deep media pack rated at 720 cfm each at 0.4-in. wg clean air flow resistance at minimum efficiency of 99.99 percent on 0.30 microns of polystyrene latex (PSL) spheres.  Documentation of tests is required.

4.  	All filters shall have a resistance to airflow of within +10 percent of each other.  Velocity uniformity shall be +20 percent at 560 cfm.  Uniformity is based on 12-in. by 12-in. readings over the filter face area.

5.  	The filters shall be equipped with extruded and anodized aluminum knife edge around the downstream face.  The knife edge shall be continuously sealed to the frames of the filters with suitable adhesive color matched to the pleated material, or shall be an integral extension of the frame extrusion.

6.  	A perforated 12-gauge face screen shall be arranged to distribute filtered airflow across the adjacent grid to prevent stratification and regenerative contamination, screen shall be finished on both sides with powder paint epoxy to match the adjacent filter frames or grid trim pieces.  The screen shall be mounted at least 1/8 in. below the edge of the media.  The air pressure drop of the screen shall not exceed 0.05-in. wg at full flow.

7.  	The ceiling manufacturer shall be responsible for the construction, testing, scheduling, and installation of the filter modules selected as part of the ceiling assembly.  Filter construction and testing shall meet the following criteria:

a. 	Construction Criteria

1)  		The media shall be constructed by pleating a continuous sheet of molded paper back and forth so the media is self supporting without the use of metal separators.  The media separator shall be non-chafing against the media.

2)  		The filter media shall be all glass made from boron silicate micro-fibers containing waterproof binder.  A single batch of media paper shall be used for all filters with common efficiency criteria.

3)  		The filter pack shall be minimum 100 millimeter (4 in.) deep, permanently sealed to the frame of the module with a fire retardant solid urethane sealant.

4)  		Media within each module shall be one continuous run without seams, supports, or penetrations.  The support edge should be arranged so that it cannot be seen after the filter module has been placed in the ceiling grid.

5)  		Each filter will have a label with data of efficiency, pressure drop, serial number, model number, flow uniformity, media lot number, and test date, accommodated from the final filter quality approved tests.

6)  		Care should be used in the selection of paints, fluid seals, sealants, and other materials to avoid those which have high gas mass loss due to out-gassing.  Potting compounds or other adhesives shall be essentially non-out-gassing after a maximum 48-hour cure time at atmospheric conditions.  Where out-gassing is unavoidable, select products with an alcohol base.

7)  		The following materials are allowed in the construction, scanning, and repair of the filters.  Any other materials which the vendor wishes to use must be approved in writing by SNL.

a)  Anodized aluminum.

b)  Fiberglass.

c)  Silica.

d)  RTV 162, GM 802 by GE.

e)  RTV 732, for defect patching only.

f)  Silicone gel sealant.

8)  		Isopropyl alcohol (IPA) or IPA/deionized water mixture shall be the only cleaning solvent used on all aluminum components during assembly and final wipe-down.  All handling of filter modules and media packs must be preformed with clean room approved barrier gloves.

b. 		Testing Criteria

1)  		Each filter shall be factory tested to determine overall resistance to airflow.

2)  		Every filter shall be automatically scan tested per the following procedure.

a)  		The automatic scanning equipment will consist of a particle counter of at least between 0.20 to 0.30 micron particle size detection capability and 1 cfm flow rate.

b)  		The scanning shall be accomplished by passing the probe with overlapping strokes so that the entire area of the filter is sampled.  A separate pass shall be made around the entire periphery of the filter along the adhesive bond between the filter pack, the rigid frame and center divider, and at the four corners of the knife edge.  The probe shall be held 1 in. from the filter face.  The corner leaks in the frame will also be checked so that there is no particle leak in the space between the filter and the ceiling grid when installed.  The transverse velocity of the sampling probe shall be maximum of 10 feet-per-minute.

c)  		Factory testing of the filter modules shall be made using challenge aerosol spheres sized at 0.20 microns and larger.  The number of particles in the challenge will be a minimum 107 particles per ft3 of 0.20 microns and larger determined from the media efficiency tests.

d)  		The upstream particle challenge shall be monitored with a separate 1 cfm flow rate sampling laser particle counter (not photometer) with ability to measure between 0.24 microns and 0.8 microns across a minimum of 15 bins.  No sources of dilution will be allowed and the upstream challenge must be a minimum of 100 x 106 particles per ft3.  The procedure shall ensure that the upstream challenge is maintained by checking for a minimum of 1 minute during the scan test of each filter.  The verification of the upstream challenge must be maintained and routine scheduled reports submitted with the filters.  Data for each filter will be available to the SNL by the filter serial numbers.

e)  		Any single particle reading during the scanning process of 3 counts per second will necessitate that a 6 to 10-second sample be taken at that location.  If the 6 to 10-second reading is 50 particles or more, a full 1-minute count is taken for which the maximum allowable count is 200 particles.  Any location which exceeds this level is a significant defect which must be repaired.

f)  		If leaks are found in the filter, use RTV 732, RTV 162, or GM 802 by GE for patching of the filter media.  Patching shall be limited to four locations per filter, with no more that 1/2-in. square per patch.  Filters requiring further patching shall be rejected.  After repair, filters shall be rechecked to ensure a leak-free filter.

3)  		The following additional automatic scan tests will be performed by the manufacturer at the factory on every fifth filter manufactured.  This testing will be done for 20 percent of the filters manufactured in a sequential order so that these tests represent the quality of all the filters manufactured for this project.  If every fifth filter does not meet the criteria for the tests as given in this Specification, all four filters manufactured prior to and after the test filter will be tested.

a)  	Efficiency by dual laser spectrometer.

b)  	Airflow uniformity with protective screen.

c)  	Automatic scanning as noted above.

d) 	Pressure drop of the whole module.

e)  		All tests will be conducted introducing the air to the filter by a method simulating actual field operation of the filter.

4)  		Procedures describing the above testing and routine scheduled reports will be submitted with the filter.

5)  		Each filter shall be individually tracked through manufacturing process to record what media lot was used, what roll of media was used, date filter was made, number of leaks and size of patch, etc.

6)  		Each filter shall have a label affixed to the exterior frame showing filter tracking number, efficiency (based on patch efficiency test), pressure drop, and number and size of patches that were required during leak testing.

D.  	Accessories and Spare Parts

1.  	The filter manufacturer shall provide a special filter holding fixture constructed to compensate for the knife edge skirt and permit the filter module to be transported and temporarily stored on its side.  Filter modules shall never be placed on face or back sides.

a. 		Sufficient floor holding fixtures shall be built as required for handling and testing filters within the manufacturing plant.

b. 		Two floor holding fixtures shall be included with the first filter shipment to permit unpacking and installation in the field.

2.  	The filter manufacturer shall provide an additional 5 percent of spare constructed filter modules to the job-site to permit immediate replacement of damaged filters or addition of area filter coverage.  Any modules used to replace defective filter shall be replaced as specified.

2.05   LIGHTING SYSTEMS

A.  	General

1.  	Luminaries (including lamp ballast and wiring between ballast and lamps) shall be integral and recessed with clean room ceiling grid.  Complete lighting system of lamps, lamp-holders, lenses, wiring, and ballasts shall be furnished and installed as part of the ceiling module.  Lighting system provided shall be 277 volt.

2. 	 Lighting levels shall be maintained at 150 footcandles.

3.  	All electrical work shall comply with the 1993 National Electrical Code and the Standards for Safety of Underwriters' Laboratories, Inc. (UL).  All electrical components shall be UL listed and labeled.

B.  	Wiring

1.  	Lamp-holder to Ballast shall be with insulated 18-gauge copper conductors secured to grid.

2.  	Wiring within grid shall be contained within and protected by sheet metal enclosure and adequate means utilized to prevent chaffing of wire insulation.

3.  	For Ceiling Grid Module System:  Ballast primary wiring from ballasts shall be 18-gauge (minimum) solid copper wire and terminated on terminal blocks located above the grid on filter modules.  Terminal boxes shall be located above the ceiling grid modules.  See Drawings.

4.  	Ground wire shall be provided between ballast/grid.

5.  	All above grid module wiring conduits shall have conduit seals.

C.  	Lamps

1.  	Lamps shall be 4-ft. T-8, 32W, 3500K, rapid start, Order Code #F32T8/TL835, manufactured by General Electric Company, GTE Sylvania, Inc., North American Phillips Lighting Corporation, or Westinghouse Electric Corporation.

2.  	Spare Lamps:  10 percent of total quantity installed.

D.  	Lens

1.  	Diffuser shall mount flush with plenum grid without external fasteners.

2. 	Clear acrylic wide angle prismatic diffuser, and opaque blank out strip shall be used.

3. 	Spare Lenses:  3 percent of total quantity installed.

4.  	Separately package lenses and blank out strips for each plenum and label indicating plenum number.

E.  	Ballasts

1.  	Integrated Circuit Electronic Fluorescent Ballasts:  ANSI C82.1; minimum power factor of 0.99, UL listed, Class P, Type 1, outdoor internally thermally protected.  Ballast shall operate lamps at a frequency of 20 to 35 Khz without a detectable flicker.  Ballasts shall provide soft start of rapid start lamps and shall meet requirements of FCC (CFR47 Part 18) for electromagnetic and radio frequency interference.

2. 	Ballast shall have less than 10 percent total harmonic distortion and less than 6 percent third harmonic distortion.

3. 	Ballast shall meet sound rating "A".

4.  	Ballast shall have a poke-in wire trap connector.

5.  	Acceptable Manufacturer:   Motorola, Magnetek.

6. 	Spare Ballasts:  Five of each size and type.

7.  	At least 20 percent of the fixtures supplied or the number shown on the Drawings shall contain one additional electronic fluorescent ballast as described above.  This ballast shall operate a single T-8 lamp inside each of these emergency fixtures and shall be energized from a separate emergency lighting circuit as shown on the Drawings.

2.06   CONFIGURATION

A.  	The ceiling grid module system shall be configured as indicated in the Drawings.

B.  	Ceiling grid modules and all internal components shall be factory painted with electrostatic powder coat epoxy after all prefabrication has been completed.

C.  	Refer to the Drawings for size and performance requirements.

PART 3 - EXECUTION

3.01   INSTALLATION/APPLICATION/ERECTION

A.  	General System Installation

1.  	The manufacturer shall provide field supervision for the complete installation of the ceiling assembly.

2.  	It is the intent that the grid system be installed to line and true level, symmetrical to room and spaces, and with due regard to appearance and structural stability.  The ceiling shall be level throughout within 1/8 in.

3.  	The grid modules shall be suspended directly from structural steel frame above in accordance with ASTM C 636 and the manufacturer's current printed instructions for the type of installation used.

B.  	Filter Installation

1.  	Filters shall be carefully removed from cartons and other packaging material.

2.  	A pre-installation filter leak field bench test will not be required for filters showing no physical signs of shipping damage.  The manufacturer shall perform field bench tests for all filters with shipping/handling damage as described in Paragraph 1.06 above.

3.  	The filters shall be installed in the support frames by personnel instructed in the proper method of installation and aware of the need for special handling precautions according to the manufacturer's instructions.  Continuous supervision shall be provided by the manufacturer to observe all stages of filter installation.

4.  	The manufacturer shall be responsible for the removal, replacement, and retesting of any HEPA filter failing the Certification Tests.

5.  	All filter modules installed within any single ceiling grid module shall have an airflow operating resistance within 5 percent of all others, a velocity uniformity of +20 percent at rated flow, and +25 percent at reduced flow.  Airflow uniformity shall be determined with two readings in each of the four quadrants measured 10 in. below the filter face.

C.  	Light Fixture Installation

1.  	Lamps and lenses shall snap in place to completely enclose fixture and provide a flush face of a grid finish.  Finished installation shall create a continuous strip of fixture lenses without any gaps or exposed cracks to capture dirt particles.

2.  	Responsibilities for installation of the lighting system shall be as follows:

a. 		Ceiling Grid Installation Contractor

1)  		Grid system module assembly complete with lamp, ballast, lamp-holders, wiring between lamp-holders and ballast and between ballast and terminal boxes.

b. 		Electrical Contractor

1)  		Installation of manufacturer-furnished lamps and lenses.

2)  		Termination of power supply conductors at terminal boxes.

3.02   PENETRATIONS

A.  	All penetrations in the clean room ceiling grid shall be pre-drilled and sealed at the factory.

B. 	No field drilling of the ceiling grid will be permitted.

C.  	All penetrations through the ceiling plane must be sealed airtight to prevent contaminant migration through the ceiling from the interstitial area into the clean room.

3.03   FIELD QUALITY CONTROL

A. 	In-Place Testing

1.  	When all filters have been installed, seals between filter and supporting framework and seals at perimeter of filter bank shall be scanned for bypass leakage.  Scan test may be made by either or both of the following methods and in accordance with IES-RP-CC-006.

a. 		Installation probe test with a discrete-particle counter using polystyrene latex (PSL) spheres sized at 0.20 microns and larger for the filter media supplied at sufficient amounts of challenge aerosol to attain uniform dispersement upstream of filters.

b. 		HEPA filter ceiling system shall be challenged with PSL spheres 0.20 to 0.30 microns having PSL concentration of 106 to 107 PSL per ft3 of challenged air.  The challenge downstream shall be no more than 0.01 percent of the upstream concentration.

1)  	Test apparatus shall include a sampling probe discrete particle counter and a challenge aerosol.

2.  	A particle count of greater than 100 particles per ft3 0.30 microns and larger shall be taken as indication of a leak(s) and further conventional scanning techniques shall be utilized to locate leak(s).

3.  	Aerosol particle size range shall be from 0.20 microns or larger for tests on the systems.

B. 	Manufacturer's Start-up Services

1.  	The manufacturer's service representative shall provide representations during initial start-up of the clean room in the presence of the SNL and the Engineer.

2.  	Upon completion of the inspections, start-up, testing, and check-out procedures, the ceiling manufacturer shall submit written notice to SNL that the units are ready for beneficial use by the SNL.

3.  	In order to establish the minimum service requirements, a manufacturer's representative for the equipment specified herein shall be present at the job-site for the minimum man-days listed, travel time excluded:  (Total)

a. 		Twenty man-days for installation supervision.

b. 		Five man-days for performance testing.

c. 		Five man-days for start-up and maintenance instructional time.

C.  	Testing and Certification:  The entire clean room will be balanced and certified by others.

D.  	Light Penetration Test

1.  	Final completion of the clean room ceiling construction must result in a room assembly which is airtight and watertight.

2.  	Contractor shall demonstrate that the finished ceiling assembly meets this criteria by performing visual bright-light test on all critical construction joints.

3.  	All construction joints shall be tested where ceiling grid modules connect to each other, in addition to all utility penetrations through the ceiling.

4.  	Tests will be performed using a minimum 400 watt light source inside the clean room, and an observer inspecting for light leakage at the test point inside the clean room.

5.  	All leakage points must be repaired and retested.

6.  	SNL reserves the right to witness confirmation tests on an unlimited number of points after field test have been completed to verify room integrity.

END OF SECTION