ACCIDENT DOSES ANALYSIS OF THE SOMBRERO

# INERTIAL FUSION ENERGY POWER PLANT DESIGN

S. Reyesa,b, J. F. Latkowskia, J. Gomez del Riob,and J. Sanzb

a Lawrence Livermore National Laboratory, P. O. Box 808, L-632,

Livermore, CA 94550, Tel: 925-424-5684

b UNED/ Dpto. Ingeniería Energética & Instituto Fusión Nuclear

E.T.S. Ingenieros Industriales, C/Ciudad Universitaria s/n, 28040 Madrid (Spain)

ABSTRACT

SOMBRERO (solid moving breeder reactor) is a conceptual design of a 1000 MWe laser-driven inertial fusion energy (IFE) power plant. An important goal of the original study was the achievement of a safe and environmentally attractive reactor of relatively simple design. However, recent work has pointed out some key issues involving safety that were not completely addressed at that time, and which need to be reviewed in order to maximize the SOMBRERO design attractiveness.

The present work uses a set of computer codes traditionally used for magnetic fusion safety studies (CHEMCON, MELCOR), which have been adopted and adapted for use in IFE safety analysis. Here we consider a loss of flow accident (LOFA) combined with a simultaneous loss of vacuum accident (LOVA) produced by a breach in the confinement building. Although confinement failure would be a very unlikely event, it must be postulated in order to produce significant off-site doses. The CHEMCON code is used to simulate the long-term thermal transient in the reactor structures resulting from oxidation and radioactive decay heat. MELCOR is used to simulate a wide range of physical phenomena including thermal-hydraulics, heat transfer, aerosol physics and fusion product release and transport. As specified in the DOE Fusion Safety Standards, an off-site dose below 1 rem (10 mSv) is the requirement to avoid public sheltering and evacuation.  The SOMBRERO accident analysis results will be evaluated according to this limit and suggestions will be made for improvements and future work.

I.	INTRODUCTION

Safety and environmental issues in the SOMBRERO IFE power plant design have been given a strong emphasis since the original report.1 The SOMBRERO concept uses a low activation material (C/C composite) in the chamber structures. The blanket consists of a moving bed of solid Li2O particles flowing through the chamber, eliminating the risk energetic chemical reactions usually associated with the use of lithium. The chamber is surrounded by a 1.7 m thick shield wall at a radius of 10 m with an additional 1 m thick confinement building wall at a radius of 55 m.

Since the time of the original study, the nuclear community (fission and fusion) has reached a consensus and established more restrictive safety goals. The DOE Fusion Safety Standards for public protection in case of accident give a limit off-site dose of 1 rem (10 mSv).2 This value is based upon a 1991 Environmental Protection Agency document that specifies the level at which sheltering and evacuation should be undertaken.3 Also since that time, new experimental data has been published on tritium retention in carbon/carbon composites,4 revealing the need for an updated safety evaluation of the SOMBRERO design.

In the present work, we have adopted the principle of considering a worst-case accident scenario. Here we assume a LOFA with loss of flow in the four circuits of the primary coolant loop. In addition, a 1m2 break in the confinement building wall is assumed, leading to a LOVA simultaneously with an air ingress event. Even though the probability of such a severe accident would be extremely low we must adopt a conservative methodology at this early stage, to later perform similar analyses considering more frequent and less severe accidents.

II.	COMPUTER CODES AND METHODOLOGY

In order to calculate off-site doses in a particular scenario, first we need to know the source term of radioactivity that is released to the environment. Neutron transport and activation, heat transfer, and thermal-hydraulics and aerosol transport calculations have been performed. Given the activity release and the specific dose of each isotope, the accident dose may be calculated.

Neutron calculations have been performed using TART5 Monte Carlo transport code. Activation of components and decay heat results were obtained from the ACAB6 activation code following 30 years of plant operation.

Prior to the calculation of radioactivity release fractions, one needs to know the temperature evolution of the different reactor components during the accident. The CHEMCON7 code is used to simulate the time-temperature histories of the structures during the transient, resulting from oxidation and radioactive decay heat. Some modifications have been introduced in the CHEMCON oxidation package for an enhanced tracking of the oxidation front. The temperature excursion of the different components is then used to determine the activation products source term available for mobilization, which will later be used as input data for the MELCOR calculations.8

MELCOR thermal-hydraulics code is used to simulate a wide range of physical phenomena including heat transfer, aerosol physics and fusion product release and transport. With these data about the radioactivity released, and the adequate dose conversion factors (DCF), off-site doses can be obtained. Data on DCF have been calculated using MACCS2 accident consequences code.9

III.	TIME-TEMPERATURE HISTORY OF THE REACTOR COMPONENTS

In order to calculate the temperature excursions of the different plant components one must account for the various energy sources existing during the transient. Three possible sources (fusion reactions, decay heat and oxidation heat) have been identified and will be discussed next.

Once the accident begins, it is conceivable that fusion reactions could continue to occur for a short period of time. During a LOFA accident about 0.44% of the graphite of the first wall is going to evaporate, increasing the carbon partial pressure of the reactor building by 1 torr and preventing the laser beam from propagating to the target. This way, no more fusion reactions would be possible and hence the reactor would be shutdown. Thus, the two only energy sources present in this scenario are the radioactive decay heat from activated materials and the oxidation heat from the exothermic combustion of carbon in presence of air. The decay heat is low enough to allow a rapid cooling of the first wall (FW) and blanket structures (the temperature of the FW drops below 1000 ºC in less than a minute). Fig. 1 shows the temperature evolution of the different components during the transient, due to the radioactive decay heat.

Figure 1. Time-temperature history of the various reactor components due to the radioactive decay heat.

To determine the importance of the oxidation of the carbon at those temperatures, we developed a CHEMCON model for SOMBRERO.1 The model included the carbon chamber structures, the Li2O blanket, inner shielding and confinement building. A series of iterations were made between the CHEMCON oxidation calculations and the MELCOR thermal-hydraulics code, to account for the oxygen diffusion through a time-dependant carbon-monoxide source (the current version of MELCOR does not account for oxidation of structures). It was found that even at temperatures below 1000 ºC the reaction rate was significant (the 1 cm thick first wall was oxidized in about 7 hours). Fig. 2 shows the temperature evolution of the various components when accounting for the air oxidation of the carbon structures.

Figure 2. Temperature evolution in the various reactor components due to oxidation and radioactive decay heat.

It must be noted that the correlations used by CHEMCON are based on experimental data of graphite oxidation with air dating more than 10 years ago. However, these results are meaningful given that the oxidation of the chamber structures would have a great impact on the radioactive mobilized fractions. All the carbon with its impurities and activation products would be mobilized in CO form, as would the tritium trapped in these structures. The activated Li2O granules would also be available for mobilization, but given the size of the particles this would be a minor contribution to the final released radioactivity fraction.

In order to avoid the oxidation of the SOMBRERO carbon structures in an air ingress event, several solutions will be discussed next. First, a passive safety feature such as an inert gas filled tank with a rupture disk, should be simple enough to implement. This would allow the gas to fill up the building when a certain differential pressure is reached, preventing the oxygen to reach the target chamber. Also, different oxidation experiments have been done with protective coatings on carbonaceous composite materials, such as Si-B-C coatings.10 Finally, alternative materials other than C/C composites should also be considered (some discussion has been already made about the usage of SiC in the blanket structures, keeping the high-conductivity C/C composite as first wall material).

IV.	ACTIVATION PRODUCTS SOURCE TERM

Assuming that the carbon structures of the FW/blanket assembly are going to suffer oxidation during the accident, there will be four main sources of radioactivity that must be considered in this scenario. First, all the carbon material will be mobilized as a result of the oxidation. Conservatively we assume that the impurities and activation products present in the carbon structures will be also mobilized, dragged along by the CO gas and finally released through the breach in the building wall.

Second and as a consequence of the oxidation of the graphite, the tritium trapped in these structures will be released. In the original report it was estimated that only 10 grams of tritium would be retained in the graphite reactor structure. Recent data about tritium trapping in C/C composites have shown that this number was underestimated. We have adopted the more realistic value of 1 kg of tritium for the total of FW/blanket graphite shells. This mass, together with the steady state inventory of the Li2O (162 g), the helium carrier gas (5 g), the reactor Xe gas (4.6 g) and the target feed system (1 g) results in a total of 1172.6 g of tritium that will be mobilized during the transient. We conservatively assume that the tritium is released in the more radiotoxic form of HTO.

Third, we assume that fraction of the Li2O inventory present in the chamber in the moment of the accident (1/3 of the total 2000 tonnes of Li2O) will be also mobilized as a consequence of the combustion of its structural support. Given the size of the granules (300 to 500 μm in diameter) most of them will deposit on the reactor horizontal structures, resulting in a minor release fraction.

Finally, the Xe gas that fills the reactor will also be mobilized and finally released through the break in the confinement.

It must be noted that if oxidation could be prevented, then only 172.6 g of tritium and the atmosphere of Xe gas would constitute the radioactive mobilized sources.

V.	RADIOACTIVITY RELEASES AND OFF-SITE DOSES

In order to estimate release fractions, a MELCOR model of SOMBRERO was developed. This model includes the FW/blanket assembly, the inner shielding and the confinement building. The radioactive source term described in the previous section is used as input data for the MELCOR calculations. We have considered a severe accident consisting of a LOFA, with loss of flow in all of the four cooling loops, with simultaneous LOVA produced by failure of the confinement building and consequent air ingress. This model is used by the code to simulate the progression of the accident.

MELCOR heat transfer package considers conduction, convection and radiation between the structures. The aerosol transport module treats the aerosol nucleation and agglomeration, vapor condensation, gravity settling and gaseous/liquid transport. A new module introduced by INEEL allows simulation of HTO transport and condensation.

A.	Results With Graphite Oxidation

Assuming that the graphite reactor structures suffer oxidation, we calculated the source term mobilization  and release fractions to the environment, and the final doses. We have considered three options for the chamber filling gas. In the first case we use Xe, including all its activation products. Second, we report results for the case that the iodine and cesium isotopes could be removed from the Xe gas by the chamber vacuum system. Finally, we show the results for the case where Kr is used instead. It can be noticed that the gaseous species (graphite in CO form and the chamber filling gas) result in a release fraction of 100%. Due to the size of the Li2O granules, most of them will deposit on the reactor horizontal structures, resulting in a 1 kg release from the initial 667 tonnes mobilized. Because of the partial condensation of the HTO on the colder building walls, we get a release fraction of 19% from the initial 1.173 kg mobilized. With the data about the activity released and the adequate DCF, off-site doses can be obtained. The DCF library has been updated to include radionuclides that were missing from traditional (fission) libraries as some of these radionuclides maybe important for fusion. Early doses were calculated using typical weather conditions and ground level release as recommended by the Fusion Safety Standards.

Results in Table 1 show that the dominant dose comes from the Xe gas, giving a result of 4.69 rem. The graphite from the FW/blanket structures results in a dose of 0.17 rem, and the Li2O makes a negligible contribution to the final dose. The design using Xe would lead to a final accident dose of 5.64 rem if the non-xenon activation products were included in the release. This value would be reduced to 1.19 rem assuming that the iodine and cesium isotopes can be separated by the chamber vacuum system. For a modified SOMBRERO using Kr instead of Xe, we calculate a total accident dose of 1.06 rem.

Table 1. Mobilized activities, release fractions and off-site doses, case of graphite oxidation.

| Radioactive source | Mobilized activity (Bq) | Release fraction (%) | Off-site dose (rem) |
| --- | --- | --- | --- |
| C-FW | 6.1E+14 | 100 | 0.05 |
| C_blanket | 1.4E+15 | 100 | 0.12 |
| Li2O | 5.8E+18 | 1.5E-4 | 0.00 |
| HTO | 4.2E+17 | 19 | 0.78 |
| Xe | 1.4E+16 | 100 | 4.69 |
| Xe* | 1.4E+16 | 100 | 0.24 |
| Kr | 8.8E+15 | 100 | 0.11 |
| Total w/Xe | 6.2E+18 |  | 5.64 |
| Total w/Xe* | 6.2E+18 |  | 1.19 |
| Total w/Kr | 6.2E+18 |  | 1.06 |

Xe* = Xe without iodine and cesium activation products

Given that our goal is an accident dose below the 1 rem limit given by the DOE Standards, other design modifications have been considered. Other than the activation products from the Xe gas in the chamber, the most contributing source to the final dose is the tritium. The quantity of tritium that condenses on the confinement building walls will depend on the time-temperature history of those structures. In order to keep the temperature of the building inner surface as low as possible, a high conductivity material could be useful. The SOMBRERO report used concrete with 2.8% vol. mild steel as the building material. We have studied different alternatives, and here we propose two options. First, increasing the steel content to 5% would reduce the release fraction of the tritium to 14% and the dose to 0.59 rem. This would result in a final dose of 1 rem in the case of Xe with removal of iodine and cesium isotopes, and 0.87 rem in the case of Kr used as chamber gas. Another alternative would be replacing the material with 97% concrete and 3% aluminum. This would also affect the thermal conductivity of the building and thus, the condensation of tritium on the walls. The tritium release fraction would be reduced to 11% and the off-site dose to 0.4 rem. This would result in a total accident dose of 0.81 rem in the case of Xe with the iodine and cesium isotopes being removed, and 0.68 rem if the chamber gas is Kr.

B.	Results Without Graphite Oxidation

Assuming that oxidation of graphite does not occur, the only radioactive source terms would be the 172.6 g of tritium trapped in other parts than the graphite chamber, and the reactor filling gas (Xe or Kr). The results in this case are shown in Table 2.

Table 2. Mobilized activities, release fractions and off-site doses, case without graphite oxidation.

| Radioactive source | Mobilized activity (Bq) | Release fraction (%) | Off-site dose (rem) |
| --- | --- | --- | --- |
| HTO | 6.2E+16 | 2.8 | 0.02 |
| Xe | 1.4E+16 | 100 | 4.69 |
| Xe* | 1.4E+16 | 100 | 0.24 |
| Kr | 8.8E+15 | 100 | 0.11 |
| Total w/Xe | 7.6E+16 |  | 4.71 |
| Total w/Xe* | 7.6E+16 |  | 0.26 |
| Total w/Kr | 7.0E+16 |  | 0.13 |

Xe* = Xe without iodine and cesium activation products

In this case the tritium dose is only 0.02 rem, but the Xe would still produce an off-site dose over 4 rem if the iodine and cesium activation products were included in the release. If these isotopes were removed by the chamber vacuum system, the final dose would be 0.26 rem. For the modified design using Kr, we get an accident dose of 0.13 rem. In these last two cases with final dose ( 1 rem, an evacuation plan would not be needed.

VI.	CONCLUSIONS AND FUTURE WORK

In the present work, accident doses have been analyzed for the SOMBRERO IFE design. A severe accident consisting on a total LOFA with simultaneous LOVA because of failure of the confinement building and subsequent air ingress event has been simulated using fusion safety codes.

During the accident, graphite structures will suffer oxidation with air, resulting in mobilization of the carbon, including the tritium trapped in it, and the Li2O granules from the blanket. The oxidation of graphite with air is a major issue that should be prevented by introducing passive safety features, protective coatings, or alternate FW and/or blanket materials.

Assuming that oxidation takes place, the calculated off-site dose results in 5.64 rem. Removing the iodine and cesium activation products from the Xe gas would result in a dose of 1.19 rem. If Kr is used as alternate gas for the reactor atmosphere this value would be reduced to 1.06 rem. If we assume that the iodine and cesium can be removed from the Xe gas, or that Kr is used instead, doses below 1 rem could be achieved with simple design modifications such as increasing the steel content in the confinement building (to 5% vol.) or adding aluminum (3% vol.) to the concrete. The higher thermal conductivity of the material would allow a less severe temperature excursion of the building walls and more tritium could condense on the confinement inner surface. If oxidation could be prevented, then the off-site dose would be 4.71 rem if the non-xenon activation products were included in the release, and 0.26 rem if the iodine and cesium isotopes were removed by the chamber vacuum system. In the case were Kr is used instead of Xe, the final dose results to be 0.13 rem.

The cases with total dose below 1 rem would meet the requirement given by the DOE Fusion Safety Standards in order to avoid public sheltering and evacuation.

Additional work is needed in the areas of C/C composites oxidation and tritium trapping and retention. Also the use of steam in the He carrier gas may reduce the tritium inventory but still needs to be evaluated. We plan to identify and simulate other more credible, less conservative accident scenarios in order to make a complete safety analysis for the SOMBRERO IFE power plant design.

## ACKNOWLEDGEMENTS

The authors would like to thank their colleagues at the INEEL and U. Wisconsin-Madison for their assistance and recommendations that have been essential to the completion of the above work.

Work performed under the auspices of the U. S. Dept. of Energy by University of California Lawrence Livermore National Laboratory under Contract W-7405-Eng-48 and under support Ministerio de Educación y Cultura, Spain, under Plan Nacional I+D+I (2000-2003) Programa Nacional de Fusion Termonuclear, and the European Union keep-in-touch Program on IFE.

## REFERENCES

[1]	W. R. Meier et al., "Osiris and SOMBRERO Inertial Confinement Fusion Power Plant Designs," W. J. Schafer Associates, Inc., DOE/ER/54100-1, WJSA-92-01 (1992).

[2]	"Safety of Magnetic Fusion Facilities: Guidance," DOE-STD-6003-96, U. S. Department of Energy, Washington, D. C. (1996).

[3]	"Manual of Protective Action Guides and Protective Action for Nuclear Incidents," PB92-164763, U. S. Environmental Protection Agency, Washington, D. C. (1991).

[4]	L. J. Wittenberg, "A Reinvestigation of the Tritium Inventory in the Carbon Struture of the SOMBRERO Direct-Drive ICF Conceptual Design Study," (2000).

[5]	D. E. Cullen, "TART98: A Coupled Neutron Photon, 3-D, Combinatorial Geometry, Time Dependent, Monte Carlo Transport Code," LLNL, UCRL-ID-126455, Rev. 2 (1998).

[6]	J. Sanz, "ACAB98: Activation code for fusion applications. User's Manual V4.0," Universidad Nacional de Educacion a Distancia (UNED), LLNL, UCRL-CR-133040 (1999).

[7]	M. J. Gaeta and B. J. Merrill, "CHEMCON User's Manual Version 3.1," Idaho National Engineering and Environmental Laboratory, INEL-95/0147 (1995).

[8]	R. O. Gauntt, R. K. Cole, S. A. Hodge, S. B. Rodriguez, R. L. Sanders, R. C. Smith, D. S. Stuart, R. M. Summers and M. F. Young, "MELCOR Computer Code Manuals," NUREG/CR-6119, Vol. 1, Rev. 1, SAND97-2398 (1997).

[9]	D. Chanin and M. L. Young, "Code Manual for MACCS2, User's Guide," NUREG/CR-6613, Vol. 1, SAND97-0594 (1998).

[10]	S. Goujard and L. Vandenbulcke, "Oxidation Tests of Carbonaceous Composite Materials Protected by Si-B-C CVD Coatings," Thin Solid Films. 245, 86-97 (1994).