# Introduction

This statement of work describes the activities required to install an antenna tower at the Liberty Research Center (LRC), a U.S. government facility located at 7301 Ridge Road, Marriottsville, MD 21104-1130, in Carroll County.  The purpose of the tower is to house a 24 ft radome, antenna system and shelter.  The tower will be high enough to allow the antenna to operate above the tree lines to eliminate any obscurations caused by current trees residing on County property.  According to County regulations, we are unable to top the trees.  The Contractor shall provide the design, labor and materials for the installation of an antenna tower at the LRC.  The erected tower shall be designed in coordination with the Army Corp of Engineers.  The contractor shall gain permission to enter and work at the LRC in accordance with their regulations.

A subsurface soil exploration was performed at the location where the antenna tower is to be installed on 22 February 2006.  The Geotechnical Report dated on 7 March 2006 is provided herein.  This test report is based on borings drilled on 22 February 2006.

A Site Survey will be conducted prior to submission of bids.

# Technical Tasks

The Contractor shall provide all necessary Architect-Engineer services by qualified Architect-Engineers licensed in the State of Maryland as required to design and prepare complete construction documents, i.e., specifications (as required), detailed construction drawings, budgetary construction cost estimates, and as-built final construction documents.  The Contractor shall design and erect an antenna tower that will house a government provided radome and shelter with the following specifications (a concept drawing is provided) in accordance with the Building Officials and Code Administrators International Code (BOCA), the International Conference of Building Officials (ICBO) Code, Carroll County Code and Building Regulations and the Army Corps of Engineers Safety Manual: EM 385-1-1.  Where regulations or guidance conflicts, the MOST STRINGENT REQUIREMENT WILL PREVAIL.

.

- The Contractor shall erect a 36 ft high antenna tower on a foundation designed in accordance with construction best practices based on the subsurface soil exploration test report and loads indicated below.

- The antenna tower shall have three levels, with the top level holding the radome.

- The contractor shall provide a concrete slab at ground level.  The concrete slab shall cover the ground under the tower and surround each support leg and be able to accommodate the weight of two 4 ton pickup trucks.

- All concrete shall be field tested to determine slump and compressive strength.  The contractor shall take concrete samples during concrete placement.

  - Slump tests shall be performed in accordance with ASTM C143-90, Standard Test Method for Slump of Hydraulic Cement Concrete.  The maximum slump shall be 5 inches, but may be increased with the addition of an approved admixture provided that the design water-cement ratio is not exceeded.  Perform tests at commencement of concrete placement, when test cylinders are made and for each batch (minimum) or every 20 cubic yards (maximum) of concrete.  Concrete not meeting the maximum slump requirements will be rejected by the Technical POC.

  - Compressive strength testing shall be in accordance with ASTM C39, Standard Test Method for Compressive Strength of Cylindrical Concrete Specimens.  The contractor shall take five test cylinders for each set of compressive strength tests.  Precautions shall be taken to prevent excessive evaporation and loss of water from the specimen.  Two cylinders for each test set shall be tested at 7 days, two cylinders at 28 days and one cylinder held in reserve.  Samples for strength tests shall be taken for each truck.  Each strength test result shall be the average of the two cylinders from the same concrete sample tested at 28 days.  The contractor shall provide the Technical POC with the test results within 1 day of receiving them.  Concrete not meeting the design specified compressive strength criteria shall be removed and replaced with new acceptable concrete.

- The Contractor shall provide the tower with three levels.  The first level shall be 12 ft above the concrete slab.  This is identified as Level 1 on the concept drawing.  Level 2, as identified on the drawing, shall be 24 ft above the concrete slab and shall support the electronic equipment shelter.  Level 3, as shown on the drawing, shall be the top of the tower, 36 ft above the concrete slab and shall support the radome.  Safety railings and access stairs shall be in accordance with Occupational Safety & Health Administration (OSHA) regulations.

- The tower structural beams shall be constructed of hot-dipped galvanized steel.  All levels of the tower shall be a minimum of 24 ft x 24 ft.

- The Contractor shall provide a tower capable of housing a 24 ft diameter radome, antenna system and a 24 thousand pound (24,000 lb) electronic shelter.  The shelter exterior dimensions are 20 ft x 8 ft x 8 ft.  The shelter shall be placed on Level 2 directly beneath the radome.  The maximum weights of the individual units are: Shelter - 24,000 pounds, Antenna System – 3,000 pounds; Radome – 2,500 pounds; HVAC system -1,500 pounds for a total equipment weight of 31,000 pounds.  The HVAC system will be placed on Level 1.  The Contractor shall design the structure to hold up to 10 personnel performing maintenance and another 4,000 pounds of maintenance equipment.  The shelter, antenna, radome and HVAC are provided by the government.  The Contractor shall place the antenna on Level 3 and the shelter on Level 2 of the tower.  The government will fasten both the antenna and shelter after it is determined that both can be fastened to the tower as required.  The government will be responsible for the placement of the HVAC equipment and the radome.

- The Contractor shall provide Levels 1, 2 & 3 walking surfaces as follows:

- Level 1: Surface should be an open grate suitable for walking which allows water to pass without puddling.

- Level 2: Surface should be an open grate suitable for walking which allows water to pass without puddling.  Level 2 shall accommodate access to cable entry ports in the shelter labeled P1 and P2 in the drawing labeled "APS Floor Entry Panels".  Panels P1 and P2 are on the bottom of the shelter for signal interface cables from an existing building.  Power entry panel labeled P4 in the drawing labeled "Exterior End Views" and antenna interface port P6 on top of the shelter in drawing labeled "APS 100-002 Exterior Top View of the shelter" must also have unlimited access.

- Level 3: Surface shall be weather tight to allow for heating/air conditioning of the radome and suitable for walking.

- A ladder or steps shall be installed on the area behind the shelter to give access from the floor of Level 2 to the floor of Level 3 into the radome.  The contractor shall provide a lockable hatch at Level 3 to block access to the radome.

- The tower wind loading requirement, with the radome considered, is for 150 mph gusts.  The ice loading requirement is as required for local conditions.

- The tower shall be installed within an existing fenced compound.  The contractor shall provide approximately four feet (4 ft) wide strip of gravel, 4 in deep, between the concrete slab and the existing fence on two sides of the concrete slab.  The contractor shall provide for weed control under the gravel.

- The Contractor shall provide a lighting ground ring around the tower approximately three (3) feet out from the base.  This ground ring shall consist of # 4/0 AWG bare copper wire with ground rods installed at each base corner, below grade.  Each leg of the tower shall be grounded to this ground ring by use of Cadweld/Exothermic weld.  The contractor shall install the lighting ground so that the tower ground shall be separate from existing site grounding systems

- The Contractor shall install two (2) PVC conduit runs of two (2) inch minimal size below grade from the tower base to the exterior of the existing building to allow for government installation of electrical power.  The approximate length is 90 ft.

- The Contractor shall install one (1) PVC conduit run of three (3) inch minimal size below grade from the tower base to the existing exterior of building to allow for government installation of signal cables.  The approximate length is 90 ft.

- The Contractor shall return the site grounds to the condition as found prior to the stated work.

The regulations and building codes cited previously need to be addressed and met as required.   The contractor is fully responsible for designing the tower to meet those regulations and building codes.  NRL will have the Liberty Research Center's Army Corp of Engineers POC, at the site for the site visit and he will be available during the design and construction process to answer your questions as will be the NRL Technical POC and site representative.

3.	Drawings

The contractor shall submit design drawings of the tower, foundation base and levels for government approval prior to installation.  These design drawings shall be submitted in the format required by Carroll County Code in order to obtain building permits and shall be stamped with professional seals.  The contractor shall provide all design calculations e.g. loads, stresses, etc.

The contractor shall provide two sets of As-Built Drawings within two business days after construction is completed.

4.	Construction Permits

The contractor shall be responsible for:

- obtaining proper zoning or other land use control approval for the project

- paying any fees due for the foregoing, and

- obtaining and paying for any building permits.

The Army Corps of Engineers will issue a permit to NRL to permit the construction of the tower at Liberty Research Center, which is leased by the Corps from the City of Baltimore.

5.  Project Manager and Points of Contact

Project Manager for this contract is Mrs. Windie Borodin, Director of the Midway Research Center; phone 703-551-1992

Technical POC at the site is Todd Miller, 202-279-7202, cell 202-437-2970.

Site POC is Elza Redman, 410-781-0487, cell 410-207-7233.

Army Corps of Engineers POC is Clayton Redmond, 443-479-5671.

6.  Schedule

All design work, drawings and design calculations shall be completed and provided for government approval under CLIN #0001 within 45 days after contract award.

After all governmental approvals have been completed the government will authorize construction under CLIN #0002.  All construction shall be completed within 90 days after exercise of CLIN #0002.

7.  Proposal

The contractor shall include the following with the proposal:

- a schedule,

- preliminary design drawings, and

- preliminary design calculations.