Follow-Up Review

of

NuMI Infrastructure Review

of

July 12 and 20, 2001

Water Inflow – HVAC – Fire P&D – Electrical Plan – Enclosure Access – Radiation Safety – Cooling Water Systems – Vacuum – Gas Systems – Cable Tray – Communications Ducts – Controls – FIRUS – CATV - Telephones

A Brief Summary of Comments with Responses

by

Bob Ducar and Dave Pushka

March 6, 2002

# Water Inflow

- Remember to put drip shields over Decay Pipe vacuum equipment in the Outfitting subcontract.  (Hylen)

The vacuum pump skid, Decay Pipe cooling skid, and the Absorber RAW skid will be built with roofs to protect equipment from dripping water.

- Be aware of potential need for drip ceilings in the Absorber area to protect equipment.  (Childress)

This is similar to the previous comment from Jim Hylen.  We are aware of this potential need and protective measures will be taken as necessary.  The conditions in this area of the enclosure will be assessed during the SB&O subcontract execution.

- Questioned if NuMI tunneling activity is contributing to a drop in the natural level of groundwater at Fermilab or having an effect on retention ponds.  (Rucinski)

While it is true that the tunneling does de-water the rock in the vicinity of the tunnel, the net impact on the natural level of groundwater at the Fermilab site or any retention system is minimal or non existent.  Net inflow to the NuMI enclosure is presently estimated at 300 gpm.  This inflow will be pumped out of the enclosure at the MINOS shaft.  Ponds are located adjacent to the MINOS service building to capture the outflow.  FESS has initiated a study to investigate routed excess outflow to the Main Injector pond system.

- Is there a concern for a bad type of mold growing in the tunnels that could cause health problems?  (Rucinski)  A somewhat related comment concerned micro-organisms in the water inflow fouling drainage paths.  (Plant)

Given the experience of Main Injector, this is an issue of concern as related to both health problems and slip hazards.  This issue has been determined to be an Action Item and has been referred to the Project Safety Coordinator for investigation and resolution.  It should be addressed by a qualified industrial hygienist.  In addition to molds, the potential of micro-organisms also should be investigated.  Micro-organisms in the Main Injector LCW piping system water led to significant damage of metals.

- During construction activities, can sump pump failure cause flooding and drowning of workers?  (Rucinski)

Sump pump failures, either by the pumps themselves or by loss of electrical power, have caused flooding during the current Tunnels and Halls construction phase.  However, these instances have never led to a credible danger of drowning due to moderate levels of inflow.  The specific characteristics of the final sump pump system, that will be located at the MINOS access shaft, are still being designed by FESS Engineering.  This final system will be installed under the SB&O subcontract.  Review of the final design of the MINOS sump pump system has been identified as an Action Item and will be coordinated by the Project Engineers.  A failure analysis of the system will be performed and/or reviewed at this future review.  The analysis will also consider time necessary to recover from various postulated failures.  The goal is to achieve a design with sufficient redundancy and alarms such that the level of the water never rises above the top of the sump pit or achieves any level sufficient to damage area equipment.  Given the area at the most downstream end of the enclosure and the rate of inflow, drowning is not a credible hazard.

- At MINOS, consider a third high level pump.  (Dan Johnson)  Similar concern raised with a call for completely redundant system.  (Plant)

The necessity of a third sump pump at MINOS has been accepted and is being designed into the system.  Rather than being a high level pump, this third pump is thought to run near continuously at a flow rate slightly less than expected inflow.  This concept will significantly reduce the cycling rate of the other two pumps with an expected increase of longevity of the pumps and their associated electrical contactors.  Also see above comment and response.

- Doesn’t think it is very well known how much water will be in the tunnels.  This could effect the design of the enclosure and air system.  (Capista)

It is agreed that there is some uncertainty in the expected water inflow.  Execution of the Tunnels and Halls subcontract includes grouting in selected areas on a case by case basis to control inflow.  This work is in process.  The basic designs of the enclosure and air system are essentially fixed at this time and not subject to change.  As the reality of the enclosure becomes more clear, the sufficiency of the design will be evaluated as to its adequacy.  If the existing designs are thought to be inadequate, changes will be made as necessary.

- Worried about drainage system plugging up with mud and silt over time.  (Capista)  Construction waste also noted as a potential problem for fouling pathways.  (Plant)

It is agreed that this is a serious concern.  Clauses in both the Tunnels and Halls and SB&O subcontracts address the issue of keeping these paths clean.  Civil construction oversight is well aware of the potential problem.  The installation of technical and scientific components present yet another opportunity for fouling of drainage paths.  Necessary actions to keep these paths clear will be specifically included in the execution of installation activities.

- Suggested intermediate pumps pumping into a header.  (Capista)

The present plan calls for all inflow to be pumped out at the MINOS shaft.  Earlier plans had a sump at Target with discharge at that shaft, but this was eliminated as a cost saving measure.  The prospect of distributed sumps would require additional excavation under the Tunnels and Halls subcontract with attendant high cost and schedule delay – clearly not an attractive option at this point in time.  While having a single pump station at the MINOS shaft can be viewed as putting all one’s eggs in one basket, there are advantages to this approach.  It recognizes that most of the water inflow is downstream of the Target shaft.  The 2,200 foot long Decay Pipe passageway is basically a no mans land.  Location of any equipment in this passageway is highly discouraged for a variety of reasons.  With the sump at MINOS shaft, maintenance and reliability issues are focused on this single location.  Since the review of last year, there has been much progress on the sump design with special attention to reliability and redundancy.

- Consider a second pumping station at Target Hall.  Initial investment will be worth it in costs later.  (Capista and Plant)

As previously stated, most of the water inflow is downstream of the Target shaft and placement of a sump at Target was eliminated as a cost saving measure.  It is currently the consensus of the engineers in FESS and the Project that a single pumping station, with adequate redundancy for electrical power and pumps, will result in a system with very high reliability.  Additionally, the current design utilizes tandem (two-stage) pumps with an attendant increase in efficiency.

- Discharge at MINOS is one acre-foot per 40 hours.  Does the Lab have a place or permit to dump that much water?  (Plant)

- Discharge water at MINOS is first pumped into a series of ponds adjacent to the MINOS service building.  The present plan is for excess water to discharge into the Indian Creek waterway.  Outflow will be tested for compliance.  It is anticipated that this discharge will meet IEPA requirements.  The new outflow will be included in the Laboratory’s existing permit with the State of Illinois.  As previously mentioned, FESS has initiated a study to investigate routed excess outflow to the Main Injector pond system.

# HVAC

- Recommendations for fans in the pump room.  (Plant)

Ventilation fans already exist in MI-62.  As plans are developed for the new CMU wall enclosing the NuMI LCW pump system, we will make sure that appropriate ventilation is provided for.

- Target Hall needs a humidity spec to save the crane.  (Hylen)

A specification does exist for the humidity in the underground spaces.  Equipment that is conservatively sized with respect to the anticipated loads is included in the scope of the SB&O subcontract.  Should the actual loads exceed the expected, local heaters or dehumidifiers will be added as determined to be necessary.  Developed crane specifications are thought to anticipate its installation in a less than ideal atmosphere.

- Would it be prudent to have some permanently mounted air sampling monitors?  (Rucinski)

Sharing your concern, Jack Steinhoff, the Fermilab Fire Chief, has requested a topside readout of enclosure levels of O2/LEL/H2S/CO similar to those produced by a TMX air sampling monitor.  This issue has been determined to be an Action Item and has been referred to the Project Safety Coordinator for investigation and resolution.  The Beams ES&H Department has identified a sampling unit with remote readout that will likely be suitable.  Planned fire detection equipment includes smoke detectors (in non-radiation areas) and VESDA type air sampling systems.  Underground areas are to be well ventilated.  Natural potentials for ODH, CO, H2S, and methane are very low to non-existent.  The Safety Coordinator should review the situation and develop recommendations.  DOE and Gage-Babcock may already have addressed these issues.

- Strong concerns about humidity conditions in tunnel leading to vacuum, magnet and power supply failures.  Reliability of the experiment will suffer.  (Capista)

A specification does exist for the humidity in the underground spaces that should result in a satisfactory environment for the installed equipment.  HVAC equipment, conservatively sized with respect to the anticipated loads, is included in the scope of the SB&O subcontract. The service building dehumidifiers are outfitted with chillers in their final stages.  It is planned to throttle back these chillers during the installation phase so as to introduce more heated air into the enclosure.  If this strategy is insufficient, local heaters and/or dehumidifiers will be added as necessary.  Humidity sensitive technical equipment, especially beamline magnets, will not be brought into the enclosure until ambient conditions are suitable.  In the overall, this is a significant issue of concern for the Project.

- Control condensation in the Carrier Tunnel to protect equipment.  Use the Carrier Tunnel itself as an air duct.  (Childress)

This idea has been considered and rejected even though there would have been enhanced protection of equipment and mitigation of a confined space hazard.  However, with the new prospect of locating some quadrupole magnets in the Carrier Tunnel, the issue has new life.  Specifically, there is presently a proposal to draw ~1,000 cfm of warm and relatively dry air from the Main Injector through the Carrier Tunnel.  This air would exhaust into the Pre-Target enclosure and be quickly evacuated by the exhaust fan at vent shaft EAV-1.  The rate of exhaust would be approximately doubled by increasing the capacity of the exhaust fan.

- Do we have back up for tunnel heating when the air circulation system is down?  (Childress)

There is no installed back-up for the air circulation system.  The thermal constant for the underground enclosure indicates that heating would not be needed in the event of a modest downtime of the air handling equipment.  Temporary installation of 480 VAC fan heaters is a relatively easy fix that could be employed to keep things warm if the downtime is extensive.

- With no humidity control in (the Decay Pipe) bypass tunnel, it could be very rough for equipment if installed.  (Plant)

- Agreed that this is a potential problem.  However, no equipment is to be installed in the Decay Pipe passageway other than a mid-point fire door and a few electrical conduits.  See related response for Carrier Tunnel.

- Questions the validity of the 2% wall wetting number.  If larger, the humidity removal system may not keep up.  (Plant)

- It is agreed that the 2% wall wetting figure is probably optimistic.  It is considered essential to keep ambient temperatures above the dew point.  Approaches to this problem are detailed in above responses.

# Fire Protection and Detection

- Questioned lack of pumps for the fire protection system.  (Rucinski)

Fire protection water comes from Casey’s pond, consistent with all of the other buildings in the vicinity of the NuMI buildings.  There is no requirement for local pumps.

- Will radiation interfere with the smoke detectors?  (Rucinski)

Radiation will indeed interfere with standard ionizing type detectors.  No smoke detectors of this type are planned for installation in radiation areas.  As an alternative, air sampling type systems (VESDA) are planned for selected areas.

# Electrical Plan

- Need more detailed planning of cables down shafts.  (Childress)

Spreadsheets listing technical and infrastructure cables have been prepared.  These listings have now been included in the Service Building and Outfitting drawings for installation during the related subcontract.  Generally, cables at Target will be in cable tray and cables at MINOS will be in conduit.  Intermediate tie points will be provided at the MINOS shaft.

- What precautions are taken to prevent shock hazards to personnel in the wet tunnel environment?  (Rucinski)

120 VAC GFCI duplex outlets are to be installed throughout the underground enclosure.  Other necessary precautions will be addressed in job specific hazard analyses as necessary and appropriate.

- Concern about being in total darkness in the event of a power outage before the emergency generator kicks in.  (Dan Johnson)

Conventional power for emergency lighting is backed-up by emergency generators at Target and MINOS.  Switchover to generator power is expected to be less than 15 seconds after the loss of conventional power.  Battery back-ups for emergency lighting are currently not entertained in the design.  This is to avoid performance of required monthly testing, as well as to avoid the generation of mixed waste for batteries in radiation areas.  (Note, however, that the emergency generators will be tested monthly.)  It is expected that the procedure for access to the underground enclosures may demand that each person carry a small flashlight.  Additionally, training associated with access will inform trainees of the potential for brief times of total darkness in the event of a power failure.

- Concern for installed equipment in the wet environment of the enclosures.  Should consider minimal incandescent lighting.  (Plant)

- Agreed that a potentially wet environment will cause difficulties.  The degree of wetness is speculative at this point in time.  Certain elements of the electrical system have been specified to hold up to the anticipated environment.  Fluorescent light fixtures specified have plastic cases with sealed lenses.  Longevity of fluorescent tubes is greater than that for incandescent bulbs operating at nominal voltage.  Additionally, the fluorescent tubes are more efficient in producing minimum required illumination.

# Enclosure Access

- Concerning access requirements, we need defined parameters to make decisions. (Dan Johnson)

This issue has been determined to be an Action Item and has been referred to the Project Safety Coordinator for investigation and resolution.  A proposal for a Check-In Check-Out (CICO) procedure has been developed with the input of safety individuals from BD, PPD and BD Operations Department but has not yet received full buy-in by the affected Divisions or the NuMI project management.  The concept has also been discussed with the Fermilab Fire Chief.  Details of access and emergency procedures and training need to be developed under the oversight of the Project Safety Coordinator and NuMI Project management.

- Should cameras be used to inspect some of the more remote areas like the Carrier Tunnel passageway?  (Plant)

- With anticipated improvements in lighting, ventilation and access, personnel access to the whole of the Carrier Tunnel will be facilitated.  The Decay Pipe passageway remains as the singular most remote area of the enclosure.  Cameras might be considered for use there.  However, it is not at all clear if cameras could replace search and secure activities.

- Gage-Babcock recommendations for occupancy limits should be followed at the onset of installation activities. (P. Martin)

It is agreed that this will be the plan.  These limits apply at the MINOS underground area that include the Absorber, muon alcoves and the near detector hall.  Occupancy will be limited to twenty-four.

- The integrated installation schedule should be completed with estimates of manpower for each task so that the access issues can be understood.  (P. Martin)

- Development of an integrated installation schedule is on the docket for the May 2002 DOE review.  Installation of the near detector dominates activity at MINOS.  Installation of the Absorber is the next most important activity.  Both require intensive use of the access shaft.  Other activities in this area are incidental in comparison.  Organizers of all these activities are aware of the access limitations at MINOS.  While there are no specific access limits at Target, there is some contention for the use of the Target access shaft.  Work activity here is dominated by Target Hall installation activities.  The other significant use of the access shaft will involve lowering of the beamline magnets.  These are finite in number, however, so we do not anticipate any serious contentions here.

- Method of recording entry and exit from the underground enclosure needs to be in place at beginning of installation activities and agreed upon by DOE, ES&H Section and the NuMI Project.  (P. Martin)

- It is agreed that recording of entry and exit (CICO) be in place at the onset of installation activities.  Reference above action item under Dan Johnson’s comment.

Radiation Safety

- The 2nd permanent stack monitor may be better placed at the Absorber vent rather than the primary beam carrier pipe vent.  (Hylen)

Nancy Grossman, in consultation with the ES&H Section, has looked at this and determined that the existing stack monitor location is sufficient.  A second monitor is not needed.  During initial operation, portable emission monitors will be used to measure the emissions and additional permanent monitors will be added if found to be necessary.

- Projections for tritium levels in horn RAW systems exceed Lab guidelines.  Need plans for dealing with this for input to a formalized review.  Important to preclude major surprises as we approach operation.  (Childress)

Kamran Vaziri of the ES&H Section has calculated the activation of the horn RAW system.  Strategies for dealing with this have been developed in conjunction with Don Cossairt.  This issue was discussed at a RAW review subsequent to this Infrastructure review.

- Some power supplies are cooled by the RAW system.  Would the room these supplies are in need to be interlocked?  (Plant)

- No power supplies are cooled with RAW.  RAW skids are located in one of the target support rooms and in the Absorber passageway near the Absorber enclosure.  It is anticipated that access to these areas will be subject to special access requirements as determined by Beams ES&H.

# Cooling Water Systems

- Provide access for cleaning of the shell and tube heat exchanger at MI-62.  (Rucinski)

The south end of the heat exchanger is positioned by an existing roll-up door.  Cleaning is thereby easily facilitated.  Additionally, the pond water strainer selected will afford easy manual flushing of the strainer to the rear of the service building without any additional fouling of the pond system.

- Stated desire to interlock pond pump to LCW/RAW systems.  Also asked for an “easy bypass” for maintenance and special running needs.  (Plant)

The primary interface here will be between the pond pumps in PV-9 with the NuMI beamline LCW system that will be located in MI-62 service building.  Controls will include local manual control for maintenance and provisions, as necessary, for special running needs.

- Stated impact of high pressure LCW on power supplies.  Strongly urged not to add pumps to solve the problem.  (Plant)

Dan Darimont of the EE Support Department was consulted to determine how the proposed LCW pressure on the horn charging power supplies compares with other installations.  The maximum pressure listed for the PEI power supplies is 250 psig.  The supplies need a minimum 60 psig differential to achieve sufficient water flow to cool the components.  We intend to run the LCW system here at 200 psig inlet and 80 psi differential.  These operating conditions are not outside of the listed conditions and are consistent with other installations in service at the Laboratory.  Therefore, the existing design is adequate.  Adding booster pumps is not necessary.

- Suggested a more complete review of the entire water system.  (Plant)

The hydraulic calculations have been calculated independently, by both Dave Pushka and Scott Reeves, and are in agreement.  Once the proposed beam optics changes are settled, the calculation will be repeated and documented in an engineering note.  (The new optics design is presently thought to present a rather modest increase in net flow requirements.)  All of the LCW and RAW systems have been documented with schematic diagrams and engineering calculations where the loads are known.  Instrumentation lists have been prepared for all water systems.  Additional review of these systems is not thought necessary given established lines of communication between the Project and the Water Group of the Beams Mechanical Support Department.  If significant issues arise, you will be informed.

Vacuum

- NuMI vacuum should be compatible with that of the Main Injector.  (Childress)

There is no doubt that the systems should be compatible.  It is planned to install sufficient pumps in the NuMI extraction line to allow it to reach a pressure compatible with that of the Main Injector.  Additionally, good vacuum is needed for proper operation of certain beamline instrumentation devices.

- To save money, the stand-by Decay Pipe vacuum pump could be smaller in size.  (Childress)

All options to reduce cost of the Decay Pipe vacuum pumps will be considered.  While there may be some advantage to reducing the size of the 2nd pump, other accommodations for the differences are likely to more than balance the savings in capital costs.

- General concerns about vacuum conditions by the Lambertsons.  Suggests Terry Anderson talk to Mishra.  (P. Martin)

Discussions have occurred and concerns are generally abated.

- Unclear as to isolation of NuMI and MI vacuum.  (Plant)

This issue has been addressed by Terry Anderson.  Automatic vacuum isolation valves have been (or will be) placed appropriately in the beamline.

# Gas Systems

No significant comments.

# Cable Tray

No significant comments.

# Communication Ducts

No significant comments.

# Controls

No significant comments.

# FIRUS

No significant comments.

# CATV

- Increase number of CATV lines going down shafts.  (Childress)

Not much interest has been shown for increased CATV connectivity between upstairs and downstairs.  If there are significant numbers of enclosure camera images that are required upstairs, the video signals would be modulated onto a single CATV cable.  The greatest use of cameras is thought to be that for hot horn handling.  These circuits will be local and underground, not needing a connection to the service building.

# Telephones

No significant comments.