BEAMLINE STABILITY WORKSHOP

NSLS-II, Aril 18-20, 2007

CONVENTIONAL FACILITIES

WORKING GROUP REPORT

John Sidarous

Presentations

For the presentations materials and other details, please refer to the BSW web site

Presentation 1:

NSLS2 Ground Motion and Vibration Studies; by Nick Simos

Nick has been developing a comprehensive 3-D FE model that incorporates the SR enclosure box, SOG, with the capability of introducing vibration sources at various locations.  The model also addresses spatial wave propagation.  Nick visited APS (along with HDR) and Spring8 to take measurement in similar operating facilities, understand the expected performance, and collect data on forcing function from large noisy equipments and vibration generated within the SR-EH buildings themselves. This modeling went further than what has been done in the past in US light sources and Nano centers.  NSLS2 and Nick are to be commended for this exceptional effort.

- Ambient vibrations were measured, verified the suitability of NSLS2 site (20nm)

- The model indicated the building attenuation of Ambient Vibrations will reduce it to approx. 12nm

- Conservative vibration input was applied to the model at several alternate locations of Service Building and AHU.  The model indicates that at 30’ distance (between AHU and SR) the SR floor vibration due to the SB generated vibration will decay to less than 1 nm.

- During the discussions Nick stated that the effect of reducing SR slab thickness from 39” to 27”.  It shows insignificant effect on floor vibration (<1nm), and shows even better performance above 40Hz.

- The measurements illustrated the effectiveness of floor isolation joints.

- A computer animation of noise traveling through the slabs indicates the presence of very quiet regions on the Exp. Hall floor between Service buildings.

- Nick’s presentation includes “Path forward” which summarizes plans for additional measurements, modeling and assessments.

Presentation 2:

Data from APS Survey, March 20007; by Hal Amick of Colin Gordon

In addition to the measurements Hal and Nick took, Hal performed Hammer test in order to assess transmissibility with distance and across joints.  The points included were on top of SR, thick SOG near SR, EH floor, below Mech. Mezzanine.

- The data shows that APS performs well below VC-A and NIST-A in both the vertical and tangential directions. The slab performs even much better in the Tangential (Axial to Beam)

- Several peaks detected at different frequencies.  The report attributes them to local sources on the floor, or inside SR, rather than building machinery.

- The approach adopted by APS (implementing acoustic features in construction and administrative controls) results in NC-64 noise with 4dba range.

Presentation 3:

Conventional Facilities Temperature Stability, by Chris Channing

Some aspects of this presentation are addressed by members of the “Temperature Stability Working Group”

- The NSLS2 team drew on the recent experience in CFN thus adopting the latest technology, especially the controls.

- The SR air system is independent from the rest of the space.  SR will be positively pressurized thus virtually eliminating the air infiltration problem experienced by APS.

- Chris assured the audience that NSLS2 selection of system design, hardware and controls, achieving and even exceeding the target Temp. Tolerance of +/- 0.1 Deg. is practical.

- A discussion took place to clarify the Temp. Variation cycle.  Accelerator group stated that the +/- 0.1 Deg per hour does not neccissate having repeated cycles every hour.  The intent is that that tolerance range should nit be exceeded in any 1 hour or shorter periods.  - The important thing is to hold the temperature at any location to within that tolerance and that the drift of local average temperature should be investigated.

- Chris stated that the controls sensor drift should not exceed +/- 0.02 Deg in 2 weeks, which was judged as acceptable.  The spatial variation, i.e. from one spot to another, is not important as long there are no significant thermal gradient across any magnet.

- At  steady state operation, after orbit has been established the loads should not vary, except by a few Watts at corrector magnets.

- The anticipated air changes per hour are 10.  Accelerator representatives indicated a desire for lower number of air changes to minimize disturbances.  Chris indicated that when the tunnel is closed (operational) this will be quite possible.

- NSLS2 intends to have no outside air makeup during operations (make up from tempered air in EH).  This will enhance temp. Stability.

Resources and Time Frame

With an experienced A/E on board, and Nick Simos as an in-house vibration expert, this  is not a strong concern at the moment.   It is assumed that the scope of work of the A/E will include the engineering  effort required to incorporate the adopted recommendations.

Recommendations:

- The effort and approach taken by NSLS2 is commendable.

- Follow-up on the “Path Forward” outlined in the various presentations made throughout the workshop.

- More validation of the assumptions of FE model, especially those related to soil.  This should be done on site using NSLS1 and measurements at several points to get a good hold on actual decay, use similar FEM to reproduce the measured results and validate or revise the soil assumptions.

- I would like to have more analysis (either numerical or measurements to separate effect of large vibration sources (AHU and chillers) to truly understand the building/slab/soil attenuation of such sources.  In APS, vibration from Arhus were source of complaints by EH users.

- With newly validated assumptions, run the same FEM to perform more parametric for slab thickness, location of Service buildings, and other excitations.

- At later design stage, consider adding the structural framing, actual out-of-balance excitations from AHU and pumps.

- Revisit the project design parameters regarding the infield service buildings.  From vibration prospective, it may be better to locate them in the outfield (maybe incorporated into LOBs)   A discussion took place, and CFG will pursue that approach from cost/benefit approach.  In either case, even with the analysis resulting in acceptable outcome, an attempt should be made to locate rotating equipments as far away from SR as practically feasible.

- A concern was expressed about the effect of the condition in the infield, especially building column and footing deformation, effect of berm, and daily/seasonal temperature variation, and vibration transmission across that boundary.  That particular Arch/ Structural detail should be devedeloped and vetted very early in the process

- The infield boundary should be analyzed by an adequate computer modeling (heat transfer, deformation, and vibration).  This should not be a difficult task and is likely to put to rest the concerns expressed.

- I asked about provision for space for user equipments and storage for all. This needs to be addressed early on.  That space could also be utilized as a buffer between various equipments and SR.

- Acoustic environment should be on the forefront early in the engineering design.  At APS, we allowed the users to install control rooms on the floor to provide quiet (NC45) for

- NSLS2 is to be forward leaning as far as the administrative policy of what users could do or not do?  Could they bring rotating equipments on the floor?  How about noise and vibration generated by users?  Source of utilities provided to users?.

- Caution; a lot of vibration sources will be added with the accelerator hardware, especially equipment and flow induced vibrations.  Need to have this considered and evaluated early on.

- In addition to the recommendations on HVAC system made by “Temperature Stability Workgroup”, I would recommend performing a in depth peer review by a ME from a sister facility (both now and during Title I)

- Use a “Computational Fluid Dynamics” CFD Model simulate the load and Temperature within the tunnel.  It was suggested to collaborate with TPS (NSRRC) who has done similar analysis.

- It was suggested to have uniform return air (this may not be necessary pending CFD results). Chris indicated that he may also consider looping the air supply ducts to allow for redundancy (for just in case an indivuaddl AHU goes down unrepentantly)

- It was suggested that supply air ducts be reduced from 20 to 15 to correspond to the 15 super cells.

- Accelerator group to confirm no significant load variation during operations.

- Consider shutting lights in SR during operations to reduce load and air changes.

- Verify that all critical and life safety systems are connected to the  Emergency Power.   This issue also came in conjunction with the cryogenic N2 system.