Isabela Project Hunt Camp Facilities

6-7-2000

The meeting with Felipe Cruz went well, however he started the meeting by stating that he did not feel that solar would work for the hunt camp. In describing the camp and it’s requirements it became obvious that the camp will be an energy and logistical challenge. Adding to the problem is that the facility is for a short-term project (3 years) and the entire camp must relocate after approximately every 6 months. The entire facility must be air transportable in under 1200 lb. units.

Recommendations-

Power System for the camp-

There is no real logical answer to the power requirements for the facility. In a remote location like this there is every good reason to specify using renewable energy, both a combination of wind and solar to power the camp to reduce the dependence on fossil fuels. However since the facility is for a short term project and is further complicated by the fact that the camp will relocate every 6 months, the cost and construction infrastructure for a renewable energy system does not make economical sense.

There are extraordinary energy demands for the camp to include power for a kitchen facility with 2 refrigerators and 2 freezers, cooking range, lighting, small appliance loads, 2 saltwater desalineators, pumps for salt water, waste water disposal systems, 4 freezers for dog food and air conditioning units on the living quarters. The renewable energy/solar system to operate such a facility through the night would require a capitol investment of over $125,000 and it would not be easy to relocate. In such a case a diesel generator is the most economically viable solution to providing power to the camp.

The best answer to controlling the energy operations of the camp is to provide a generator capable of handling the average load of the system. However the problem with the camp facility is that the generator must be drastically oversized to withstand the large potential motor start requirements of the refrigeration units, and as a result will run inefficiently a majority of the time. The answer is to operate the generator in conjunction with a battery storage bank and inverters which can handle motor start requirements, store excess generator capacity and even shut down the generator during periods when it is not required. A sufficiently sized battery bank can also have the capacity to provide the camps energy during the night when quiet time is desired. Generally such a hybrid generator/battery system can reduce engine run time by up to 66%. In the case of this camp facility with its high load requirements, by downsizing the generator and having a planned operation of 16 hours a day it is possible to reduce engine run time by 40% and corresponding fuel consumption by 60%. This is a major factor considering the high logistical costs of fuel delivery to the camp locations.

The load calculations for the camp are estimated to be a 24-hour demand of 174 kWhr. A 12 kW generator operating  14.5 hours per day will generate all the daily power for the camp. However peak load demand on the generator is estimated to be 15.2 kW, which with electrical motor starting would require a 20kW generator. A 12 kW generator combined with a battery bank and two 5.5kW inverters would have the capacity to handle any peak loads the system requires and the fuel savings are dramatic.

12kW Generator, 1.4 gallons per hour @ 14.5 hours per day X 365 X 3 years = 22,228.50 Gallons of fuel @ $1.50 delivered cost = $ 33,342.75VS-

20kW Generator, 2.1 gallons per hour @ 24 hours per day X 365 X 3 years = 55,188 Gallons of fuel @ $1.50 delivered cost = $ 82,782.00

The cost of the inverters (2 at $3,000 and the batteries 4 @ $2,500 + hookups $500.00) a total of $16,500.00 will pay for it self almost four times over and will provide quiet time for camp operations. A further benefit to having the inverters and batteries is the ability to add solar or small wind generators to further reduce engine run time.

Another option to meditate the environmental concerns of using diesel fuel for camp operations is to offset the emissions created in camp by installing solar and renewable energy at the Park Headquarters. This would reduce the diesel fuel use and related emissions on Santa Cruz Island, essentially buying back the emissions caused by the camp generator. A good demonstration project could be to install a 4.4kW solar array, with two 300 watt wind generators on the facility shading the bicycle parking area at Park Headquarters. This size array would generate electricity for the park, generate interest in renewable energy by the public and demonstrate the Parks environmental mission. Such an installation would cost under $30,000 and could be paid for out of the fuel savings from camp operations.

Further recommendations to manage energy usage-

- Provide one propane stove in addition to the electric stove to allow for cooking without the generator. The propane stove should have electronic ignition, not pilot lights to reduce propane usage.

- When the living quarters are not occupied during the day the air conditioners should be shut off to prevent unnecessary cooling load.

- Run the desalinator units during the day when the generator is running and the air conditioners are turned off.

- Use a heat exchanger off the generator engine to provide hot water for the camp.

- Using the generator to burn up “bad” helicopter fuel will reduce fuel shipments to the camp and eliminate the problems of disposal of waste fuel.

Logistical Movements-

During the relocation of the camp facilities it is logistically imperative that the Guadalupe River be made available to the project. Transporting materials by helicopter sling load over 8-10 miles will require over 20-minute round trips. Assuming 3 trips per hour, refueling stops and crew breaks, in one day only 21,000 pounds of material can be transported. If the Guadalupe River were to assist, by using the helicopter to sling loads  onto the boat, which can transport 44,000 pounds of deck cargo and than moving the material by sea to the new site, many hours of valuable helicopter time would be saved.. Than by unloading the boat with the helicopter in conjunction with regular sling transport operations more than triple the amount of material can be moved in one day.

The project should purchase 50 Mega-Bags for the staging of materials and for camp movement. These Mega-Bags have become an indispensable tool at Channel Islands NP for aerial sling work and cargo operations. They are low in cost, last a long time and allow for better, safer sling operations.  http://www.trimeg.com  $27.00 each delivered in California.

Disposal of human waste can be a problem, but the concept of using a marine head treatment process should work well as the camp facilities are located in a marine environment.

I will check with the inverter manufacturer and get their recommendations on system configurations and provide the information to Felipe. In addition information on the reverse osmosis water makers is being sent from Village Marine.

Kent Bullard

Maintenance Supervisor

Channel Islands National Park

kent_bullard@nps.gov