## New Method
Fume Hood Energy Use Example [Seattle weather conditions] • Prepared by Evan Mills and Dale Sartor -- LBNL Applications Team
System Assumptions
Hoods use 100% outside air, 24/7/365 operation; constant-volume system
Hood Flow (six-foot nominal opening) |  | 1250 | CFM
Combined fan power (supply/exhaust) [2] |  | 1.8 | W/CFM | Kjelgaard assumes 0.9W/CFM for supply only)
Cooling plant efficiency [1] |  | 1 | kW/ton | Kjelgaard assumes a range of 0.45 to 1.4
Heating system efficiency |  | 70% |  | for a range of cooling plant types
Reheat Energy (assume average delta-T is 10F: 55->65F) |  | 94608 | BTU/year-CFM
Outside air is cooled or heated to 55deg. F supply temperature |  |  | = (0.018 BTU)(10deg F)(60min)(24h)(365days)
Air is reheated at each zone for temperature control; Conservatism: supply air often cooler, humidification energy not included in this analysis
State | Washington | Washington
City | Seattle | Seattle
| (Gas reheat) | (Electric Reheat)
Electricity Price: avg. of com'l and ind'l tariff ($/kWh) [3] | 0.07 | 0.07
Electricity Demand Charge ($/kW-year) | 120 | 120
Natural Gas Price ($/MBTU) [3] | 6.5 | 6.5
Cooling & Air-handling Electricity
Cooling ton-hours/CFM (55deg supply) [1] | 2.49 | 2.49
Chiller energy (kWh/year) | 3112.5 | 3112.5
Fan energy (kWh/year) | 19710 | 19710
Total (kWh/year) | 22822.5 | 22822.5
Total Power (kW/hood)
Fan | 2.25 | 2.25
Chiller (assuming outside air cooled 40 degrees F) | 4.5 | 4.5
Reheat |  | 3.9555
Total kW | 6.75 | 10.7055
Cooling and Air-handling Electricity Cost
Electricity ($/year) | 1597.575 | 1597.575 | not including reheat (included under heating energy)
Demand ($/year) | 810 | 1284.6557 | includes demand cost for reheat
Total ($/year) | 2407.575 | 2882.2307
Heating Energy
Supply Heating Energy (Therms/CFM) [1] | 0.61 | 0.61
Supply at 55 deg. F (BTU) | 76250000 | 76250000
Reheat 10 deg (55 to 65F) (BTU) | 118260000 | 118260000
Total (BTU) | 194510000 | 194510000
Energy (kWh) |  | 34649.8682 | electric reheat energy
Energy (BTU, gas) | 277871428.5714 | 0
Heating Cost ($/year) | 1806.1643 | 2425.4908
Total Per-Hood Energy Cost ($/year) | 4213.7393 | 5307.7215
$/CFM | 3.371 | 4.2462
Sources:
1. Kjelgaard, J.M. 2001. Engineering Weather Data. McGraw-Hill. ISBN 0-07-137029-3
2. Weale, J., D. Sartor, and E.L. Lee. 2001. "How Low can Your Go? Low Pressure Drop Laboratory Design.
3. Energy Prices: (average of industrial and commercial tariffs). Demand charges are LBNL estimates.
elect | http://www.eia.doe.gov/cneaf/electricity/epm/epmt53p1.html | http://www.eia.doe.gov/cneaf/electricity/epm/epmt53p1.html
gas | http://www.eia.doe.gov/oil_gas/natural_gas/info_glance/sector.html | http://www.eia.doe.gov/oil_gas/natural_gas/info_glance/sector.html