Dog Kennel Septic System

Park Headquarters, Puerto Ayora, Santa Cruz Island

On Monday June 5, 2000 I met with Jeff, the hunt dog coordinator and we went to the new dog kennel facility which is just being completed. The project presented for my review is the design and configuration of the wastewater systems for the facility which are required for hunt operations, but are desired by the park to be designed to prevent contamination of the sub surface water supply.

The present configuration of the kennel has a capacity of fifty dogs in the facility, which is split into two areas, which for this report I will refer to as the north septic (NS) and the south septic (SS) systems. Currently the plumbing discharge lines and junction boxes have been installed, and work has begun to excavate for the two septic tanks. The SS is also required to service the office/food preparation facility. It is also proposed that the kennel facilities may be expanded in the future and an additional septic system may be required.

On Tuesday June 6, I met with Carlos, the Park Engineer and we discussed the design for the septic tanks, possible solutions to include evapo-transpiration (ET) of septic effluent and inspected the current site conditions. I told him to proceed with the tank construction and found there are adjacent areas, which may function for the ET site. Site conditions are very difficult for excavation in the dense lava materials and blasting may be required to install the septic tanks. The areas for the ET beds are also constrained by terrain and grade for gravity flow from the septic tanks. The septic tanks will be constructed to the current design for the islands, with a three stage tank, with the third chamber being an open bottom chamber semi filled with rock as a filter to the grotto below, with very limited contact time for treatment. We had discussion on leach systems, the infiltrator chambers, evapo-transportation and local material design.

With a 50 meter transect tape I measured the ET bed sites for the dog kennels. The NS  bed is located 18.5 meters to the west of the septic tank and will provide a bed size of 6x9 meters (54 m².).  The SS is more restricted by terrain and is located to the south adjacent (3.5 meters) to the septic tank and will provide a bed size of 6x8 meters (48 m².)

Recommendations-

Short Term- Proceed with the construction of the septic tanks of the standard island design with four important design modifications.

- Provide a top access opening (Boca de vista) into the third filter chamber to allow for making the plumbing connections to connect to the evapo-transpiration beds. The discharge line to the bed will be installed through an opening drilled through the side of the chamber.

- Seal the inside of the first and second chambers of the septic tanks to prevent groundwater intrusion or leakage of untreated liquids into the groundwater aquifer.

- Install piping “Tee” baffles on the first chamber inlet and outlets of both chambers to prevent transfer of surface scum and untreated materials. Between the chambers only one 4” pipe is required. The boca de vistas should be positioned to allow for inspection and cleaning of the inlet of the camara de acumulacion, the outlet of the camara de sedimentacion, and a small boca provided above the first chamber discharge to allow for maintenance. See the diagram next page-

- The discharge from the floor and sink in the kitchen should join in a junction box which will function as a grease trap, and than be plumbed to enter the camara de acumulacion of the septic tank. It will be very important to stress to the workers preparing the dog food to avoid flushing any grease, animal fat or bone into the waste water system to avoid clogging the lines. The grease trap box will require regular cleaning to remove any accumulated materials.

Water conservation both as a supply and as a wastewater treatment concern should be an important consideration in the operation of this facility. The idea of using fresh water to wash dog waste into a drain for treatment may require a second thought. Water should be used to keep the kennels clean and sanitary, but accumulations of fecal matter should be manually collected and disposed of. Three options exist for the disposal. 1. Haul to the municipal dump, which is less preferred due to sanitation concerns, waste of important man-hours and resources. However regular dump trips will be required to dispose of animal byproducts from the butchering operation so some dog waste can also be disposed of in this manner. 2. Construct a sealed dry compost pit for solid waste decomposition. This option is least desired, as some biological leaching into the sub surface area will occur. 3. Dispose of dog fecal matter directly into the camara de acumulacion of the north system septic tank. This is the recommended preferred option as the north system is lightly loaded and has the capacity for the installation of the larger ET system. However care should be taken in this process to only dump fecal matter while avoiding bones, other trash items and sand/rock matter, which will eventually fill the camara de acumulacion.

Long Term- Construct Evapo-transpiration beds to perform final treatment of the septic effluent and discharge of liquids into the atmosphere. This will allow for sanitary waste treatment and prevent effluent discharge into the sub surface aquifer, which provides water to the park facilities. Attached to this report are design criteria for the sizing of the ET beds and construction specifications.

If the kennel facilities are expanded an additional septic system is required it is recommended that tank location and ET bed site location be given important consideration. The low area in the center of the kennel compound may be desirable as the new kennel sewage lines could flow to the central point and the low area can provide the ET bed site with minimal surface disturbance. A more cost-effective alternative may be to install a pump and utilize the existing North Septic system that has the capacity to handle the additional 300 liters per day the new facilities could generate.

This report is site specific for the dog kennel facility, but the calculations on evaporation and systems sizing can readily be adapted for other waste treatment facilities in the Puerto Ayora area.

Kent Bullard

Maintenance Supervisor

Channel Islands National Park

kent_bullard@nps.gov

On-Site Disposal of Waste Water through Evapo-Transpiration

System Calculation and Design Criteria

Isla Santa Cruz, Galápagos, Ecuador

1. INTRODUCTION

Domestic wastewater disposal in the islands has traditionally involved a three-stage septic tank in which the last chamber is rock filled, open on the bottom and acts as a filter for the final effluent. This system in conjunction with existing sub terrain features of extremely porous lava material does not allow for sufficient contact and treatment time before the effluent comes into contact with the sub surface fresh water aquifer.  This has resulted in the contamination of the aquifer and problems for the population in obtaining safe potable water. The availability of and type of building materials obtainable on the island limit options in the design and construction of on site effluent treatment facilities.

2. OVERVIEW OF SYSTEM COMPONENTS

Liquid sewage wastes are treated in a sealed, locally constructed two stage concrete septic tank of a nominal liquid capacity of 3,900 liters (1,000 gallons). 2M x 2.45M x 1.5M exterior dimensions.

Waste liquid volumes are reduced through practice of water conservation and it is estimated that for the North Septic System (NS) daily flow will be less than 150 liters. The South Septic System (SS) flow will be higher as it also serves the office with bathroom (toilet and sink), the veterinarian office with sink, and the kitchen used to prepare food for the dogs. The estimated flow for the SS is 450 liters per day. This will allow for a minimum of eight days of contact time in the septic tank for treatment.

A grease trap is a simple tank, which allows any particulate matter from the kitchen drain system to settle out. Oil, fats and other materials, which are lighter, than water and remain on the surface, are separated in this manner and can be manually, removed to prevent clogging of the septic system.

An Evapo-transpiration (ET) Bed, a locally constructed sand and gravel bed, plastic lined and planted with native grass and shrubs, recycles the final effluent waste through evaporation and transpiration.

3. WASTE VOLUMES

The initial sizing of the septic tank and evapo-transpiration treatment bed is determined by the amount of waste flow expected from each facility.

Toilet Flows

It is assumed that the flow rate from the toilet system will be 3.25L (0.9 USG) per use. As this is a daytime only work facility with limited staff use is assumed that less than 30 flush cycles will occur daily. A sign above the toilet, suggesting to only flush when required will help to conserve water supplies and reduce septic system loading. 
Other Flows

Waste from the sinks in the toilet, veterinary office and food preparation facility are assumed to be for primarily cleaning actions and estimated at 200L per day.

The wash down water effluent from the kennel facilities is estimated at 150L per day, based on cleaning the 25 dog kennels.

Total flows

Based on these figures total flows for the North System would be 150L, and the South System would be 450L.

For reference below is a table, which shows, assumed wastewater flown for households practicing water conservation.

Assumed total Wastewater Flows from Households of Different Sizes

| # Persons | Flows |  |
| --- | --- | --- |
|  | Liters/Day | US Gal./Day |
| 1 | 165 | 44 |
| 2 | 330 | 87 |
| 3 | 495 | 131 |
| 4 | 660 | 175 |
| 5 | 825 | 218 |
| 6 | 990 | 262 |

4. GREASE TRAP

A simple grease trap is required to allow the small amounts of particulate matter in the gray water to settle out, while at the same time separating oil, fats and other materials, which are lighter than water. The use of a grease trap prevents solids from clogging up and reducing the effectiveness of the septic tank and evapo-transpiration bed.

The design of a grease trap is very simple, and because it is not handling toilet wastes, the trap need only be big enough to handle 24 hours gray water output from the kitchen sink. Based on the above flow rates, the existing grease trap at .5m X .5m has a capacity to handle the estimated 200 liter flow per day.

5. EVAPO-TRANSPIRATION (ET) BED

5.1 How It Works

An Evapo-Transpiration Bed works to evaporate waste liquids in three main ways:

- Natural Evaporation

- Transpiration of Plants

- Increased evaporation from the heat energy of bacterial action

Precipitation penetrating the bed must then be subtracted from the total impact of these three factors to find the net evaporation performance of an ET Bed.

Once these factors are known (as the are from monthly weather records at Puerto Ayora) it is a relatively simple matter to determine the size of the bed required to handle the amount of waste water being produced.

The method of calculating natural evaporation figures, and the numbers for Puerto Ayora (for 1995, considered an average weather year), are shown at Appendix 1, while the figures for transpiration and bacterial action are shown at Appendix 2 and 3 respectively. Precipitation numbers are shown at Appendix 4.

As shown below the results from adding these factors together for Puerto Ayora, varies from a low figure for net evaporation/transpiration of 4.3mm. (0.34") per day in December to 11.8mm. (0.46") per day in April.

Table 2

Net Daily Evaporation By Month, 1995, for Puerto Ayora, Isla Santa Cruz

|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| mm. per Day | 4.4 | 10.5 | 11.2 | 11.8 | 11.4 | 10.6 | 10.7 | 10.5 | 10.1 | 8.8 | 8.2 | 4.3 |
| Inches per day | .18 | .4 | .45 | .46 | .44 | .41 | .43 | .42 | .41 | .37 | .37 | .34 |
| Liters/day /M² | 4.4 | 10.5 | 11.2 | 11.8 | 11.4 | 10.6 | 10.7 | 10.5 | 10.1 | 8.8 | 8.2 | 4.3 |

5.2 Building an Evapo-transpiration (ET) Bed

ET Beds are simple and very inexpensive to construct. Bed calculations shown in this guide are based on a bed depth of 60cm. Because the calculated level of liquid in the bed is never closer than 30cm from the surface, the 60cm depth provides a safety reservoir.

The bed should be located so that the output from the septic tank will flow naturally into the ET bed with a gentle slope at the interface between the gravel and sand layers.

As the ET bed is to be built over rocky ground, a sand or fine crushed lava layer about 2.5cm deep should be placed under the plastic sheet. This material should be compacted to prevent settlement and is important as it protects the plastic lining the bed from puncture.

The plastic liner should be 3 layers of black or clear plastic, 10  mil. thick and should be extended upwards around the sides so that the upper edge of the sheet is right up to the surface level. The sheet should be supported from the outside by a berm of fine crushed lava or sandy material. If an overlap of the sheets is required, this should be about 50cm (20") wide to keep the bed watertight.

Immediately above the sheet 2.5cm of sand or fine crushed lava material should be used to protect the sheet from sharp stones, and above this the bed should be filled with a 15cm base of loosely placed 1cm-2cm crushed lava material. Immediately on top of the 1-2cm material, a 4" perforated plastic sewer pipe, placed 1 meter from the edge of the bed and 2.5-3 meters apart, and should be placed with a gradient of 1-2o. It is preferable to attach a 4" ventilation pipe at the end of the distribution pipe, with a hood surmounting it, to assist in providing a greater supply of oxygen to the ET bed. Both ends of the pipes are connected forming a circle of pipe in the bed. This is desirable to allow flow around the bed system in case one lateral line was to become clogged by debris. The 4” perforated pipes are than covered with 1-2cm material, covering and surrounding the pipes by 5-7cm. If the perforated pipes are not locally available, the pipes can be manufactured by drilling a 1cm hole spaced at 10cm intervals on both sides of the pipes on a line 1/3 of the way up from the bottom. If possible bring the supply pipe from the septic tank over the berm. If this is not possible to grade or site conditions the entry through the berm must be sealed to prevent leakage around the pipe. Use mortar, plastic tape/glue or similar sealing materials. 

Above the 1-2cm crushed lava material (gravel) layer, the bed should be filled with 45cm of fine crushed lava of a grain size of about 1mm. (4 mil.). After settling, the bed should be filled so that it has a center crown of about 15cm above the sidewalls for diversion of rain. The bed should be level or above the surface of the surrounding terrain around the perimeter to prevent rainwater runoff from entering the bed.

Putting no more than a sprinkle (1cm) of topsoil on the surface, a cap is than formed which will help seal the surface and promote runoff of rains. Native grass such as the Sedge should be plug  (bare root) planted in the bed. Additionally some native shrubs can also be planted (bare-root) in the bed.  About 25-30 Sedge should be planted per square meter and one shrub per square meter. These plants are crucial in performing evapo-transpiration functions. The ideal shrubs should be each about 30-45cm high when planted. Dr. Mark Gardner of the Darwin Station can provide further information on the types of native plant materials to use.

5.3 Sizing An ET Bed

An ET bed may be sized in the following way:

i) Determine the amount of wastewater per month the ET bed is to be designed to handle.

In this system a figure of 450 Liters per day, or 13,500 Liters per month is assumed. And the design criteria will address the South System, which has the greatest waste flow.

ii) Determine the net average daily evaporation through the whole year in Liters/month/M² by:-

a) Adding together the "Net Daily Evaporation by Month" in Liters/day/M² for every month of the year. (See Table 2)

b) Divide by 12 to obtain the average net monthly figure

c) Multiply by 30 to get average monthly evaporation in Liters

per month per square meter.

In Puerto Ayora this average monthly figure (calculated from table 2) is 112.5/12 X 30 = 281 Liters per month per square meter of ET bed.

iii) Divide the assumed monthly wastewater volume (in this case 13,500 Liters) by the monthly evaporation per square meter. (281 Liters) to determine the number of square meters required .

In Puerto Ayora this works out to 13,500/281 or a bed size of 48 M² for the South Septic System.

For a residence in Puerto Ayora of 5 people, with a monthly flow of 25,000 Liters a bed size of 88 M² would be required, or about 17.5 M² of ET bed per person. Table 3 below shows the required bed size in Puerto Ayora for different household sizes, assuming a total output of 165 Liters per person per day.

Table 3 
Required ET Bed Size in Puerto Ayora for Differing Household Sizes

| # People | ET Bed M² |
| --- | --- |
| 1 | 17.5 |
| 2 | 35 |
| 3 | 52.5 |
| 4 | 70 |
| 5 | 87.5 |
| 6 | 122.5 |

For interest, Appendix 5 shows projected liquid levels in a 87.5 M² bed every month of the year, for 1995, given an input rate of 25,000 Liters per month. The level peaks in January at a level about 15cm below the surface, and the bed is virtually empty from August through October.

7.4 Safety Factors Included In ET Bed Sizing

The safety factors incorporated into bed sizing are as follows: 
The calculation method assumes the maximum liquid level in Puerto Ayora would be about 30cm below the surface of the bed. 
The benefits of extra transpiration from the planting of shrubs has been ignored. Planting shrubs could increase overall net daily evaporation by 25%, and are strongly advised to increase bed performance. 
Transpiration rates are based on plant activity in the first year only. Rate of evaporation increases in subsequent years as the plants mature have been ignored.

Transpiration rates for plants are based on grasses with known evaporation rates in North Carolina which are dormant and less effective in evaporative activity between October and March which is the rainy season in Puerto Ayora and more rain water intrusion to the bed would occur.

The daily evaporation rates for bacterial action are based on figures from Miami, which is less temperate than Puerto Ayora, and thus less effective in biological evaporative action.

Taken together these safety factors provide substantial reserves. However, if input increases far above design capacity, the bed should be extended in size.

APPENDIX 1.

Natural Evaporation from the Saturated Sand Layer in the Bed 

Everyone is familiar with evaporation, and how the amount of liquid evaporated naturally varies with climate and the time of year. Figures for average evaporation are available by month for all climatic zones in North America. These figures are normally for "Pan Evaporation" which is the amount of evaporation that will occur from a free standing container of water.

In Puerto Ayora pan evaporation varies from 1.2mm (.047") per day in December to 3.3mm (.13") per day in March.

Table 4

Daily Pan Evaporation Rates By Month For Puerto Ayora, 1995

|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| mm/day | 1.9 | 3.0 | 3.3 | 2.3 | 2.0 | 1.7 | 2.0 | 1.9 | 2.1 | 1.8 | 1.61 | 1.2 |
| Inches/day | .075 | .12 | .13 | .09 | .08 | .07 | .08 | .075 | .083 | .07 | .063 | .05 |

It is not so widely known that these pan evaporation figures can increase dramatically if instead of having a container of water, the liquid is contained in a semi saturated sand or fine crushed (1mm) lava bed. In such a situation, liquid covers the surface of the grains of material, and there is a very greatly increased contact area between air and liquid. The increased evaporation which results, can also be quantified. This increase, which can more than double pan evaporation figures, varies with the depth of the liquid in the bed as shown in Table 5 below.

Table 5

% Increase To Pan Evaporation With Waste Liquid At Different Levels Below bed Surface

Down in cm

| 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| +120% | +113% | +93% | +71% | +60% | +40% | +30% | +12% | 0 | -12% | -23% | -33% |

As an example, in Puerto Ayora in January, if the depth of liquid in the bed was 5mm below the surface, then evaporation would increase from the regular pan evaporation rate of 1.9mm (.075") per day to 4.2mm (.165") per day. Evaporation rates for Puerto Ayora with waste levels 20cm down in the bed are shown for each month on Table 6 below.

Table 6

Assumed Daily Evaporation Rates By Month With Liquid 20cm Down In The Sand Bed

(71% Better Than Straight Pan Evaporation)

|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| mm/day | 3.25 | 5.3 | 5.6 | 3.9 | 3.4 | 2.9 | 3.4 | 3.3 | 3.6 | 3.0 | 2.7 | 2.1 |
| Inches/day | .13 | .20 | .22 | .15 | .14 | .11 | .15 | .13 | .14 | .12 | .11 | .08 |

APPENDIX 2.

Transpiration From The Vegetation Planted In The Bed

In order to grow, plants need to draw liquid in through their roots. After use by the plant, excess liquid is transpirated, or given back to the atmosphere, through the foliage.

Some plants transpirate much more than others, for example one corn plant requires some 4.2 L (1.1 USG) per day during a Michigan growing season, whereas a small maple tree would need about 65L (17 USG) per day in New England.

Often a mixture of grass and shrubs proves to be the ideal vegetation for an evapo-transpiration bed.

Transpiration volumes vary, not only with type of vegetation, but also with the time of year, climatic zone, the amount of oxygen in the waste, and the number of years the vegetation has been planted.

Transpiration figures using conservative assumptions of first year grass only are shown below in table 7.

Dr. Mark Gardner of Estatión Científica Charles Darwin recommends the use of Sedge (cyperus lingularis and c. andersonii) as native materials, which would perform well as transpiration growth and which are readily available and can be plug planted. He can also recommend the best growing shrubs to use, which can increase bed evaporation by as much as 25%.

Table 7

Estimated Daily Transpiration Rates By Month Assuming only Grass Planted (No Shrubs) with fully aerobic waste water. Figures vary with plants having a dormant season Oct-Mar. which builds a safety factor into the calculations for Puerto Ayora which has a more mild climate year round.

|  | Jan* | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| mm/day | 2.0 | 2.1 | 3.2 | 4.5 | 4.5 | 4.3 | 4.1 | 3.9 | 3.7 | 2.7 | 2.3 | 2.1 |
| Inches/day | 0.08 | 0.08 | 0.13 | 0.18 | 0.17 | 0.16 | 0.15 | 0.15 | 0.15 | 0.13 | 0.13 | 0.13 |

*Based on South Carolina figures.

If 25-30 shrubs per 1000 sq. ft. were planted, figures would almost double.

APPENDIX 3

Evaporation from the Heat Generated by Bacterial Action in the Bed

& Totals for All Three Evaporation Effects.

3.1 Evaporation from the Heat Generated by Bacterial Action in the Bed 
Bacterial action in the bed occurs naturally to oxidize organic material and convert it to stable nutrients which can be taken up and used by plants. This bacterial action releases heat energy which in turn increases evaporation rates.

The amount of energy released will depend on a number of factors, including the amount of dissolved oxygen in the excess liquid, and the ambient temperature. The figures by month, assuming aerobic waste liquid, is shown at Table 8. The slightly colder temperature in Miami reduces the effectiveness of aerobic action which builds a buffer into system calculations for Puerto Ayora.

Table 8 
Daily Evaporation from Bacterial Action By Month In Miami For Aerobic Waste Liquid.

|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| mm./day | 3.3 | 3.3 | 3.3 | 3.4 | 3.4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.4 | 3.3 | 3.3 |
| Inches/day | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.14 | 0.14 | 0.14 | 0.14 | 0.13 | 0.13 | 0.13 |

3.2 Total Evaporation resulting From the Evaporation, Transpiration & Bacterial Action 
Total amounts of liquids removed from the ET bed is the sum of natural evaporation (Table 6), Transpiration (Table 7), and Bacterial Action (Table 8). Table 9 below is the sum of these three tables, before taking into account the negative impact of precipitation (See Appendix 4).

Table 9 
Daily Total Evaporation/transpiration By Month for Puerto Ayora.

|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| mm./day | 8.55 | 10.7 | 12.1 | 11.8 | 11.4 | 10.7 | 11 | 10.7 | 10.7 | 9.1 | 8.3 | 4.5 |
| Inches/day | .34 | .41 | .48 | .46 | .44 | .41 | .44 | .42 | .43 | .38 | .37 | .34 |

APPENDIX 4

Negative Impact of Precipitation & Total Net evaporation

4.1 Negative Impact of Precipitation 
The evapo-transpiration bed is also subject to precipitation in the form of rain which has to be deducted from total evaporation/transpiration as detailed in Table 9.

Infiltration of precipitation into the Recycling Bed can be minimized somewhat by good bed design. As shown in the section on "Building the Recycling Bed", the best approach is to build the bed with a small 6" dome in the middle so that a proportion of precipitation drains off. Studies have shown that such a dome will, on average, allow only 70 % of the precipitation to penetrate the bed. The negative impact of precipitation obviously varies by climatic zone and month. The figures for Puerto Ayora, 1995 are shown on Table 10. 

Table 10

Average Daily Precipitation In Puerto Ayora By Month, for 1995, with Penetration Rate Of 70%

|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Total Precip. mm/day | 5.9 | .30 | 1.3 | .01 | .04 | .14 | .44 | .32 | .86 | .51 | .16 | .31 |
| Infiltration (70%) mm/day | 4.1 | .21 | .90 | NA | .03 | .09 | .31 | .22 | .6 | .35 | .11 | .22 |
| Infiltration (70%) inches/day | .16 | NA | .03 | NA | NA | NA | .01 | NA | .02 | .01 | NA | NA |

  - Daily Total Net Evaporation by Month 
By taking Total Evaporation/Transpiration figures (Table 9), and subtracting the amount of precipitation penetrating the bed (Table 10), the Daily Total Net Evaporation performance of a Recycling Bed is determined. These performance figures are shown for Miami at Table 11.

Table 11 
Daily Net Evaporation By Month

|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| mm/day | 4.42 | 10.5 | 11.2 | 11.8 | 11.4 | 10.6 | 10.7 | 10.5 | 10.1 | 8.8 | 8.2 | 4.3 |
| Inches/day | 0.18 | 0.40 | 0.45 | 0.46 | 0.44 | 0.41 | 0.43 | 0.42 | 0.41 | 0.37 | 0.37 | 0.34 |

The above mm/day figures translate directly to Liters (L) per square meter (m2) per day. Thus, for May a Bed of 1 m2 can evaporate 11.4 L/day in Puerto Ayora. To convert inches per day to US Gallons per square foot, multiply by 0.62

APPENDIX 5

Loading of 87.5 M² ET Bed with Input of 25,000 Liters/Month to determine Liquid Levels by Month.

To check the Bed sizing in the example in Item 7.3 above, the ET bed has been loaded month by month to ensure that the levels in the bed are well down in the bed throughout the year. Starting in the month of October, the Table below shows that the level rises through to February and then declines until by August the bed is virtually empty.

Table 3

Utilization Of 87.5 M² Bed With Input 25,000 Liters/month

This table starts in October when it is assumed the bed would have no carry over from the preceding months.

| Mth. | 87.5 M² bed Capacity 87.5 M² X 60cm deep (52.5 M³ Approx. 52,500 Liters) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Evaporation Liters/Month | Input Liters/Month | ET Surplus/ (deficit) Liters/Month | Liters in Bed Cumulative Surplus/(deficit) | % Bed capacity used |
| Oct | 23,820 | 25,000 | (1,180) | (1,180) | 2% |
| Nov | 21,525 | 25,000 | (3,475) | (4655) | 9% |
| Dec | 11,663 | 25,000 | (13,337) | (17,992) | 34% |
| Jan | 11,935 | 25,000 | (13,065) | (31,057) | 59% |
| Feb | 25,725 | 25,000 | 725 | (30,332) | 58% |
| Mar | 30,380 | 25,000 | 5,380 | (24,952) | 47% |
| Apr | 30,975 | 25,000 | 5,975 | (18,977) | 36% |
| May | 30,922 | 25,000 | 5,922 | (13,055) | 25% |
| Jun | 27,825 | 25,000 | 2,825 | (10,230) | 19% |
| Jul | 29,024 | 25,000 | 4,024 | (6,206) | 12% |
| Aug | 28,481 | 25,000 | 3,481 | (2,725) | 5% |
| Sep | 26,512 | 25,000 | 1,512 | (1,213) | 2% |

Note- These figures are based on 1995 weather data in which the annual rainfall was 316mm, slightly higher than the median rainfall figure of 297mm. Rainfall at Puerto Ayora is cyclic with dry years followed by wet years. The importance of the safety factors built into the calculations are obvious, but during a bad El Nino cycle it is possible for the system to overflow allowing partially treated effluent diluted with rainwater to enter the aquifer. But even developed sewer systems and standard leach fields fail with regular occurrence when flooded by El Nino rains. With this system in place even during the worst El Nino year when 9 times the mean rainfall fell, over 50% of the effluent will be treated. When averaged with the dry year cycles this system will treat almost all of the effluent through evapo-transpiration with out any contact with groundwater.

Reference-

On-Site Recycling of Domestic Sewage in Florida,

By: C.M.Wilkinson    Fall 1996, http://www.

Native Plant Reference from Dr. Mark Gardner, Estatión Científica Charles Darwin, Santa Cruz, Galápagos, Ecuador

Weather Data from Estatión Científica Charles Darwin, Santa Cruz, Galápagos, Ecuador

Taking Care of Your Septic System

- Always conserve water to reduce the amount of wastewater that must be treated and disposed of.

- Repair all leaking faucets and toilets.

- Dispose of only biological wastes into the system.

- Divert all down spouts, rainwater and other surface water away from the septic tank and disposal field.

- Do not use your sink as a garbage disposal.

- Do not put solvents, oils, paints, thinners, disinfectants, pesticides, etc. down the drain. This can disrupt the biological treatment method.

- Do not dig in the evapo-transpiration bed, or build anything over the system.

- Do not plant anything in the ET bed except native plants and shrubs.

- Do not drive over the ET bed or compact it in any way.

Please Do Not Flush the Following Items:

paper towels

hair combings

fats, grease and oils

dental floss

gauze bandages

coffee grounds

condoms

disposable diapers

cigarette butts

kitty litter

tampons

sanitary napkins

panty liners

Line drawing of proposed ET bed construction is available at the following-

http://www.nps.gov/chis/septic.jpg