July 22, 1994

Contract #TW0592

SPECIAL SPECIFICATION

SECTION 16495

TRANSFER SWITCHES

PART 1 - GENERAL                                           						  Page

1.01 Related Documents	2

1.02 Summary	2

1.03 Remote Annunciation System Description	3

1.04 Remote Annunciation and Control System Description	3

1.05 Submittals	3

1.06 Quality Assurance	4

PART 2 - PRODUCTS

2.01 Manufacturers 	6

2.02 Transfer Switch Products, General 	6

2.03 Automatic Transfer Switches 	8

2.04 Automatic Transfer Switch Features	8

2.05 Bypass/Isolation Switch 	10

2.06 Remote Annunciator Panel	10

2.07 Remote Annunciator and Control Panel	11

2.08 Finishes	11

2.09 Source Quality Control	11

PART 3 - EXECUTION

3.01 Installation 	12

3.02 Wiring to Remote Components 	12

3.03 Connections	12

3.04 Grounding	12

3.05 Field Quality Control	12

3.06 Demonstration	14

SPECIAL SPECIFICATION

SECTION 16495

TRANSFER SWITCHES

PART 1 - GENERAL

1.01 RELATED DOCUMENTS

A.  Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.02 SUMMARY

A.  	This Section includes transfer switches rated 600 V and less.  It includes the following items:

1.  	Automatic transfer switch (ATS).

2.  	Bypass/isolation switch (BP/IS).

3.  	Nonautomatic transfer switch (NATS).

4.  	Remote annunciation system.

5.  	Remote annunciation and control system.

B.  	Related Sections:  The following Sections contain requirements that relate to this Section:

1.  	Transfer switches integral with uninterruptible power supply systems are specified in Division 16 Section "Uninterruptible Power Supply Systems."

2.  	Transfer switches integral with battery systems are specified in Division 16 Section "Central Battery Inverter System."

3.  	Conductors for hard-wired connections between transfer switches and remote equipment are specified in Division 16 Section "Wires and Cables."

4.  	Data circuits between transfer switches and remote panels are specified in Division 16 Section "Control/Signal Transmission Media."

1.03 REMOTE ANNUNCIATION SYSTEM DESCRIPTION

A.  	Functional Description:  A remote annunciator panel annunciates conditions at indicated transfer switches including:

1.  	Sources available (as defined by actual pick-up and drop-out settings of transfer switch controls).

2.  	Switch position.

3.  	Switch in test mode.

4.  	Failure of digital communications link.

1.04 REMOTE ANNUNCIATION AND CONTROL SYSTEM DESCRIPTION

A.  	Functional Description:  A remote annunciation and control panel provides the functions listed below at indicated transfer switches:

1.  	Sources-available indication (as defined by actual pick-up and drop-out settings of transfer switch controls).

2. 	Switch position indication.

3.  	Switch in test mode indication.

4.  	Failure of digital communications link indication.

5.  	Key switch or user code access to control functions of panel.

6.  	Control of switch test initiation.

7.  	Control of switch operation in either direction.

8.  	Control of bypass of time delay for transfer to normal source.

B.  	Malfunction of the annunciator unit or communication link does not affect functions of the ATS.  In the event of a failure of the communication link the ATS automatically reverts to stand-alone, self-contained operation.  No ATS sensing, controlling, or operating function depends on the remote panel for proper operation.

1.05 SUBMITTALS

A.  	General:  Submit the following according to Conditions of Contract and Division 1 Specification Sections.

B.  	Shop drawings or published product data for each transfer switch, including dimensioned plans, sections, and elevations showing minimum clearances; conductor entry provisions; gutter space; installed features and devices; and materials lists.

C.  	Wiring diagrams, elementary or schematic, differentiating between manufacturer-installed and field-installed wiring.

D.  	Single-line diagrams of transfer switch units showing connections between automatic transfer switch, bypass/isolation switch, power source, and load, plus interlocking provisions.

E.  	Operation and maintenance data for each type of product, for inclusion in Operating and Maintenance Manual specified in Division 1.  Include all features and operating sequences, both automatic and manual.  List all factory settings of relays and provide relay setting and calibration instructions.

F.  	Manufacturer's certificate of compliance to the referenced standards and tested short-circuit closing and withstand ratings applicable to the protective devices and current ratings used in this Project, as indicated and as specified in paragraph "Tested Fault Current Ratings."

1.06 QUALITY ASSURANCE

A.  	Manufacturer's Qualifications:  Firms are experienced in manufacturing equipment of the types and capacities indicated and have a record of successful in-service performance.

B.  	Emergency Service:  Manufacturer maintains a service center capable of providing emergency maintenance and repairs at the Project site with an 8-hour maximum response time.

C.  	Comply with NFPA 70, "National Electrical Code," for components and installation.

D.  	Comply with NFPA 99, "Standard for Essential Electrical Systems for Health Care Facilities," and NFPA 110, "Standard for Emergency and Standby Power Systems."

E.  	Comply with NEMA ICS 1, "General Standards for Industrial Control," ICS 2, "Industrial Control Devices, Controllers and Assemblies," and ICS 6, "Enclosures for Industrial Controls and Systems."

F.  	UL Listing and Labeling:  Items furnished under this Section are listed and labeled by UL for emergency service under UL Standard 1008.

G.  	Nationally Recognized Testing Laboratory Listing (NRTL) and Labeling:  Items furnished under this Section are listed and labeled by a NRTL for emergency service under UL Standard 1008.

1.  	Terms "Listed" and "Labeled":  As defined in the "National Electrical Code," Article 100.

2.  	Listing and Labeling Agency Qualifications:  A "Nationally Recognized Testing Laboratory" (NRTL) as defined in OSHA Regulation 1910.7.

H.  	UL Compliance:  Comply with UL Standard 1008, "Automatic Transfer Switches," except where requirements of these Specifications are stricter.

I.  	Single-Source Responsibility:  Obtain ATSs, BP/ISs, remote annunciators, and remote annunciator and control panels from a single manufacturer that assumes responsibility for all system components furnished.

PART 2 - PRODUCTS

2.01 MANUFACTURERS

A.  	Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated in the Work include, but are not limited to, the following:

B.  	Manufacturers:  Subject to compliance with requirements, provide products by the following:

1.  	Automatic Switch Co.

2.  	Caterpillar, Inc.

3.  	Kohler Co.

4.  	Onan Corp.

5.  	Russelectric, Inc.

6.  	Zenith Controls, Inc.

2.02 TRANSFER SWITCH PRODUCTS, GENERAL

A.  	Number of Poles and Current and Voltage Ratings:  As indicated.

1.  	Units smaller than 600 amperes do not have different current ratings for different classes or mixtures of loads, including 100 percent tungsten filament lamp or 100 percent inductive load.

2.  	Units 600 amperes and larger have current ratings that apply to mixtures of loads including 30-percent-maximum tungsten filament lamp load.

B.  	Tested Fault-Current Ratings:  Closing and withstand ratings exceed the indicated available rms symmetrical fault current at the equipment terminals based on testing according to UL Standard 1008, conducted at full-rated system voltage and 20 percent power factor.  Rate each product for withstand duration time as follows when tested for rated short-circuit current correlated with the actual type of circuit protective device indicated for transfer switches for this Project:

1.  	Molded-Case Circuit Breakers, 150 Amperes or Smaller:  1.5 closing and withstand duration cycles.

2.  	Molded-Case Circuit Breakers, Larger than 150 Amperes:  3 closing and withstand duration cycles.

3.  	Power Circuit Breakers:  10 closing and withstand duration cycles.

4.  	Current-Limiting Fuses:  0.5 (nominal) closing and withstand duration cycles.

C.  	Annunciation and Control Interface Components:  Devices at transfer switches for communicating with remote annunciators or annunciator/control panels have communications capability matched with the remote device.

D.  	Solid-State Controls:  Repetitive accuracy of all settings is plus or minus 2 percent or better over an operating temperature range of minus 20 deg C to 70 deg C.

E.  	Resistance to Damage by Voltage Transients:  Components meet or exceed voltage surge withstand capability requirements when tested according to ANSI C37.90.1, IEEE Guide for Surge Withstand Capability (SWC) Tests.  Components meet or exceed voltage impulse withstand test of NEMA ICS 1.

F.  	Four-Pole Switches:  Provide full-capacity neutral switching.

G.  	Enclosures:  General-purpose NEMA 1, conforming to UL Standard 508, "Electric Industrial Control Equipment," except as otherwise indicated.

H.  	Factory Wiring:  Train and bundle factory wiring and identify consistently with shop drawings, either by color code or by numbered or lettered wire and cable tape markers at terminations.

1.  	Designated terminals accommodate field wiring.

2.  	Power Terminals Arrangement and Field Wiring Space:  Suitable for top, side, or bottom entrance of feeder conductors as indicated.

3.  	Terminals:  Pressure-type, suitable for copper or aluminum conductors of sizes indicated.

4.  	Control Wiring:  Equipped with lugs suitable for connection to terminal strips.

I.  	Electrical Operation:  Where indicated, accomplish by a nonfused, momentarily energized solenoid or electric motor-operated mechanism, mechanically and electrically interlocked in both directions.  Switches using components of molded-case circuit breakers or contactors not designed for continuous-duty, repetitive switching between active power sources are not acceptable.

J.  	Switch Action:  Mechanically held in both directions for double-throw switches.

K.  	Switch Contacts:  Use silver composition for switching load current.  Units rated 225 amperes and more have separate arcing contacts.

L.  	Overcurrent devices are not part of switch products.

2.03 AUTOMATIC TRANSFER SWITCHES (ATSs)

A.  	Comply with Level 1 equipment according to NFPA 110, "Standard for Emergency and Standby Power Systems."

B.  	Switching Arrangement:  Double-throw type, incapable of pauses or intermediate position stops during normal functioning except as indicated.

C.  	Manual Switch Operation:  Manually operated under load with the door closed with either or both sources energized.  Transfer time is same as for electrical operation.  Control circuit automatically disconnects from electrical operator during manual operation.

D.  	Signal-Before-Transfer Contacts:  A set of normally open/normally closed dry contacts operates in advance of retransfer to normal source.  Interval is adjustable from 1 to 30 seconds.

E.  	Digital Communications Interface:  Full-duplex RS 422 type, matched to capability of remote annunciator or annunciator and control panel.

2.04 AUTOMATIC TRANSFER SWITCH FEATURES

A.  	Voltage sensing for each phase of normal source.  Pick-up voltage is adjustable from 85 percent to 100 percent nominal, and drop-out voltage is adjustable from 75 percent to 98 percent pick-up value.  Factory set for pick-up at 90 percent and drop-out at 85 percent.

B.  	Time-delay override of normal source voltage-sensing delays transfer and engine start signals.  Adjustable 0 to 6 seconds, and factory set at 1 second.

C.  	Voltage/Frequency Lockout Relay:  Prevent premature transfer.  Voltage pick-up is adjustable from 85 percent to 100 percent nominal.  Factory set to pick-up at 90 percent.  Pick-up frequency is adjustable from 90 percent to 100 percent nominal.  Factory set to pick-up at 95 percent.

D.  	Retransfer Time Delay:  Adjustable from 0 to 30 minutes and factory set at 10 minutes.  Provides automatic defeat of the delay upon loss of voltage or sustained undervoltage of the emergency source, provided the normal supply has been restored.

E.  	Test Switch:  Simulates normal source failure.

F.  	Switch-Position Pilot Lights:  Indicate source to which the load is connected.

G.  	Source-Available Indicating Lights:  Supervise sources via the transfer switch normal and emergency source-sensing circuits.

1.  	Normal Power Supervision:  Green light with nameplate engraved "Normal Source Available."

2.  	Emergency Power Supervision:  Red light with nameplate engraved "Emergency Source Available."

H.  	Unassigned Auxiliary Contacts:  Two normally open SPDT contacts for each switch position.

1.  	Rating:  10 amperes at 240 V a.c.

I.  	Transfer Override Switch:  Overrides automatic retransfer control so the ATS will remain connected to the emergency power source regardless of the condition of the normal source.  A pilot light indicates the override status.

J. 	Engine Starting Contacts:  One isolated normally closed and 1 isolated normally open.  Contacts are gold flashed or gold plated and rated 10 amperes at 32 V d.c. minimum.

K.  	Engine Shut-Down Contacts:  Instantaneous, to initiate shut-down sequence at remote engine-generator controls after retransfer of the load to normal or preferred source.

L.  	Engine Shut-Down Contacts:  Time delay adjustable from 0 to 5 minutes; factory set at 5 minutes.

M.  	Engine-Generator Exerciser:  Solid-state programmable time switch starts engine-generator set and transfers load to it from normal source for a preset time, then retransfers and shuts down engine after a preset cool-down period.  Initiate exercise cycle at preset intervals adjustable from 7 to 30 days.  Running periods are adjustable from 10 to 30 minutes.  Factory-set periods are for 7 days and 20 minutes, respectively.  Exerciser features include:

1.  	Exerciser transfer selector switch, which permits selection between exercise with and without load transfer.

2.  	Push button programming controls with digital display of settings.

3.  	Integral battery operation of time switch when normal control power is not available.

2.05 BYPASS/ISOLATION SWITCH (BP/IS)

A.  	Comply with requirements for Level 1 equipment per NFPA 110, Standard for Emergency and Standby Power Systems.

B.  	Description:  Manual type, arranged to select and connect either source of power directly to the load, isolating the transfer switch from the load and from both power sources.  Include the following features:

1.  	Means to lock the BP/IS in the position that isolates the transfer switch, with an arrangement that permits complete electrical testing of the transfer switch while isolated.  While isolated, interlocks prevent transfer switch operation except for testing or maintenance.

2.  	Draw-Out Arrangement for the Transfer Switch:  Provides physical separation from live parts for testing and maintenance operations.

3.  	Current, Voltage, Closing, and Short-Circuit Withstand Ratings:  Equal to or greater than that of the associated ATS, with the same phase arrangement and number of poles.

4.  	Contact temperatures of BP/IS do not exceed those of ATS contacts when they are carrying rated load.

5.  	Operability:  Constructed so that load bypass and transfer switch isolation can be performed by 1 person in no more than 2 operations in 15 seconds or less.

6.  	Legend:  Manufacturer's standard legend for control labels and instruction signs give detailed operating instructions.

7.  	Maintainability:  Fabricate BP/IS to allow convenient removal of major components from the front without removal of other parts or main power conductors.

C.  	Interconnect BP/IS and ATS with copper bus bars plated at connection points and braced for the indicated available short circuit current.

2.06 REMOTE ANNUNCIATOR PANEL

A.  	Description:  Hard-wired lamp type with audible signal and silencing switch.  Indicating lights are grouped for each transfer switch monitored.  Label each group indicating the transfer switch it monitors, the location of the switch, and the identity of the load it serves.

B.  	Mounting:  Flush, modular, steel cabinet except as indicated.

C.  	Lamp Test:  Push-to-test or "lamp test" switch on front panel.

2.07 REMOTE ANNUNCIATOR AND CONTROL PANEL

A.  	Description:  Solid-state control and indicating panel.  Group controls and indicating lights for each transfer switch together.  Label each group indicating the transfer switch it controls, the location of that switch, and the load it serves.

B.  	Digital Communications Capability:  Matched to that of transfer switches supervised.

C.  	Mounting:  Flush, modular, steel cabinet except as indicated.

2.08 FINISHES

A.  	Enclosures:  Manufacturer's standard enamel over corrosion-resistant pretreatment and primer.

2.09 SOURCE QUALITY CONTROL

A. 	Factory test components, assembled switches, and associated equipment to ensure proper operation.  Check transfer time and voltage, frequency, and time-delay settings for conformance with specified requirements.  Perform dielectric strength test conforming to NEMA ICS 1.

PART 3 - EXECUTION

3.01 INSTALLATION

A.  	Floor Mounting of Transfer Switches:  Level and anchor the unit to the floor.

B.  	Annunciator Panel Mounting:  Mount flush in wall except as indicated.

C.  	Identify components according to Division 16 Section "Electrical Identification."

3.02 WIRING TO REMOTE COMPONENTS

A.  	Match the type and number of cables and conductors to the control and communications requirements of the transfer switches used.  Increase raceway sizes at no additional cost to the owner if necessary to accommodate required wiring.

3.03 CONNECTIONS

A.  	Tighten factory-made connections, including connectors, terminals, bus joints, mountings, and grounding.  Tighten field-connected connectors and terminals, including screws and bolts, according to equipment manufacturer's published torque tightening values.  When manufacturer's torquing requirements are not indicated, tighten connectors and terminals to comply with tightening torques specified in UL Standards 486A and 486B.

3.04 GROUNDING

A.  	Make equipment grounding connections for transfer switch units as indicated and as required by the NEC.

3.05 FIELD QUALITY CONTROL

A.  	Manufacturer's Field Services:  Provide services of a factory-authorized service representative to supervise field tests.

B.  	Preliminary Tests:  Perform electrical tests as recommended by the manufacturer and as follows:

1.  	Measure phase-to-phase and phase-to-ground insulation resistance levels with insulation resistance tester, including external annunciator and control circuits.  Use test voltages and procedure recommended by the manufacturer.  Meet manufacturer's specified minimum resistance.

2.  	Check for electrical continuity of circuits and for short circuits.

C.  	Field Tests:  Give 7-day advance notice of the tests and perform tests in presence of owner's representative.

D.  	Coordinate tests with tests of generator plant and run them concurrently.

E.  	Tests:  As recommended by the manufacturer and as follows:

1.  	Contact Resistance Test:  Measure resistance of power contacts for ATSs, NATSs, and BP/ISs.  Resolve values in excess of 500 micro-ohms and differences between adjacent poles exceeding 50 percent.

2.  	Ground Fault Tests:  Coordinate with testing specified in Division 16 Section "Overcurrent Protective Devices" to ensure sensors are properly selected and located to optimize ground-fault protection where power is being delivered from either source.

a.  	Verify grounding points and sensor ratings and locations.

b.  	Apply simulated fault current at the sensors and observe reaction of circuit interrupting devices.

3.  	Operational Tests:  Demonstrate interlock, sequence, and operational function for each switch at least 3 times.

a.  	Simulate power failures of normal source to ATSs and of emergency source with normal source available.

b.  	Simulate low phase-to-ground voltage for each phase of normal source of ATSs.

c.  	Verify time-delay settings and pick-up and drop-out voltages.

F.  	Test Failures:  Correct deficiencies identified by tests and prepare for retest.  Verify that equipment meets the specified requirements.

G.  	Reports:  Maintain a written record of observations and tests.  Report defective materials and workmanship and retest corrected items.  Record adjustable relay settings and measured insulation and contact resistances and time delays.  Attach a label or tag to each tested component indicating satisfactory completion of tests.

3.06 DEMONSTRATION

A.  	Training:  Furnish the services of a factory-authorized service representative to instruct Owner's personnel in the operation, maintenance, and adjustment of transfer switches and related equipment.  Provide a minimum of 4 hours of instruction scheduled 7 days in advance.

END OF SECTION 16495