Project Number:  AW-0507

Contract Number:  TW-0500

Date:  2/1/94

SPECIAL SPECIFICATION

SECTION 16501

FLUORESCENT LUMINAIRES

Page

PART 1 - GENERAL

1.01	Related Documens	1

1.02	References	1

1.03	Definitions	2

1.04	System Description	3

1.05	Submittals	3

1.06	Delivery, Storage, And Handling	6

PART 2 - PRODUCTS

2.01	Luminaires	7

2.02	Ballast	10

2.03	Lamps	13

PART 3 - EXECUTION

3.01	Installation	14

3.02	Field Quality Control	15

SPECIAL SPECIFICATION

SECTION 16501

FLUORESCENT LUMINARIES

PART 1 - GENERAL

1.01	RELATED DOCUMENTS

A.	Provide materials, equipment, accessories, and workmanship as specified on drawings.  Make luminaire parts and components not specifically identified on the drawings, of materials most appropriate to their use or function, and resistant to corrosion and to thermal and mechanical stresses encountered in normal application and function of the luminaries.

B.	Provide luminaries of sizes, types, and ratings indicated; complete with, but not necessarily limited to, housings, lamps, starters and wiring.  Provide each luminaire with lamps as specified.  Specifications for luminaire components such as reflectors, lenses, lamps and ballasts shall be found elsewhere in this document.

1.02	REFERENCES

A.	Title 10, Code of Federal Regulations, Department of Energy

435	Energy Conservation Voluntary Performance Standards for New Building; Mandatory for Federal Buildings.

436	Federal Energy Management Programs.

B.	Illumination Engineering Society (IES) Lighting Handbook, 8th Edition

C.	American National Standards Institute (ANSI)

C78.1		For The Dimensional and Electrical Characteristics of Fluorescent Lamps.

C81.61	For Electrical Lamps Bases.

C81.63	For Gauges For Electrical Lamp Bases and Lampholders.

C82.1		For Ballast For Fluorescent Lamps - Specifications.

C82.2		Fluorescent Lamp Ballasts - Methods of Measurement.

1.03	DEFINITIONS

A.	Ballast Efficacy Factor (BEF):  ratio of relative light output to power input in watts, at specified test conditions, expressed as a percent.

B.	Ballast Factor (BF):  ratio of a commercial ballast lamp lumens to a reference ballast lamp lumens, used to correct lamp lumen output form rated to actual.

C.	Coefficient of Utilization (CU):  ratio of lumens form a luminaire calculated as received on the workplane to the lumens emitted by the luminaire's lamps.

D.	Color Rendering Index (CRI):  a measure of the degree of color shift objects undergo when illuminated by the light source as compared with those same objects when illuminated by a reference source of comparable color temperature.

E.	Correlated Color Temperature (CCT):  the absolute temperature of a blackbody whose chromaticity most nearly resembles that of the light source.

F.	Efficacy:  the total luminous flux emitted by a lamp divided by the total lamp power input; expressed in lumens per watt.

G.	Efficiency:  the lumens emitted by a luminaire divided by the lumens generated by the luminaire's lamps.

H.	Lamp Current Crest Factor (LCCF):  ratio of peak lamp current to the root mean square (RMS) lamp current.  Higher LCCF contribute to a reduction in lamp life.

1.04	SYSTEM DESCRIPTION

A.	Design Requirements:

1.	Contractor shall provide luminaries fabricated, wired and installed in compliance with current edition of applicable city, state and national codes.

2.	Contractor shall provide interior luminaries and electrical components listed and labeled by UL or Electrical Testing Laboratories (EL).  Lighting equipment shall comply with UL standards pertaining to interior luminaries including:  UL 1570 and UL 542.

3.	Contractor shall provide luminaries which comply with applicable requirements of the National Electrical Manufacturers Association (NEMA) LE 4 pertaining to recessed luminaries and with NFPA 70, National Electrical Code, as applicable to construction and installation of interior building luminaries.

1.05	SUBMITTALS

A.	Product Data:

1.	Luminaire information shall be submitted where directed in Specification Section 01300 and on all equipment furnished by the contractor with internal wiring and controls differing from the contract drawings or not shown on the contract drawings.

2.	Luminaires or other materials shall not be shipped, stored or installed until submitted shop drawings, samples, catalogue cuts, test data, certificated, or other accordance with submittal comments.

B.	Shop Drawings:

1.	Shop drawings, samples, test data and certificates shall be submitted for SNL approval in accordance with submittal list and drawings.  Submit samples at SNL's request catalogue cuts, complete photometric records and cost savings documentation.  Submit documentation detailing software or method used to determine all cost, and both fixture calculations and cost feasibility studies for substitutions.  In addition, the following information shall be submitted:

a.	Photometrics shall be prepared by an Independent Testing Laboratory (ITL) for the same lamp/ballast combinations as specified per drawings.  Photometric data shall be submitted with the specified lamp/ballast combination, at the time mannufacturer's cuts are submitted.  Photometric testing and reporting shall conform to IES LM - 41 procedures and include:  luminaire catalogue number, lamp type, ballast, ballast factor, input watts, and 10° increments for 0° to 180° vertical, candlepower distribution curves, lumen output data and spacing criteria.

1.	Substitutions shall be equal to or better than luminaries specified and include the same lamp lumens (avg.), color rendering, and be equal to or exceed maximum lamp life.  Substitute information shall include manufacture recommended external fuse size.

2.	Costs savings report shall include:  maintenance factor for group relamping; A/C cost savings; luminaire heat load contribution and heat cost savings; ballast replacement cost; group relamping cost; ballast factor for lamp/ballast combination, ballast efficacy factor, wattage per square foot for total area(s) where luminaire is being installed; projected payback period.  Submit ITL test data for ballast verifying compliance with specification requirement for project specific lamp/ballast combinations.

b.	Applications for specular retrofit reflectors to existing luminaries, Contractor shall submit a computer generated plot of illuminance at a work plane height of 2'-6" above finished floor, and luminance on walls and ceilings for typical spaced indicated on drawings.  Calculations shall model partial height partitions, architectural elements, furnishings, or obstructions above 2'-6".  Include documentation identifying computer program used and input forms listings assumptions for room reflectance, initial lamp lumens, ballast factor, luminaries dirt depreciation, lamp lumen depreciation and room surface dirt depreciation.  Photometric data shall be generated from existing luminaire with proposed reflector and tested by ITL.

c.	Shop drawings shall indicate materials, finishes, metal gauges, overall and detail dimensions, sizes, electrical and mechanical connections, fasteners, welds, joints, end conditions, and provisions for the work of others.  Indicate complete details of luminaire including manufacturers catalogue numbers for sockets, ballasts, lightshields, switches and type of wiring, and targeting and locking devices for adjustable luminaries.  Indicate type and extent of junctions of dissimilar metals.  Standard catalogue cuts shall be supplemented by additional drawings if information or descriptions listed above are not included in the cuts.

d.	Contractor shall submit catalogue cuts of lamps and ballasts to be provided for each type luminaire.

C.	Samples:

1.	Contractor shall submit 2 samples.  Supply a completely operable luminaire with lamp(s), and a six foot long cord and plug for standard 120 volt service.  For 277 volt luminaries, contractor shall provide 277/120 volt transformers if required by SNL.

2.	Contractor shall tag samples with project name and number, equipment number, and luminaire type.  Contractor shall deliver samples to SNL representative for review.  SDR  shall notify Contractor to transport sample to work site after review has been completed.  Transportation costs shall be Contractors responsibility.  Contractor shall make luminaries identical with approved samples.

1.06	DELIVERY, STORAGE, AND HANDLING

A.	Luminaries shall comply as follows:

1.	Luminaries shall be provided with fluorescent lamps in quantity, type and wattage, and compatible with ballast, as specified.

2.	Exposed finishes shall be protected during manufacture, transport, storage, and handling.  Delivered materials shall be identical to approved samples.  Damaged materials shall be repaired and/or replaced as directed by SDR.

B.	Acceptable at Site:

1.	SDR has the right to refuse acceptance of damaged luminaries, their accessories, and materials not approved by SNL submittal process.  Costs for removing refused materials and supplying required equipment will be at Contractor's expense.

C.	Storage and Protection:

1.	Luminaries shall be stored under cover, above ground, in clean, dry areas, and shall be labeled as to type of fixture, project number, and location to be installed.

2.	Contractor shall be responsible for all costs for transportation of fixtures, labor, vehicle, packing materials and pallets.

PART 2 - PRODUCTS

2.01	 LUMINARIES

A.	Luminaries shall comply as follows:

1.	Luminaries shall be provided with fluorescent lamps in quantity, type and wattage, and compatible with ballasts, as specified.

2.	Contractor shall verify whether luminaries require air return capability or are to be static.

3.	When specified, fluorescent luminaries shall have electromagnetic interference filters.  Filters shall either be integral or external to the ballast, but must be integral to luminaire assemble.  Provide one filter per ballast that suppressed electromagnetic interference as required by MIL-STD-461, "Electromagnetic Emissions and Susceptibility Requirements for the Control of Electromagnetic Interference."

4.	Luminaries shall meet applicable UL 1570 requirements.  The appropriate UL label or listing, or ETL Testing Laboratory label or listing, will be acceptable as evidence of compliance with UL 1570.  Luminaries shall also comply with applicable National Electrical Code provisions, with energy efficiency requirements mandated by 10 CFR 435 and 436, including requirements mandated in the National Energy Policy Act of 1992.

5.	Luminaries shall be fully assembled when shipped from the factory.

6.	Plainly mark all luminaries for operation of specified lamps and ballasts and according to proper lamp type in accordance with UL Publication 1570 entitled "Standard for Safety - Fluorescent Lighting Fixtures".  The following lamp characteristics should be noted:

a.	Lamp diameter code (T-8, T-10, T-12), with nominal lamp wattage.

b.	Start type (rapid start, instant start),

c.	Correlated color temperature (CCT) and color rendering index (CRI).

7.	Unless otherwise noted, use only completely concealed hardware.  Latching on luminaire door frames shall be unobtrusive.  Make luminaire free from light leaks by the inherent design of the body and frame.  Bond gaskets, when used, to the luminaire metal.  Use bottom relamping unless otherwise noted.

8.	Luminaire wiring:

a.	Provide wiring between fluorescent lampholders and associated operating and starting equipment in compliance with UL 1570 and NEC.

9.	Lampholders:

a.	Provide fluorescent luminaire lampholders that are white, constructed of heat resistant plastic.  Lampholders shall comply with UL 542 and ANSI C81.

b.	Provide lampholders suitable for specified lamps, and position lamps in optically correct spacing and relationship to lenses, reflectors, filters, and baffles.

10.	Finishes:

a.	Provide reflective surfaces with a white baked enamel finish with a minimum reflectance of 86%.  Prior to painting, give all parts proper etched surface preparation to assure paint adherence and durability.

11.	Lenses/Louvers/Trim:

a.	All lenses and louvers shall be held positively within door frames so hinging or motion of frame will not cause diffusing element to drop out.  Trim shall be drawn to ceiling as tight as necessary, insuring complete contact of trim with ceiling surrounding luminaire.

b.	Unless otherwise specified, prismatic lenses shall be made of clear virgin acrylic of nominal 0.125" overall thickness for nominal 2' x 4' pieces; lens shall be composed of 3/16" square female prismatic cones with non-convex prism faces of maximum 0/080" depth and aligned to 45° to length and width of lens panel; lens shall be a minimum of 7.5 oz. per square foot; shall be strain-free and uniform in appearance; shall have minimum 80% visible transmittance.

12.	Reflectors:

a.	Aluminum reflectors and shielding media shall have a minimum thickness in accordance with current UL standard 1570 for ballast covers.

Reflectors shall be absolutely free of tooling marks, spinning lines, and indentation marks caused by riveting or other assemble techniques.  No rivets, springs or other hardware shall be visible after installation.

b.	Reflectors shall be free from blemishes, scratches, or indentations which would distort their reflective function.

c.	Any aluminum reflector, cone, or baffle, utilized in whole or in part within bottom two inches of luminaries, shall have low iridescent coating to reduce rainbow effect from tri-phosphor lamps.

d.	Specular silver reflectors shall be comprised of unitized single piece construction for permanent mounting inside luminaire.  A multi-piece reflector assemble shall only be considered if parts maintain fixed and accurate positioning in relation to lamps and housing, installation costs are not increased, and ballast access and luminaire maintenance is not compromised.  Use a minimum reflector thickness of 0.020 inch consisting of silver film laminated on aluminum or steel substrate or high performance aluminum finish or multiple thin film coating.  Material shall retain a minimum 93% specular reflectivity, 96% image clarity, and 95% total reflectivity for a minimum of 5 years, when cleaned as directed.

2.02	BALLAST

A.	Ballast for fluorescent fixtures shall be "UL listed", comply with Safety Standard UL 935, "CBM" labeled, and certified to meet ANSI 82.1.

B.	Ballast shall be rated as "high power factor" and shall be "Class P" with thermostatic (automatic resetting) type internal protection.

C.	Ballasts for fluorescent luminaries shall be sound rated by the manufacturer and shall have a rating of "A" (20-24 lb).

D.	Ballast rated for low temperature starting (starting at temperatures around -20°) shall be provided in fixtures mounted in cold rooms, unheated buildings, outdoors, or as indicated on drawings.

E.	Ballast mounted in fixed or permanently installed fluorescent fixtures shall be provided with an externally removable fuse holder and fuse in the input power line.

1.	The fuse holder shall ba a BUSS type HLR, installed in the ballast compartment, such that the conductors are not exposed in lamp compartment or externally.

2.	Fuses shall be glass tube, dual element, time-delay type (Bussman "Fusetron" type GMF or equal).

3.	Fuseholder shall mounted so that it can be removed either from outside fixture enclosure at fixture end or from inside the lamp compartment, without opening ballast compartment.

4.	Fuse size shall be specified on equipment list or drawings.  In case of substitution, external fuse size shall be included with manufacturer data.

F.	Ballast shall be marked showing compatibility with Energy Saving Lamps.

G.	Ballast shall meet minimum efficiency and efficacy factors as specified in Appendix A.

H.	Ballasts shall not contain polychlorinated biphenyl (PCBs).

I.	Total Line Current Harmonic Distortion shall not exceed 20%.

J.	Energy Savings Ballast shall also comply to the following:

1.	Energy savings ballasts designed for F40/T-12/RS lamps shall be compatible for use with both 40 watt and 34 watt lamps.

2.	Light output BF shall be no less than 0.95 (+.025) when tested with 40 watt lamps and no less than 0.875 (+.025) when tested with 34 watt lamps.

3.	Ballasts shall have an electronic component which cuts off power to lamp filaments of a rapid star lamp(s), once lamp(s) have started.

4.	Cathode voltage for rapid start lamps during starting shall be between 3.4 and 4.5v across a dummy load and between, 2.5 and 4.0v during operation as per ANSI C82.

5.	LCCF shall not exceed 1.7 when tested with 40 watt T-12 lamps, nor exceed 1.9 for 34 watt lamps, as per ANSI C82.1.

6.	Dimming ballasts shall only be used on a dimming circuit designed expressly for cathode cut-out type ballasts and shall not reduce lamp life.

K.	Electronic ballast shall also comply with the following:

1.	Ballast shall be specifically designed for the operation of T-8 lamps.

2.	Light output (BF) shall be between .85 and 1.0 when tested with a compatible full-wattage lamp (40W T-12 or 32W T-8).

3.	Ballast shall be regulated to maintain light output which does not vary more than + 5% for all 4-foot rapid start fluorescent lamps in the proper lamp/ballast combination within operating ranges of + 10% of center voltage.  (E.g.:  120V or 277V).

4.	Cathode voltage for rapid start lamps during starting shall be between 3.4 and 4.5V during operation per ANSI C82.1.

5.	Ballast shall have a frequency of operation of 20 kHz or greater and incorporate adequate 50 Hz filtering in order to operate with less than 5% flicker (maximum 0.20 Flicker Index) with any triphosor lamp suitable for use with ballast.

6.	LCCF shall not exceed 1.7 when tested with 40W T-12 or T-8 lamps.

7.	Electronic ballast THD shall not exceed 15%.

L.	Dimmable Electronic Ballast shall also comply with:

1.	Ballast shall be high frequency, solid state type for adjustable light output control of fluorescent lamps.

2.	Ballast shall dim continuously from 100% to at least 20% of full light output without strobe effect or lamp flicker.

3.	BF shall not be less than .89 (+, 025) at 100% output and not less than 0.15 when dimmed to 20% power (tested with 40W T-12 lamp).

4.	THD shall not exceed 20% throughout the dimming range.

5.	LCCF shall not exceed 1.7 throughout the dimming range.

6.	Ballast shall maintain full lamp filament heat during dimming or normal operation of lamps and capable of operating lamps at full output if dimming components fail.

2.03	LAMPS

A.	Lamps provided shall conform to ANSI C78.1.

B.	New lamps shall be provided for each fluorescent fixture installed.  Lamps shall be free or dirt fingerprints; therefore, wiped when installed.

C.	Unless otherwise specified, lamp phosphors shall be a composition which includes tri-stimulus or modified tri-stimulus rare earth phosphors, with a CCT of 3500 Kelvin and a CRI of not less than 69.

D.	Mortality curves shall show that less than 10% of lamps are burned out at 70% or rated life.

PART 3 - EXECUTION

3.01	INSTALLATION

A.	Install luminaires complete with lamps, parts, attachments, devices, hardware, hangers, cables, supports, channels, frames, brackets, and internal and external wiring as specified by drawings.

B.	Coordinate installation of luminaires with other trades to insure installations do not interfere with other work.

C.	Install luminaires plumb, square, and level with ceiling and walls, and in alignment with adjacent lighting fixtures.  Unless otherwise specified, recessed luminaires flush mounting in ceiling grid shall be secured in place using "Caddy Acoustical Tee Bar Clip" (Cat No. 515, or similar).

D.	Install luminaires, complete with lamps, with protective wrapping (plastic protective cover on parabolic insert or acrylic lens) in place.

E.	Ground non-current carrying parts of electrical equipment in accordance with UL and NEC provisions.

F.	Conduit shall not fasten to Tee Bar support hangers, but be supported by building steel, unistrut, or some channel installed for the specific reason to support conduit.

3.02	FIELD QUALITY CONTROL

A.	Upon completion of installation of lighting fixtures, and after circuits have been energized, apply power and demonstrate capability and compliance with requirements.  Correct or remove and replace malfunctioning units, then re-test to demonstrate compliance.  Coordinate field tests with SDR.

1.	Lamps shall be fully operable, no burnt-out lamps.  Burnout lamps shall be replaced.

2.	Remove any protective covering form luminaires.  Clean all dirt, fingerprints and debris from lens, parabolic insert, lamps and lamp compartment.

END OF SECTION

APPENDIX A

A1.01	TABLES

A.	National Energy Conservation Standard for Fluorescent Lamp Ballast Table:

Ballast		Total Nominal	Ballast

Application		Input Voltage	Lamp Watts		Efficacy Factor

(1) F40T12 Lamp	     120V		     40		    1.805

(1) F40T12 Lamp	     277V		     40		    1.805

(2) F40T12 Lamps	     120V		     80		    1.060

(2) F40T12 Lamps	     277V		     80		    1.050

(2) F96T12 Lamps	     120V		    150		    0.570

(2) F96T12 Lamps	     277V		    150		    0.570

(2) F96T12/HO Lamps   120V		    220		    0.390

(2) F96T12/HO Lamps   277V		    220		    0.390

B.	Exceptions:

1.	Dimming ballasts, ballasts designed to operate at 0° or less are exempted from these standards.

C.	Ballast Factor (BF):

1.	BF must meet or exceed the following:

a.	40 Watt or slimline must be 92.5% or greater.

b.	High Output lamps must be 95% or greater.

2.	BF must be determined by laboratory testing, not by calculations.

D.	Minimum Efficiency Standards Table:

Lamp			Nominal		Minimum		Avg. Lamp

Type			Lamp Wattage	CRI			Efficacy (LPW)*

F40			  >35W		  69			     75

F40			  <35W		  45			     75

F40/U		  >35W		  69			     68

F40/U		  <35W		  45			     64

F96T12		  >65W		  69			     80

F96T12		  <65W		  45			     80

F96T12		  >100W		  69			     80

F96T12		  <100W		  45			     80

* Lumen per Watt Efficacy

E.	Fluorescent lamps impacted by minimum efficiencies standards are:

1.	F40 bi-pin rapid-start straight lamps and U-shaped rated at 28 watts or more.

2.	F96/HO, high output lamps, 96 inches in length, rapid start, 800 ma. types.

3.	F96, slimline 96 inches in length, instant start, single pin of 52 watts or more.