4/14/03

WESTERN AREA POWER ADMINISTRATION –SF6 ANNUAL REPORT FOR YEAR 2002

Introduction and Background

In 2000, the EPA invited Western to join a new voluntary partnership aimed at reducing SF6 emissions from the electric power industry.  The partnership is an opportunity for the electric power industry to work toward protection of the environment in a non-regulatory situation, where the participants use mainly their own flexibility and methods to ensure reduction of SF6 releases.  The partnership is formalized between EPA and each participating utility through a Memorandum of Understanding (MOU) entitled “SF6 Emissions Reduction Partnership for Electric Power Systems”.

Western had to decide to sign or not sign the MOU.  Because SF6 is a potent greenhouse gas and a serious threat to the global environment, Western and the utility industry must take the issue of SF6 reduction seriously.  If the issue of SF6 reduction is ignored, the likelihood of SF6 control and regulation is more certain.  The options available to Western were:

- Sign the MOU and begin the program prescribed by EPA to control SF6 emissions.

- Not sign the MOU, and take no action to reduce SF6 emissions.

- Not sign the MOU, but formulate an alternative SF6 emission control program.

Western chose alternative 3 and enacted a plan for reduction of SF6 emissions in 2000.  The plan focuses on providing cost-effective and reliable service for our customers while protecting the environment from greenhouse gas.  In 2000, Western focused on scanning over 200 known leakers and making repairs.  In 2001, Western focused on remaining leaking equipment of lesser priority from the previous year.  For 2002, only 7 pieces of equipment were leak-scanned using the laser-vue camera developed by the Electric Power Research Institute (EPRI).  The leaks, mostly small, were quickly detected and repaired, requiring few outages.  As was mentioned in last year’s report for 2001, Western foresaw in 2002 of having fewer pieces of equipment to scan and repair for SF6 emissions due to the effectiveness of the program.

Currently, Western is nearing completion of developing a pilot tracking system at two of its regional offices to determine the amount of SF6 released to the atmosphere.  If successful, the tracking system will be implemented throughout Western. The tracking system will record how much SF6 is purchased and added to new and existing equipment. It will also track the amount of SF6 gas in cylinders immediately after purchase and prior to return of cylinders to supplier.

Western considers SF6 leakage prevention a higher priority than developing a tracking and recording system.   Money and resources will be allocated gradually over time to develop a cost-effective tracking and recording system.

The next section gives updated specific details on Western’s SF6 Emissions Reduction Program.

## Western’s SF6 Emissions Reduction Program 2002 update

Western has enacted an emissions reduction program that includes planning, setting baselines, tracking, and reporting in a cost-effective manner.  The plan emphasizes immediate reduction of SF6 emissions.  Key items in this plan are:

- Goal: Developing a Western-wide SF6 Emissions Reduction Policy.  Achievement: All Western regional offices have committed to participating in having equipment scanned and repaired.

- Goal: Designing a basic SF6 gas use and emissions tracking procedure.  Achievement:  Currently nearing completion in RMR (Rocky Mountain Region) and some of UGPR (Upper Great Plains Region) divisions.  Figures for emissions are included with this report.

- Goal: Incorporating SF6 emissions reduction training, programs, and policies for proper handling into other routine training, such as at annual employee meeting/training sessions, tailgate meetings. Achievement: All regions are currently training maintenance employees on the importance of reducing SF6 emissions based on procedures written in Western’s Power System Maintenance Manual – Chapter 4.

- Goal: Using leakage detection equipment such as the EPRI laser-vue camera to locate leakage.  Achievement: Nearly 200 scans have been performed since 2000, with over 100 in 2000, nearly 90 in 2001 and less than 10 in 2002.  Many more are planned for 2003.

- Goal: Characterizing SF6 filled equipment by age, leakage history, and “reputation”. Achievement: In 2001, focus was on scan and repair of leaking equipment. In 2002, focus was on scan and repair of remaining less leaking equipment.  In 2003, more equipment will be scanned and characterized.  Another contractor (EIS) will perform scans in 2003.

- Goal: Seal equipment on a priority basis from the characterization information.  Achievement: In 2001, leaking equipment was repaired including some minor leaking equipment.  In 2002, remaining leaking equipment was repaired.

- Goal: Prepare an annual report on estimated SF6 use.  Achievement:  Annual report prepared for 2001, but did not include estimated SF6 usage.  The annual report for 2002 includes estimated figures for SF6 emissions.  Two regions have submitted data for this report.

- Goal: Prepare an annual report on maintenance activities conducted to reduce emissions. Achievement: Annual report prepared for 2002 includes maintenance activities performed to reduce SF6 emissions.

- Goal: Submit an informal report to EPA annually.  Achievement: Annual report is being submitted to EPA for 2002.

## Analysis

Western’s program has quickly begun to reduce SF6 emissions and demonstrated a commitment to the EPA effort at minimal cost to our customers.  Information will be submitted annually to EPA and other interested parties.  A solid baseline and the ongoing status of actual SF6 emissions will be available in more detail in subsequent years.  Western’s program offers the immediate benefits of:

- Immediate reduction in SF6 gas released to the environment.

- Improvement in operation of SF6-filled equipment

- Improved scheduling for replacement of SF6-filled equipment

- Reduction of possible equipment failures

- Adherence to Western’s guidelines provided in chapter 4 of PSMM to enhance maintenance of SF6 filled equipment, improve handling of SF6 gas and address the mitigation of SF6 gas health hazards

- Reduction in SF6-gas costs

- Improvement in power system reliability (SF6 filled breakers can be scanned for SF6 leakage while in-service)

- Commitment to efforts in complying with EPA’s current Voluntary SF6 regulations

- Preparation for complying with EPA’s possible future mandatory SF6 regulations

- Addressing emission issues in a time frame built around Western’s budget and adaptability

- Responsiveness to health, safety and environmental issues while being prudent in the use of funds and staffing.

2002 update on additional facts and information

Nameplate capacity of SF6: Western has approximately 750 pieces of SF6 filled equipment averaging approximately 300 pounds per piece of equipment.  The total amount of SF6 is approximately 225,000 pounds.  To date, an exact figure has not been obtained.  A computer based tracking program for maintenance activities in Western does not have all of the SF6 filled equipment entered into the database.  Over the next few years Western hopes to have this accomplished.  This will provide a more accurate figure for emission leakage rate from SF6 gas filled equipment.

Inventory based emissions of SF6: Some of the regions within Western have completed or are nearing completion of developing an inventory system to track procurement of SF6, track how much is added to existing and new equipment, and returns, etc, as well as leakage rates.  The system follows closely the tracking protocol in EPA’s MOU.

Western’s policy for proper handling of SF6: Western regularly trains its maintenance employees on proper handling of SF6 gas.  This training is part of our apprenticeship program and Foreman training programs as well as our periodic environmental training and updates.

Handling procedures for SF6: Western’s maintenance personnel have developed specific handling procedures for SF6; these include adding gas to breakers, recycling gas, filtering gas, etc.  These are detailed in chapter 4 of our Power System Maintenance Manual.  In addition, Western has been an active participant in helping EPRI develop their manual on Proper maintenance and handling procedures for SF6 gas.

Summary of Western Area Power’s accomplishments in SF6 emission reduction for 2002:

- Leak testing accomplished:

Desert Southwest Regional Office (DSWR): No equipment scans performed in 2002.

Rocky Mountain Regional Office (RMR): No equipment scans performed in 2002.

Sierra Nevada Regional Office (SNR): No equipment scans performed in 2002.

Upper Great Plains Regional office (UGPR): 7 pieces of equipment were scanned in UGPR region by EPRI (Electric Power Research Institute) at Tyndall, Flandreau and Watertown substations in the South Dakota Maintenance Division (SDMD). The EPRI report for scans of those pieces of equipment has been included with this report.

II: 	Leak repairs accomplished:

DSWR: 345Kv circuit breaker (# 194) leaking at Flagstaff; performed manufacturer rebuild, which greatly reduced leakage but did not eliminate leakage entirely.

RMR: No repairs were needed.

SNR: No repairs were needed.

UGPR: Repaired leaks at Tyndall, Watertown, and Summit Substations in the SDMD. The breakers at Watertown which were repaired are old and are scheduled for replacement in the near future.

III:	Tracking System development

:

DSWR: Nothing to report.

RMR: The SF6 work group has been having informal telephone conversations on simplifying year-end activities and tracking methods.  We believe the annual summary can be completed by reviewing maintenance records for the year and reporting actual SF6 gas usage.  This will substantially reduce costs by eliminating the need to go out and weigh each bottle of SF6 in the inventory.   Property has made substantial progress in identifying which cylinders belong to Western and returning those which do not belong to us to the owner.  CSO Construction Engineering revised contract language to clarify that unused gas and cylinders left over after equipment installation will be returned to the supplier.  This will ensure that RMR adds only the SF6 contained in the equipment to our inventory, making it easier track gas usage.  Work is continuing on refining this process.  More accurate data will be available in future years.

SNR: Nothing to report.

UGPR:  Last year, Western’s Upper Great Plains North Dakota Maintenance Division (NDMD) began developed a tracking system and uses excel spreadsheet to enter beginning and end of year inventories.  This year, figures for SF6 emissions have been determined for Upper Great Plains North Dakota Maintenance Division (NDMD) and Upper Great Plains Montana Maintenance Division (MMD).  However, total nameplate capacity of SF6 for all equipment in these divisions is not yet available.  Based on estimated nameplate capacity, an emission rate has been determined for NDMD.  SDMD has nothing to report.

IV:	SF6 emission figures:

DSWR: Nothing to report.

RMR:  Based on data received from maintenance records, the 2002 emission rate for SF6 filled equipment is 3.2 %.  Next year, with more development of the tracking system, the figure will be more accurate.

SNR:  Nothing to report.

UGPR: Based on inventory and estimated nameplate capacity, the 2002 emission rate for NDMD was 1.6 %.  The MMD had no emission rate to report; estimated nameplate capacity has not yet been determined.  Next year, with a more accurate nameplate capacity, the figure will be more accurate.  The SDMD has nothing to report.

V.	EPRI’s work in helping Western reduce SF6 emissions.

A major part of Western’s successful program is immediately detecting and reducing SF6 emissions to the environment.  This has been accomplished with EPRI laser-vue camera scanning of Western’s SF6 filled equipment.  The camera operators have proven to be thorough and skilled in detecting large leaks in obvious places such as rupture discs and small pinhole leaks in less obvious places such as fittings and tubing in control cabinets.  As seen in the following photos, the camera operators have done outstanding precise work.  Having a highly skilled camera operator is absolutely essential to the success of emission reduction of SF6 gas. Attached are reports of SF6 leakage detection activities at Western facilities in 2002.

SF6 Leak Inspection Results for Western Area Power Administration Company

Summary Report, May 2002

EPRIsolutions Inspector Mark Messana

Co-sponsor
Western Area Power Administration Company

DISCLAIMER OF WARRANTIES AND LIMITATION OF LIABILITIES

THIS REPORT WAS PREPARED BY THE ORGANIZATION(S) NAMED BELOW AS AN ACCOUNT OF WORK SPONSORED OR COSPONSORED BY EPRISOLUTIONS, INC. NEITHER EPRISOLUTIONS, THE ELECTRIC POWER RESEARCH INSTITUTE, INC. (EPRI), ANY MEMBER OF EPRI, ANY COSPONSOR, THE ORGANIZATION(S) NAMED BELOW, NOR ANY PERSON ACTING ON BEHALF OF ANY OF THEM:

(A) MAKES ANY WARRANTY OR REPRESENTATION WHATSOEVER, EXPRESS OR IMPLIED, (I) WITH RESPECT TO THE USE OF ANY INFORMATION, APPARATUS, METHOD, PROCESS, OR SIMILAR ITEM DISCLOSED IN THIS REPORT, INCLUDING MERCHANTABILITY AND FITNESS FOR A PARTICULAR PURPOSE, OR (II) THAT SUCH USE DOES NOT INFRINGE ON OR INTERFERE WITH PRIVATELY OWNED RIGHTS, INCLUDING ANY PARTY’S INTELLECTUAL PROPERTY, OR (III) THAT THIS REPORT IS SUITABLE TO ANY PARTICULAR USER’S CIRCUMSTANCE; OR

(B) ASSUMES RESPONSIBILITY FOR ANY DAMAGES OR OTHER LIABILITY WHATSOEVER (INCLUDING ANY CONSEQUENTIAL DAMAGES, EVEN IF EPRISOLUTIONS OR ANY EPRISOLUTIONS REPRESENTATIVE HAS BEEN ADVISED OF THE POSSIBILITY OF SUCH DAMAGES) RESULTING FROM YOUR SELECTION OR USE OF THIS REPORT OR ANY INFORMATION, APPARATUS, METHOD, PROCESS, OR SIMILAR ITEM DISCLOSED IN THIS REPORT.

ORGANIZATION(S) THAT PREPARED THIS REPORT

EPRIsolutions

Citations

This report was prepared by

Mark Messana

Senior Technical Specialist

EPRIsolutions

115 East New Lenox Rd.

Lenox MA 01240

Tel: 413 499 5056

Fax: 413 499 5718

E-mail: mmessana@epri.com

Principal Investigator

Mark Messana
Senior Technical Specialist
EPRIsolutions

The report is a corporate document that should be cited in the literature in the following manner:

SF6 Inspection for Western Area Power Administration Company

personnel

EPRIsolutions Inspector:

Mark Messana

Senior Technical Specialist

EPRIsolutions

115 East New Lenox Rd.

Lenox MA 01240

Tel: 413 499 5056

Fax: 413 499 5718

E-mail: mmessana@epri.com

Western Area Power Administration:

Bill Timmons

Electrical Engineer

Corporate Service Office

12155 W. Alameda Pkwy.

P.O. Box 281213

Lakewood, CO.

E-mail: timmons@wapa.gov

Contents

1 introduction	1

2 background	1

3 inspections	3

Watertown Substation Inspection results	4

Summit Substation Inspection results	5

Tyndall Substation Inspection results	3.4

List of Figures

Figure 2-1 Video capture of SF6 image DILO DN 8	1

Figure 2-2 Video capture of SF6 image DILO DN 8	1

Figure 2-3 A calibrated 1-kg/yr. SF6 leak (left) and as viewed through the TG – 20 Gas Imaging System (right) at 1 m with no zoom.  The yellow circle surrounds a dark cloud of gas emanating from the nozzle.	2

# introduction

On May 6, 2002, Mark Messana of EPRIsolutions performed sulfur hexafluoride (SF6) inspections on various equipment at the following substations in South Dakota.

- Watertown Substation:

- Summit Substation:

- Tyndall Substation:

The inspections, which were performed using EPRI’s TG – 20 Gas Imaging System, identified 2 SF6 leaks, which are detailed in this report.

# background

The TG – 20 Gas Imaging System makes it possible to “see” SF6 leaks, which look like smoke emanating from the equipment (see examples below).  Note the black cloud around the DILO ND8 high-pressure tube union.  The cloud moves with the air currents, which makes it easier to identify against a motionless background.  Also note how the cloud has moved from one image to the other.

| Figure 0-1 Video capture of SF6 image DILO DN 8 | Figure 0-2 Video capture of SF6 image DILO DN 8 |
| --- | --- |

The magnitude of a leak can be difficult to judge.  For instance, the photo below shows a 1-kg/yr. leak viewed from a distance of 1 m.  The leak, which was on the bottom end of what the camera can detect, would be classified as minor.  The test was done indoors with only a small amount of air movement.  In addition, the background was a aluminum surface painted with flat paint, and the zoom was turned off.  The leak was identifiable out to 7 m; much beyond that and it is unlikely that the leak would have been detectable under these conditions.

Figure 0-3 A calibrated 1-kg/yr. SF6 leak (left) and as viewed through the TG – 20 Gas Imaging System (right) at 1 m with no zoom. The yellow circle surrounds a dark cloud of gas emanating from the nozzle.

The laser emitted by the TG – 20 Gas Imaging System also produces a “photo-acoustic” effect – a buzzing sound – as it hits the SF6 gas.  This further helps to identify leaks.  Many of the leaks identified in this report were also checked with snoop (a soap and water mixture) and/or an audible leak detector.

SF6 is widely used in the electric power industry as an insulator for high-voltage circuit breakers, switchgear, and other substation equipment.  Although pure SF6 is chemically inert, it is a potent greenhouse gas, with a per-molecule global warming potential far exceeding that of carbon dioxide.  As such, detecting SF6 leaks gas has become more important as environmental regulators forge ahead with programs aimed at curbing emissions of SF6 and other greenhouse gases.  SF6 leakage isn’t just an environmental concern, it’s also an economic one – the gas is expensive and its replacement cost is high, which makes leak detection a high priority.

The traditional method of detecting SF6 leaks involves applying a soap solution that bubbles at the site of escaping gas.  This approach is both time-consuming and costly, especially because it requires de-energizing equipment during inspection.  The soap solution often temporarily blocks the leak, and hence the leak goes undetected.  To meet the industry’s need for improved SF6 detection, EPRI participated in the development of the GasVue laser camera, which can locate even pinhole leaks quickly and precisely – without having to de-energize equipment.

# inspections

The inspection of equipment at was done on May 6 thru May 9, 2002.  A description and photos of the findings follow.

Watertown Substation Inspection Results

| Breaker #WT1762 Watertown No.2 Line | Leak was located on the bottom side of the CT housing. Under the Aluminum shield. |
| --- | --- |
| Watertown Substation | Leak 1, Major leak |
| Mitsubishi 115kV Breaker SN-960950101 | Tape Time: 16:15:32 to 16:16:38 |

Watertown Substation Inspection results

| Breaker #7296, Groton-White Tie Line | Leak is located at value #1, under the orange nut. Found packing nut leaking. Note: Tighten packing nut and the leak was repaired. |
| --- | --- |
| Watertown Substation | Leak 2, Major leak |
| Westinghouse 345kV Breaker SN-1-62Y5306 | Tape Time: 8:31:04 to 8:32:16 |

Watertown Substation Inspection results

| Breaker #7296, Groton-White Tie Line | Leak was found inside of cabinet at the SF6 compressor. The location of the leak was at the compressor shaft seal. |
| --- | --- |
| Watertown Substation | Leak 3, Major leak |
| Westinghouse 345kV Breaker SN-1-62Y5306 | Tape Time: 8:45:57 to 8:47:09 |

Watertown Substation Inspection Results

| Breaker #7292, White Line | Leak was found inside of the cabinet at the top of the dryer! This was at the plumping connection coming from the SF6 compressor. |
| --- | --- |
| Watertown Substation | Leak 4, Miner Leak |
| Westinghouse 345kV Breaker SN-2-62Y5306 | Tape Time: 9:13:45 to 9:14:48 |

Summit Substation Inspection Results

| Breaker #1152, Center Phase | Leak is located on the outer housing of breaker. Found the casting leaking SF6 gas. |
| --- | --- |
| Summit Substation | Leak 4, Miner Leak |
| Westinghouse 69kV Breaker SN-1-67Y1639 | Tape Time: 10:55:25 to 10:56:27 |

Summit Substation Inspection Results

| Breaker #1252, Center Phase | Leak was located on the outside Tee connection! This is at a weld joint on the Tee to pipe connection. |
| --- | --- |
| Summit Substation | Leak 5, Major Leak |
| Westinghouse 69kV Breaker SN-2-67Y1686 | Tape Time: 11:14:30 to 11:15:30 |

Tyndall Substation Inspection Results

| Breaker #162 | Leak was located under the center phase at the Tee location on the plumping. This is the eastside of the Tee. |
| --- | --- |
| Tyndall Substation | Leak 6, Major Leak |
| Siemens 115kV Breaker | Tape Time: 08:04:10 to 08:05:10 |