SPECIAL SPECIFICATION

SECTION 05501

METAL FABRICATIONS

Page

PART 1 - GENERAL

1.01	Description of Work .............................................................................	3

1.02	References ........................................................................................	3

1.03	Definitions .......................................................................................	7

1.04	Submittals ........................................................................................	7

1.05	Quality Assurance ...............................................................................	7

1.06	Delivery, Storage, and Handling ..............................................................	8

1.07	Project Conditions ..............................................................................	8

1.08	Sequencing and Scheduling ....................................................................	9

1.09	System Performances Requirements ..........................................................	9

PART 2 - PRODUCTS

2.01	Ferrous Metals ..................................................................................	10

2.02	Stainless Steel ...................................................................................	11

2.03	Aluminum .......................................................................................	12

2.04	Grout .............................................................................................	12

2.05	Fasteners .........................................................................................	12

2.06	Paint ..............................................................................................	13

2.07	Concrete Fill .....................................................................................	13

2.08	Fabrication, General ............................................................................	14

2.09	Steel Ladders ....................................................................................	15

2.10	Metal Bar Gratings ..............................................................................	16

2.11	Steel Pipe Guardrails and Handrails ..........................................................	17

2.12	Cast Nosings ....................................................................................	19

2.13	Steel Framed Stairs .............................................................................	19

2.14	Finishes ..........................................................................................	20

2.15	Steel and Iron Finishes .........................................................................	21

2.16	Aluminum Finish ...............................................................................	21

PART 3 - EXECUTION

3.01	Examination .....................................................................................	22

3.02	Preparation ......................................................................................	22

3.03	Installation, General ............................................................................	22

3.04	Installation of Metal Bar Gratings ............................................................	23

3.05	Installation of Steel Pipe Guardrails and Handrails .........................................	24

3.06	Installation of Cast Nosings ...................................................................	25

3.07	Adjusting and Cleaning ........................................................................	25

SPECIAL SPECIFICATION

SECTION 05501

METAL FABRICATIONS

PART 1 - GENERAL

1.01	DESCRIPTION OF WORK

A.	This section includes the following metal fabrications:

1.	Ladders.

2.	Metal bar gratings.

3.	Steel pipe guardrails and handrails

4.	Cast nosings

5.	Metal stairs.

B.	Related Sections:  Refer to Division 5, Section "Structural Steel" for structural steel framing components.

1.02	REFERENCES

A.	Aluminum Association (AA)

B.	American National Standards Institute (ANSI )

A14.3	Safety Requirements for Fixed Ladders

C.	American Society of Testing and Materials (ASTM)

A27	Specification for Steel Castings, Carbon, for General Application

A36	Specification for Structural Steel

A47	Specification for Ferritic Malleable Iron Castings

A48	Specification for Gray Iron Castings

A53	Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated Welded and Seamless

A123	Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products

A153	Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware

A167	Specification for Stainless and Heat-Resisting Steel Bars and Shapes

A276	Specification for Stainless and Heat-Resisting Steel Bars and Shapes

A307	Specification for Carbon Steel Bolts and Studs, 60,000 PSI Tensile Strength

A366	Specification for Steel, Sheet, Carbon, Cold-Rolled, Commercial Quality

A446	Specification for Steel Sheet, Zinc-Coated (Galvanized) by the Hot-Dip Process, Structural (Physical) Quality

A500	Specification for Cold-Formed Welded and Seamless Carbon Steel Structural Tubing in Rounds and Shapes

A510	Specification for General Requirements for Wire Rods and Coarse Round Wire, Carbon Steel

A526	Specification for Steel Sheet, Zinc-Coated (Galvanized) by the Hot-Dip Process, Commercial Quality

A569	Specification for Steel, Carbon (0.15 Maximum, Percent), Hot-Rolled Sheet and Strip, Commercial Quality

A570	Specification for Steel, Sheet and Strip, Carbon, Hot-Rolled, Structural Quality

A780	Practice for Repair of Damaged and Uncoated Areas of Hot-Dip Galvanized Coatings

A786	Specification for Rolled Steel Floor Plates

B221	Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Shapes, and Tubes

B632	Specification for Aluminum-Alloy Rolled Tread Plate

C1107	Specification for Packaged Dry, Hydraulic-Cement Grout (Nonshrink)

E985	Specification for Permanent Metal Railing Systems and Rails for Building.

D.	American Welding Society (AWS):

D1.1	Structural Welding Code - Steel

D1.3	Structural Welding Code - Sheet Steel.

E.	Code of Federal Regulations (CFR):

Title 29 Part 1910	Labor-Occupational Safety and Health Standards

F.	Corps of Engineers (CE)

CRD C621	Specification for Nonshrink Grout

G.	Federal Specifications (FS):

FF-B-561	Bolts, Screw, Lag

FF-B-588	Bolt, Toggle, and Expansion Sleeve, Screw

FF-S-92	Screw, Machine, Slotted, Cross-Recessed or Hexagon Head

FF-S-111	Screw, Wood

FF-S-325	Shield, Expansion; Nail, Expansion; and Nail, Drive Screw (Devices, Anchoring, Masonry)

FF-W-84	Washers, Lock (Spring)

FF-W-92	Washer, Flat (Plain).

TT-P-664	Primer Coating, Alkyd, Corrosion-Inhibiting, Lead and Chromate Free, VOC-Compliant

TT-P-645	Primer, Paint, Zinc Chromate, Alkyd Type

H.	Military Standardization Documents (MIL):

P-21035	Paint, High Zinc Dust Content, Galvanizing Repair

I.	National Association of Architectural Metal Manufacturers (NAAMM)

AMP 500	Metal Finishes Manual

AMP 510	Metal Stair Manual

MBG 531	Metal Bar Grating Manual

MBG 532	Heavy Duty Metal Bar Grating Manual

Pipe Railing Manual.

J.	National Fire Protection Association (NFPA)

101	Life Safety Code

K.	Steel Structures Painting Council (SSPC)

SSPC-PA1	Paint Application Specification No. 1

SSPC Paint 12	Paint Specification No. 12 Cold Applied Asphalt Mastic (Extra Thick Film)

SSPC Paint 20	Paint Specification No. 20 Zinc-Rich Primers (Type I, "Inorganic," and Type II, "Organic")

SSPC-SP1	Surface Preparation Specification No. 1 "Solvent Cleaning"

SSPC-SP2	Surface Preparation Specification No. 2 "Hand-Tool Cleaning"

SSPC-SP3	Surface Preparation Specification No. 3  "Power Tool Cleaning"

SSPC-SP7	Surface Preparation Specification No. 7 "Brush-Off Blast Cleaning"

L.	Uniform Building Code (UBC)

M.	Uniform Federal Accessibility Standards (UFAS)

Fed. Std. 795

1.03	DEFINITIONS

A.	Refer to ASTM E985 for railing-related terms that apply to this section.

B.	Refer to the NAAMM publications listed in Article 1.02 "References" for definition of terms that apply to this section.

1.04	SUBMITTALS

A.	General:  Submit the following in accordance with Conditions of Contract and Division 1, Section "Descriptive Submittals".

B.	Product Data:  Submit product data for products used in metal fabrications, including paint products, grout and fasteners.

C.	Shop Drawings:  Submit detailed shop and erection drawings of each metal fabrication indicated.  Include plans, elevations, sections, and details of metal fabrications and their connections.  Show anchorage and accessory items.

D.	Welder certificates signed by Contractor certifying that welders comply with requirements specified in 1.05C.

E.	Qualification data for firm specified in 1.05B to demonstrate their capabilities and experience.

1.05	QUALITY ASSURANCE

A.	Codes and Standards:  Comply with provisions of the following, except as otherwise indicated.  Where conflicts occur, comply with the more stringent requirements.

1.	ANSI 14.3.

2.	AWS D1.1 and D1.3.

3.	NFPA 101.

B.	Fabricator Qualifications:  Firm experienced in successfully producing metal fabrications similar to that shown on the drawings, with sufficient production capacity to produce required units without causing delay in the work.

C.	Qualify welding processes and welding operators in accordance with AWS D1.1 and D1.3.  Certify that each welder has satisfactorily passed AWS qualification tests for welding processes involved and, if pertinent, has undergone recertification.

D.	All materials used shall be free of lead, and asbestos fibers.

E.	Use of damaged items is prohibited except by specific authorization of Sandia Delegated Representative (SDR) in writing.

1.06	DELIVERY, STORAGE, AND HANDLING

A.	Deliver materials to the job site in good condition and properly protected against damage to finished surfaces.

B.	Storage on Site:  Store materials in a location and in a manner to avoid damage.  Stacking shall be done in a way which will prevent bending.  Store metal components and materials in a clean, dry location.  Cover with waterproof paper, tarpaulin or polyethylene sheeting in a manner that will permit circulation of air inside the cover.

C.	Keep handling on-site to a minimum.  Exercise care to avoid damage to finishes of material.

1.07	PROJECT CONDITIONS

A.	Field Measurements:  Check actual locations of walls and other construction to which metal fabrications must fit, by accurate field measurements before fabrication; show recorded measurements on final shop drawings.  Coordinate fabrication schedule with construction progress to avoid delay of work.

B.	Where field measurements cannot be made without delaying the work, guarantee dimensions and proceed with fabrication of products without field measurements.  Coordinate construction to ensure that actual opening dimensions correspond to guaranteed dimensions.  Allow for trimming and fitting.

1.08	SEQUENCING AND SCHEDULING

A.	Sequence and coordinate installation of wall handrails as follows:

1.	Mount handrails only on completed walls.  Do not support handrails temporarily by any means not satisfying structural performance requirements.

2.	Mount handrails only on gypsum board assemblies reinforced with proper blocking and backing to receive anchors, and where the location of concealed anchor plates has been clearly marked for benefit of Installer.

1.09	SYSTEM PERFORMANCES REQUIREMENTS

A.	Structural Performance:  Design, engineer, fabricate, and install the following metal fabrications to withstand the folowing structural loads without exceeding the allowable design working stress of the materials involved, including anchors and connections.  Apply each load to produce the maximum stress in each respective component of each metal fabrication.

1.	Top Rail of Guardrail Systems:  Capable of withstanding the following loads applied as indicated:

a.	Concentrated load of 300 lbf. applied at any point non-concurrently, vertically downward, or horizontally.

b.	Uniform load of 100 lbf. per linear ft. applied non-concurrently, vertically downward or horizontally.

c.	Concentrated and unifrom loads above need not be assumed to act concurrently.

2.	Handrails Not Serving as Top Rails:  Capable of withstanding the following loads applied as indicated:

a.	Concentrated load of 200 lbf. applied at any point non-concurrently, vertically downward or horizontally.

b.	Uniform load of 50 lbf. per linear foot applied non-concurrently, vertically downward or horizontally.

c.	Concentrated and uniform loads above need not be assumed to act concurrently.

3.	Infill Area of Guardrail Systems:  Capable of withstanding a horizontal concentrated load of 200 lbf. applied to one sq. ft. at any point in the system including panels, intermediate rails balusters, or other elements composing the infill area.

a.	Above load need not be assumed to be acting concurrently with uniform horizontal loads on top rails of railing systems in determining stress on guard.

4.	Treads of Steel Stairs:  Capable of withstanding a uniform load of 100 lbf. per sq. ft. or a concentrated load of 300 lbf. on a area of 4 sq. inches located in the center of the tread, whichever produces the greater stress.

a.	Platforms of Steel Stairs:  Capable of withstanding a uniform load of 100 lbf. per sq. ft.

PART 2 - PRODUCTS

2.01	FERROUS METALS

A.	Metal Surfaces, General:  Form metal fabrications exposed to view upon completion of the work, provide materials selected for their surface flatness, smoothness, and freedom from surface blemishes.  Do not use materials whose exposed surfaces exhibit pitting, seam marks, roller marks, rolled trade names, roughness, and, for steel sheet, variations in flatness exceeding those permitted by referenced standards for stretcher-leveled sheet.

B.	Steel Plates, Shapes, and Bars:  ASTM A36.

C.	Rolled Steel Floor Plates:  ASTM A786.

D.	Steel Bars for Gratings:  ASTM A569 or ASTM A36.Å

E.	Wire Rod for Grating Cross Bars:  ASTM A510.

F.	Steel Tubing:  Cold-formed, ASTM A500, Grade B, unless otherwise indicated.

G.	Uncoated Structural Steel Sheet:  Hot-rolled, ASTM A570, Grade 30 unless otherwise indicated.

H.	Uncoated Steel Sheet (Commercial quality):  Cold-rolled,  ASTM A366.

I.	Galvanized Steel Sheet:  Quality as follows:

1.	Structural Quality:  ASTM A446; Grade A, unless another grade required for design loading, and G90 coating designation unless otherwise indicated.

2.	Commercial Quality:  ASTM A526, G90 coating designation unless otherwise indicated.

J.	Steel Pipe:  ASTM A53, Type S, Grade B, standard weight (schedule 40), black finish, unless otherwise indicated.

K.	Gray Iron Castings:  ASTM A48, Class 30.

L.	Malleable Iron Castings:  ASTM A47, Grade 32510.

M.	Brackets, Flanges and Anchors:  Cast or formed metal of the same type material and finish as supported rails, unless otherwise indicated.

N.	Concrete Inserts:  Threaded or wedge type; galvanized ferrous castings, either malleable iron, ASTM A47, or cast steel, ASTM A27.  Provide bolts, washers, and shims as required, hot-dip galvanized per ASTM A153.

O.	Welding Rods and Bare Electrodes:  Select in accordance with AWS specifications for the metal alloy to be welded.

2.02	STAINLESS STEEL

A.	Bar Stock:  ASTM A276, Type 302 or 304.

B.	Plate:  ASTM A167, Type 302 or 304.

2.03	ALUMINUM

A.	Extruded Bars and Shapes:  ASTM B221, alloy 6061-T6 or 6063-T6 for bearing bars of gratings and shapes and 6061-T6 for grating cross bars.

B.	Aluminum-Alloy Rolled Tread Plate:  ASTM B632, alloy 6061-T4 for treads and 6061-T6 for platforms.

2.04	GROUT

A.	Nonshrink Nonmetallic Grout:  Premixed, factory-packaged, nonstaining, noncorrosive, nongaseous grout complying with ASTM C1107 (formerly referenced as CE CRD C621).  Provide grout specifically recommended by manufacturer for interior and exterior applications of type specified in this section.

B.	Subject to compliance with requirements, products that may be incorporated in the work include, but are not limited to the following:

Euco N-S Grout - Euclid Chemical Co.

Kemset - Chem-Masters Corp.

Crystex - L & M Construction Chemicals, Inc.

Sonogrout - Sonneborn Building Products Div., Rexnord Chemical Products, Inc.

Supreme Grout - Cormix, Inc.

Sure-Grip High Performance Grout - Dayton Superior

Vibropruf #11 - Lambert Corp.

2.05	FASTENERS

A.	General:  Provide zinc-coated fasteners for exterior use or where built into exterior walls.  Select fasteners for the type, grade, and class required.  Suspect/counterfeit bolts will not be accepted and will be replaced at Contractor's expense.

B.	Bolts and Nuts:  Regular hexagon head type, ASTM A307, Grade A.

C.	Lag Bolts:  Square head type, FS FF-B-561.

D.	Machine Screws:  FS FF-S-92.

E.	Wood Screws:  Flat head carbon steel, FS FF-S-111.

F.	Plain Washers:  Round, carbon steel, FS FF-W-92.

G.	Expansion Anchors:  Expansion anchors complying with FS FF-S-325.

H.	Toggle Bolts:  Tumble-wing type, FS FF-B-588, type, class, and style as required.

I.	Lock Washers:  Helical spring type carbon steel, FS FF-W-84.

J.	Special Fasteners:  Split nuts, indicator washers and others, as indicated.

2.06	PAINT

A.	Shop Primer for Ferrous Metal:  Red oxide, lead- and cadmium-free, corrosion-inhibiting primer complying with performance requirements of FS TT-P-664.

B.	Galvanizing Repair Paint:  High zinc dust content paint for regalvanizing welds in galvanized steel, with dry film containing not less than 94% zinc dust by weight, and complying with MIL-P-21035 or SSPC-Paint-20.

C.	Bituminous Paint:  Cold-applied asphalt mastic complying with SSPC-Paint-12 except containing no asbestos fibers.

D.	Zinc Chromate Primer:  FS TT-P-645.

2.07	CONCRETE FILL

A.	Concrete Materials and Properties:  Comply with requirements for Division 3, Section "Cast-in-Place Concrete" for normal weight, ready-mix concrete with minimum 28-day compressive strength of 3000 psi (21 MPa), unless higher strength indicated.

B.	Nonslip Aggregate Finish:  Factory-graded, packaged material containing fused aluminum oxide grits or crushed emery as abrasive aggregate; rust-proof and nonglazing; unaffected by freezing, moisture, or cleaning materials.

2.08	FABRICATION, GENERAL

A.	Form metal fabrications from materials of size, thickness, and shapes indicated but not less than that needed to comply with performance requirements indicated.  Work to dimensions indicated or accepted on shop drawings, using proven details of fabrication and support.  Use type of materials indicated or specified for various components of each metal fabrication.

B.	Form exposed work true to line and level with accurate angles and surfaces and straight sharp edges.

C.	Allow for thermal movement resulting from the following maximum change (range) in ambient temperature in the design, fabrication, and installation of installed metal assemblies to prevent buckling, opening up of joints, and overstressing of welds and fasteners.  Base design calculations on actual surface temperatures of metals due to both solar heat gain and nighttime sky heat loss.  Temperature change (Range):  100 deg F (38 deg C).

D.	Shear and punch metals cleanly and accurately.  Remove burrs.

E.	Ease exposed edges to a radius of approximately 1/32 inch ( 0.794 mm), unless otherwise indicated.  Form bent-metal corners to smallest radius possible without causing grain separation or otherwise impairing work.

F.	Remove sharp or rough areas on exposed traffic surfaces.

G.	Weld corners and seams continuously to comply with AWS recommendations and the following:

1.	Use materials and methods that minimize distortion and develop strength and corrosion resistance of base metals.

2.	Obtain fusion without undercut or overlap.

3.	Remove welding flux immediately.

4.	At exposed connections, finish exposed welds and surfaces smooth and blended so that no roughness shows after finishing and contour of welded surface matched those adjacent.

H.	Form exposed connections with hairline joints, flush and smooth, using concealed fasteners wherever possible.  Use exposed fasteners of type indicated or, if not indicated, Phillips flat-head (countersunk) screws or bolts.  Locate joints where least conspicuous.

I.	Provide for anchorage of type indicated; coordinate with supporting structure.  Fabricate and space anchoring devices to provide adequate support for intended use.

J.	Shop Assembly:  Preassemble items in shop to greatest extent possible to minimize field splicing and assembly.  Disassemble units only as necessary for shipping and handling limitations.  Use connections that maintain structural value of joined pieces.  Clearly mark units for reassembly and coordinated installation.

K.	Cut, reinforce, drill and tap miscellaneous metal work as indicated to receive finish hardware, screws, and similar items.

L.	Fabricate joints that will be exposed to weather in a manner to exclude water, or provide weep holes where water may accumulate.

2.09	STEEL LADDERS

A.	General:  Fabricate ladders for the locations shown, with dimensions, spacings, details and anchorages as indicated.  Comply with requirements of ANSI A14.3 and CFR 29 1910.27; where conflicts occur, comply with the more stringent requirements.

B.	Side Rails:  Continuous steel flat bars, minimum size (cross section) 2-1/2" x 3/8" (63.5 mm x 9.5 mm), with eased edges, spaced 18 inches (0.46 m) apart.  For ladders subject to unusually corrosive atmospheric exposures, steel flat bars 2-1/2" x 1/2" (63.5 mm x 12.7 mm).

C.	Bar Rungs:  Round steel bars, minimum 3/4 inch (19.1 mm) diameter, spaced no greater than 12 inches (305 mm) o.c. and uniform throughout the length of the ladder.  Individual metal rungs embedded in concrete which serve as access to pits and other areas under floors, should have a minimum diameter of 1 inch (25 mm) or shall otherwise be treated to resist corrosion and rusting.

D.	Fit rungs  in centerline of side rails, plug weld and grind smooth on outer rail faces.

E.	Support each ladder at top and bottom and at intermediate points spaced not more than 5'-0" (1.5 m) o.c. by means of welded brackets, unless otherwise indicated.

1.	Size brackets to support design dead and live loads indicated and to hold centerline of ladder rungs clear of the wall surface by not less than 7 inches (178 mm).

2	Extend side rails 42 inches (1.1 m) above top rung, and return rails to wall or structure unless other secure handholds are provided.  If the adjacent structure does not extend above the top rung, goose-neck the extended rails back to the structure to provide secure ladder access.

2.10	METAL BAR GRATINGS

A.	General:  Produce metal bar gratings of description indicated per NAAMM marking system that comply with the following:

1.	Metal Bar Grating Standard:  "Standard Specifications for Metal Bar Grating and Metal Bar Grating Treads" published in ANSI/NAAMM MBG 531.

2.	Heavy Duty Metal Bar Grating Standard:  "Guide Specifications for Heavy Duty Metal Bar Grating" published in ANSI/NAAMM MBG 532.

B.	If gratings are located in walking surfaces, gratings shall have spaces no greater than 1/2 inch (12.7 mm) wide in one direction.  If gratings have elongated openings, then they shall be placed so that the long dimension is perpendicular to the dominant direction of travel.

C.	Fabricate steel gratings to comply with requirements as indicated on the drawings.

D.	Traffic Surface for Steel Bar Gratings:  Plain, unless otherwise indicated.

E.	Steel Finish:  Shop prime paint applied in accordance with manufacturer's standard practice.

F.	Fabricate removable grating sections with banding bars attached by welding to entire perimeter of each section.  Include anchors and fasteners of type indicated, or if not indicated, as recommended by manufacturer, for attachment to supports.

1.	Heavy Duty Grating:  Provide not less than 4 anchor blocks, 1/4 inch (6.4 mm) minimum thickness,  for each section of grating composed of bearing bars over 3/16 inch (4.8 mm) in thickness, with each block shop-welded to 2 bearing bars.

2.	Nonheavy Duty Grating:  Provide not less than 4 saddle clips for each grating section composed of rectangular bearing bars 3/16 inch (4.8 mm) or less in thickness and spaced not less than 15/16 inch (23.8 mm) o.c., with each clip designed and fabricated to fit over 2 bearing bars.  Furnish threaded bolts with nuts and washers for each clip required, unless otherwise indicated.

G.	Fabricate cutouts in grating sections for penetrations indicated.  Arrange layout of cutouts to permit grating removal without disturbing items penetrating gratings.

1.	Edge band openings in grating that interrupt 4 or more bearing bars with bars of same size and material as bearing bars.

2.	Do not notch bearing bars at supports to maintain elevation.

H.	Available Manufacturers:  Subject to compliance with requirements, manufacturers offering metal bar gratings that may be incorporated in the Work include, but are not limited to, the following:

Alabama Metal Industries Corp.

Barnet/Bates Corp.

IKG Industries

Klemp Corp.

Ohio Gratings, Inc.

Seidelhuber Metal Products, Inc.

2.11	STEEL PIPE GUARDRAILS AND HANDRAILS

A.	General:  Fabricate pipe guardrails and handrails to comply with requirements indicated for dimensions, details, finish, and member sizes, including wall thickness of pipe, post spacings, and anchorage.

B.	Interconnect guardrails and handrail members by butt-welding or welding with internal connectors, at fabricator's option, unless otherwise indicated.  At tee and cross intersections, cope ends of intersecting members to fit contour of pipe to which end is joined, weld all around and grind smooth.

C.	Form changes in directions of railing members as follows:

1.	By use of welded prefabricated steel elbow fittings.

2.	By bending, of radius indicated.

3.	By mitering at elbow bends.

D.	Form simple and compound curves by bending pipe in jigs to produce uniform curvature for each repetitive configuration required; maintain cylindrical cross-section of pipe throughout entire bend without buckling, twisting, cracking, or otherwise deforming exposed surfaces of pipe.

E.	Provide wall returns at ends of wall-mounted handrails, unless otherwise indicated.

F.	Close exposed ends of pipe by welding 3/16 inch (4.8 mm) thick steel plate in place or by use of prefabricated fittings, except where clearance of end of pipe and adjoining wall surface is 1/4 inch (6.4 mm) or less.

G.	Toe Boards:  Where indicated, provide toe boards at railings around openings and at the edge of open-sided floors and platforms.  Fabricate to dimensions and details indicated, or if not indicated, use 4 inches high x 1/4 inch (102 mm x 6.4 mm) steel bar welded to each railing post.

H.	Brackets, Flanges, Fittings, and Anchors:  Provide wall brackets, end closures, flanges, miscellaneous fittings, and anchors for interconnections of pipe and attachment of guardrails and handrails to other work.  Furnish inserts and other anchorage devices for connecting guardrails and handrails to concrete or masonry work.

1.	For railing posts set in concrete, fabricate sleeves from steel pipe not less than 6 inches (152 mm) long and with an inside diameter not less than 1/2 inch (12.7 mm) greater than the outside diameter of post, with steel plate closure welded to bottom of sleeve.

2.	For removable railing posts, fabricate slip-fit sockets from steel pipe whose inside diameter is sized for a close fit with posts and to limit deflection of post without lateral load, measured at top, to not more than 1/12 of post height.  Provide socket covers designed and fabricated to resist accidental dislodgement.

I.	Fillers:  Provide steel sheet or plate fillers of thickness and size indicated or required to support structural loads of handrails where needed to transfer wall bracket loads through wall finishes to structural supports.  Size fillers to suit wall finish thicknesses.  Size fills to produce adequate bearing to prevent bracket rotation and overstressing of substrate.

2.12	CAST NOSINGS

A.	Fabricate units of cast aluminum; 4 inches wide by 5/16 inches thick.  Provide units with integral abrasive finish.  Furnish in lengths as required to accurately fit each opening or conditions.  Cast units with an integral abrasive grit consisting of aluminum oxide, silicone carbide, or a combination of both.  Provide a fluted or cross-hatched surface.

B.	Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated in the Work include, but are not limited to, the following:

AMSTEP Products, division of American Safety Technologies, Inc.

American Safety Tread Co., Inc.

IKG Industries

Safe-T-Metal Co., Inc.

Wooster Products Inc.

C.	Provide anchors for embedding units in concrete, either integral or applied to units, as standard with the manufacturer.

D.	Apply black asphaltic coating to concealed bottoms, sides, and edges of cast-iron units set into concrete.

2.13	STEEL FRAMED STAIRS

A.	General:  Construct stairs to conform to sizes and arrangements indicated with welded connections, unless otherwise indicated.  Provide complete stair assemblies, including metal framing, hangers, columns, railings, newels, balusters, struts, clips, brackets, bearing plates, and other components necessary for the support of stairs and platforms, and as required to anchor and contain the stairs on the supporting structure.  Fabricate treads and platforms of exterior stairs to accommodate slopes to drain in finished traffic surfaces.

B.	Stair Framing:  Fabricate stringers of structural steel channels, or plates, or a combination thereof, as indicated.  Provide closures for exposed ends of stringers.  Construct platforms of structural steel channel headers and miscellaneous framing members as indicated.  Bolt or weld headers to stringers, newels, and framing members to stringers and headers; fabricate and join so that bolts, if used, do not appear on finish surfaces.

C.	Metal Pan Risers, Subtreads, and Subplatforms:  Shape metal pans for risers and subtreads to conform to configuration shown.  Provide thickness of structural steel sheet for metal pans as indicated.

1.	Form metal pans of uncoated cold-rolled steel sheet, unless otherwise indicated.

2.	Form metal pans of galvanized steel sheet, where indicated on the drawings.

3.	Attach Risers and Subtreads to Stringers by the following methods:

a.	Directly weld risers and subtreads to stringers; locate welds on side of metal pans to be concealed by concrete fill.

b.	Attach by means of brackets made of steel angles or bars.  Weld brackets to stringers and attach metal pans to brackets by welding or bolting.

4.	Provide subplatforms of configuration and construction shown, with thickness of structural steel sheet as indicated.  Attach subplatform to platform framing members with welds or as otherwise indicated.  Construct subplatforms with smooth soffits.

D.	Stair Guardrails and Handrails:  Comply with applicable requirements specified elsewhere in this section for steel pipe guardrails and handrails, and as follows:

1.	Railings may be bent at corners, rail returns, and wall returns, instead of using prefabricated fittings.

2.	Connect railing posts to stair framing by direct welding, unless otherwise indicated.

2.14	FINISHES

A.	General:  Comply with NAAMM  AMP 500 "Metal Finishes Manual" for recommendations relative to application and designations of finishes.

B.	Finish metal fabrications after assembly.

2.15	STEEL AND IRON FINISHES

A.	General:  Shop-paint uncoated surfaces of metal fabrications, except those to be embedded in concrete or masonry or to receive sprayed-on fireproofing, surfaces and edges to be welded, and galvanized surfaces, unless otherwise indicated.  Comply with requirements of SSPC-PA 1 for shop painting.

B.	Galvanizing:  For those items indicated for galvanizing, apply zinc-coating by the hot-dip process in compliance with the following requirements:

1.	ASTM A123 for galvanizing both fabricated and unfabricated iron and steel products made of uncoated rolled, pressed, and forced shapes, plates, bars, and strip 0.0299 inch (0.7595 mm) thick and heavier.

2.	ASTM A153 for galvanizing iron and steel hardware.

C.	Surface Preparation for Shop Priming:  Prepare uncoated ferrous metal surfaces to comply with minimum requirements indicated below.

1.	Remove oil, grease and similar contaminants in accordance with SP-1, "Solvent Cleaning".

2.	Remove loose rust, scale, spatter, slag and other deleterious materials in accordance with SSPC, utilizing the following methods as required:

SP-2"Hand-Tool Cleaning"

SP-3"Power-Tool Cleaning"

SP-7"Brush-Off  Blast Cleaning"

D.	Painting:  Immediately after surface preparation, apply structural steel primer paint in accordance with manufacturer's instructions and at a rate to provide dry film thickness of not less than 3.0 mils (0.076 mm).  Use painting methods that result in full coverage of joints, corners, edges, and exposed surfaces.  Apply 2 coats of paint to surfaces that are inaccessible after assembly or erection.

2.16	ALUMINUM FINISH

A.	Mill (as fabricated) finish, unless otherwise indicated.

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Installer shall examine the areas and conditions under which metal fabrication items are to be installed.  Notify the SDR in writing of conditions detrimental to the proper and timely completion of the work.  Do not proceed with the work until unsatisfactory conditions have been corrected in a manner acceptable to the Installer and SDR.

3.02	PREPARATION

A.	Coordinate and furnish anchorages, setting drawings, diagrams, templates, instructions, and directions for installation of anchorages, including concrete inserts, sleeves, anchor bolts, and miscellaneous items having integral anchors that are to be embedded in concrete or masonry construction.  Coordinate delivery of such items to project site.

B.	Center nosings on tread widths with noses flush with riser faces and tread surfaces.

C.	Set sleeves in concrete with tops flush with finish surface elevations; protect sleeves from water and concrete entry.

3.03	INSTALLATION, GENERAL

A.	Fastening to In-Place Construction:  Provide anchorage devices and fasteners where necessary for securing miscellaneous metal fabrications to in-place construction; include threaded fasteners for concrete and masonry inserts, toggle bolts, through-bolts, lag bolts, wood screws and other connectors as required.

B.	Cutting, Fitting and Placement:  Perform cutting, drilling, and fitting required for installation of miscellaneous metal fabrications.  Set metal fabrication accurately in location, alignment, and elevation; with edges and surfaces level, plumb, true, and free of rack; and measured from established lines and levels.

C.	Provide temporary bracing or anchors in formwork for items that are to be built into concrete masonry or similar construction.

D.	Fit exposed connections accurately together to form hairline joints.  Weld connections that are not to be left as exposed joints, but cannot be shop-welded because of shipping size limitations.  Do not weld, cut, or abrade the surfaces of exterior units which have been hot-dip galvanized after fabrication, and are intended for bolted or screwed field connections.

E.	Field Welding:  Comply with AWS Code for procedures of manual shielded metal-arch welding, appearance and quality of welds made, methods used in correcting welding work, and the following:

1.	Use materials and methods that minimize distortion and develop strength and corrosion resistance of base metals.

2.	Obtain fusion without undercut or overlap.

3.	Remove welding flux immediately.

4.	At exposed connections, finish exposed welds and surfaces smooth and blended so that no roughness shows after finishing and contour of welded surfaces matches those adjacent.

F.	Grout:  Follow manufacturer's recommendations for substrate preparation and application.

G.	Corrosion Protection:  Coat concealed surfaces of aluminum that will come into contact with grout, concrete, masonry, wood, or dissimilar metals with a heavy coat of bituminous paint or zinc chromate primer.

3.04	INSTALLATION OF METAL BAR GRATINGS

A.	General:  Install gratings to comply with requirements of NAAMM grating standard that apply to grating types and bar sizes indicated, including installation clearances and standard anchoring details.

B.	Secure removable units to supporting members with type and size of clips and fasteners indicated, or if not indicated, as recommended by grating manufacturer for type of installation conditions shown.

3.05	INSTALLATION OF STEEL PIPE GUARDRAILS AND HANDRAILS

A.	Adjust railings prior to anchoring to ensure matching alignment at abutting joints.  Space posts at spacing indicated, or if not indicated, as required by design loadings.  Plumb posts in each direction.  Secure posts and railing ends to building construction as follows:

1.	Anchor posts in concrete by means of pipe sleeves preset and anchored into concrete.  After posts have been inserted into sleeves, fill annular space between post and sleeve solid with nonshrink, nonmetallic grout, mixed and placed to comply with anchoring material manufacturer's directions.

2.	Anchor posts and rail ends to steel with welded connections, unless otherwise indicated.

3.	Anchor  posts and rail ends into concrete and masonry with steel round flanges welded to post and rail ends, and anchored into wall construction with expansion shields and bolts.

4.	Install removable railing sections where indicated in slip-fit metal sockets cast into concrete.  Accurately locate sockets to match post spacing.

B.	Secure handrails to wall with wall brackets and end fittings.  Provide bracket with not less than 1-1/2 inch (38.1 mm) clearance from inside face of handrail and finished wall surface.  Locate brackets at spacing not less than 5'-0" (1.5 m) o.c., unless otherwise indicated.  Secure wall brackets and wall return fittings to building construction as follows:

1.	Use type of bracket with flange tapped for concealed anchorage to threaded hanger bolt.

2.	For concrete and solid masonry anchorage, use drilled-in expansion shield and either concealed hanger bolt or exposed lag bolt, as applicable.

3.	For hollow masonry anchorage, fasten brackets directly on masonry wall using toggle bolts.

4.	For steel framed gypsum board assemblies, fasten brackets to wood blocking using lag bolts or to metal blocking using self-tapping screws, of size and type required to support structural loads.

C.	Expansion Joints:  Provide expansion joints at locations indicated, or if not indicated, at intervals not to exceed 40 feet (12.2 m).  Provide slip joint with internal sleeve extending 2 inches (51 mm) beyond joint on either side; fasten internal sleeve securely to one side; locate joint within 6 inches (152 mm) of posts.

3.06	INSTALLATION OF CAST NOSINGS

A.	Install cast nosings and treads with anchorage system indicated to comply with manufacturer's recommendations.

3.07	ADJUSTING AND CLEANING

A.	Touch-Up Painting of Steel Items:  Immediately after erection, clean field welds, bolted connections, abraded areas of shop paint, and paint exposed areas with same material as used for shop painting to comply with SSPC-PA 1 requirements for touch-up of field painted surfaces.  Apply by brush or spray to provide a minimum dry film thickness of 3.0 mils (0.076 mm).

B.	For galvanized surfaces clean welds, bolted connections and abraded areas and apply galvanizing repair paint to comply with ASTM A780.

END OF SECTION