## Walk Thru List
Questions for the Facility Operator
|  |  |  | RESPONSE
Obtain 12 Months of Electric Bills
Do Bills Contain Monthly Demand Values?
Bills Contains On-Peak and Off-Peak Consumption?
Name of Rate Schedule(s) Used
Obtain 12 Months of Gas Bills
Do Bills Contain Energy Usage?
Is Gas Purchased Under Contract?
Name of Rate Schedule(s) Used
Obtain 12 Months of Fuel Oil Bills (If Used) |  |  |  |  | Gallons
| Do Bills Contain Amount Used |  |  |  | Liters
| Type of Fuel Oil Used |  |  | No. 2
No. 6
YES
NO
Industrial Loads - Ask for Information on Operating Schedules
| Number of Hours of Operation on Weekdays? |  |  |  | Hrs./Day
| Number of Hours of Operation on Weekends? |  |  |  | Hrs./Day
| Schedule of Major Process Heat Loads? |  |  |  | Hrs./Day
Does the Plant Have a Steam System?
| Operating Pressure |  |  |  | psig
Commercial Loads - Ask for Information on Operating Schedules
| Hours Facility is Open for Business or Largely Occupied? |  |  |  | Hrs./Day
Type of Heating System(s)?
Indicate All Types
Type of Cooling System(s)?
[6 empty] | Yes | Yes
Electric Parameters
Certain Issues with the Current Electric Power Service Can Impact CHP Economics. These Questions Investigate Power Service Issues
How Many Electric Services Drops Are There to the Facility?
How Many Electric Meters Serve the Facility?
| Estimate the Distance Between the Multiple Meters in Your Facility |  |  |  | Feet
Do All of Your Service Drops Originate at the Same Utility Feeder?
Has the Facility Experienced Problems with Power Quality Such as:
| Low Voltage? |  |  | If Yes, Please Describe:
| Poor Frequency Quality? |  |  | If Yes, Please Describe:
| Does the Facility Have Any Significant Need for UPS Systems? |  |  | If Yes, Please Describe:
| Estimate the Number of Momentary Electric Power Outages |  |  |  | (<1 Second) per year
Momentary Power Drops are Power Fluctuations that Cause Computer Equipment to Reset a Full Blackout
Estimated Cost of a Momentary Power Outage
| Estimate the Number of Non-momentary or Complete Electric Power Outages |  |  |  | Occurances per year
| Estimate Cost of a Non-MomentaryPower Outage |  |  |  | per Hour
Does the Facility Have Back-Up Generation?
Yes
| What is the Size of the Back-Up Generators |  |  |  | kWe | No
Are the Back-Up Generators Diesel Fuel?
| How Old are the Back-Up Generators |  |  |  | Years
What is the Facilities Current Power Factor
(This Question Can Generally be Skipped for Commercial Buildings)
Overall Location and Equipment Questions
Overall Location Questions: It is Important to Find a Location for the CHP System That Allows the System to be Affordably Connected to the Electric and Thermal Loads
If CHP is Installed - Where Can it Be Located?
| How Close are the Existing Electric Feeders to This Location? |  |  |  | Feet
Does a Single Electric Distribution System Exist that Can be Used?
(Question Important for Multi-Building Campuses)
Does a Hot Water or Steam Piping System Exist that Could be Used?
| How Close is the Existing Heating Plant? |  |  |  | Feet
Existing Equipment: A CHP system will need to tie into existing heating and cooling systems. The current state of these systems will affect the savings and the first cost
| What is the Approximate Efficiency of the Existing Heating System? |  |  |  | %
| How Old is the Current Heating System? |  |  |  | Years
How is Heat Distributed to the Building? Steam, Hot Water, or Hot Air
If Steam, What Operating Pressure? If Water, At What Delivery Temp?
| What Sizes are the Existing Heating Equipment? |  | Type | Capacity | Units
| Please Mark Type of Heating System: | No. 1 |  |  |  | GHA
| GSB = Gas Fired Steam Boiler GHW = Gas Hot Water Boiler | No. 2 |  |  |  | GB
| OSB = Oil Fired Steam Boiler OHW = Oil Hot Water Boiler | No. 3 |  |  |  | GHW
| ESB = Electric Steam Boiler EHW = Electric Hot Water Boiler | No. 4 |  |  |  | OHA
| OHW = Oil Hot Water Boiler O = Other (Please Describe) | No. 5 |  |  |  | OB
| ERT = Rooftop Units-Electric Heat GRT = Rooftop Units-Gas Heat |  |  |  |  | OHW
| Estimate the Maximum Cooling Load? |  |  |  | Tons | O
Yes
| Does the Facility Have a Chilled Water Distribution System? |  |  |  |  | No
| How Long is the Distance to the Existing Chiller Room? |  |  |  | Feet
| How Old are the Existing Chillers |  |  |  | Years
| What Sizes and Type are the Existing Chillers? | No. 1 |  |  | Tons | E
| Please Indicate the Type of Chillers E = Electric Chillers | No. 2 |  |  | Tons | AS
| AS = Absorption (Steam Fired) AH = Absorption (Hot Water Fired) | No. 3 |  |  | Tons | AH
| AD = Absorption (Direct Fired) ED = Engine Driven | No. 4 |  |  | Tons | ED
| SD = Steam Turbine Driven O = Other | No. 5 |  |  | Tons | O
| Are There Concerns about Noise at the Selected System Location? |  |  | If Yes, Please Describe
| Are There Concerns about Vibration at the Selected System Location? |  |  | If Yes, Please Describe
Other Questions
Questions to Consider that Facility Operators May Be Able to Help With
| Would the Facility be Able to Obtain Gas at a Lower Rate if the Gas Consumption of the Facility Were Larger? |  |  |  |  | Yes
No
| What are the Electric Utility Stand-By Charges in This Area? |  |  |  | $/kW/Mo
Is the Facility Eligible for any State/Federal/Utility Rebate Programs?
Is the Facility Owned by a For-Profit Company?
If Yes, What is Their Marginal Corporate Tax Rate?
| Would the Facility be Interested in Leasing a CHP Plant? |  |  | Please Explain:
| Would the Facility be Interested in Having a Third Party Own the CHP Plant and Sell Them Power/Heating/Cooling? |  |  | Please Explain:
Note on D7: Indicated as Separate Amounts on Bill
Note on D6: Demand is Shown in kW
Note on E8: Rate Schedule Should Be Indicated on Bill
Note on E9: Rate Schedule Should Be Indicated on Bill
Note on D12: Energy Shown on Bill as Therms or BTU-h
Note on E14: Rate Schedule Should Be Indicated on Bill
Note on E15: Rate Schedule Should Be Indicated on Bill
Note on E18: Indicate Units of Measure on Bill
Note on D5: The Facility Manager should be able to get these for you. In some areas, electric usage can be downloaded from the utility website if the meter and account number are known. In some cases, the facility may be purchasing electricity "unbundled" where they are buying electicity wholesale and being charged "wires" fees for transmission and distribution. NOTE: There may be more than one monthly bill for a facility if it has multiple meters on-site.
Note on D11: The Facility Manager should be able to get these for you. Be sure to get and add transportation fees if gas is purchased from a wholesale supplier under a separate contract from the local gas distributor.
Note on E46: Central Boiler, Central Hot Water System, Roof Type Units, and/or Area Heaters
Note on E47: Central Boiler, Central Hot Water System, Roof Type Units, and/or Area Heaters
Note on E48: Central Boiler, Central Hot Water System, Roof Type Units, and/or Area Heaters
Note on E50: Electric Central Chillers, Absorption Central Chillers, Engine Driven Central Chillers, or Roof Type Units
Note on E51: Electric Central Chillers, Absorption Central Chillers, Engine Driven Central Chillers, or Roof Type Units
Note on E52: Electric Central Chillers, Absorption Central Chillers, Engine Driven Central Chillers, or Roof Type Units
Note on E66: This may be difficult to definitively ascertain without walking around the outside of the facility and looking for wire drops. To make sure that the connection is still "live" you will need to find a corresponding electrical distribution panel that is still active that can be associated with that service drop. Sometimes there are separate meters associated with each service drop.
Note on E68: The Facility Manager should be able to tell you this. If not, often multiples meters are billed on the same electric account and will be shown on the bill. Note: Sometimes separate bills will be issued for separate meters
Note on E72: This may be difficult to ascertain unless you are able to walk the feeder lines back to determine if they are fed off of different transformers. Be aware that sometimes feeder lines may be disconnected and crosstied away from a transformer, and may not be obvious without careful observation.
Note on D75: Low voltage indication may include such thngs as: motor failures, diming lights, or equipment resets.
Note on D78: Poor frequency indication may include such thngs as: sluggish motor operation, flickering lights, or equipment resets.
Note on D81: UPS systems may be benificial if there is equipment that shuts down or resets during momentary electric pertibations, or sensitve electornic equipment such as computers or automated process equipment.
Note on E84: Ask facility manager to estimate the number of momentary outages (<1 second) the facility can expect to experience in a year
Note on E86: This cost should be estimated based on the impact of the momentary interuption of electrical power such as; equipment resetting, loss of production/business, or loss of product.
Note on E88: Ask facility manager to estimate the number of non-momentary outages (>1 minute) the facility can expect to experience in a year.
Note on E90: This cost should be estimated based on the impact of the non- momentary interuption of electrical power such as; loss of production/business, or loss of product.
Note on D96: If back-up generator(s) are diesel fueled, they are note suited for CHP system use because they are not designed for continous operatoion and they have high emissions.
Note on E98: If generator is >20 years old consideration should be given to replacing it. Credit should be taken on a like-for-like bases in the financial assessment of the CHP project.
Note on E100: Power Factor is usually only a concern where there are large inductive loads, such as synchoronous motors, being used in industrial application and can generally be ignored in commercial applications. If power factor is an issue for a facility, generally the electric utility will have notified the facility or a capictor bank may have been installed near the service drop to the facility to offset the effect on the utility distribution lines.
Note on B107: Ideally this location will be within or adjacent to a central heating and cooling facility. It may be possible to locate some, if not all, of the equipment within an existing central heating/cooling facility. If this is not possible, the generating system may need to be remotely located, with heat recovery piping to the eating and cooling plant. However, the cost for this piping over very long distances can make the CHP system unattractive Enough space will be needed to site the generation equipment, heat exchange equipment, switchgear, (and if desired absorption chillers and/or desiccant systems), and connecting lines and duct work. Space also must be allocated for maintenance work on the equipment. Finally, engine generators are not recommended for installation on upper floors due to weight load and vibration. If a new structure needs to be built to house the CHP equipment it can substainially add to the cost of the project of a small system (<1 MWe).
Note on E110: Running electrical feeds across a distance will add cost to a project and may make a small (<250 kWe) project financially unattractive.
Note on D112: Combining feeds can add substantially to the cost of a project. Generally 2 feeds can be combined with reasonable costs. It may be less expensive to split the facility and install CHP on only 1 of the feeders. In rare cases, it also may not be possible for the utility to supply the back-up demand load to the facility off of one feeder. This can further add to the cost of the project.
Note on D115: Central heating facilities or heating distribution systems make it more cost effective when installing CHP.
Note on E117: It is impractical due to heat losses to run heat recovery ducting very far. It also adds to the CHP project cost.
Note on E122: If the current heating system has a low efficiency consideration should be given to replacing it as part of the CHP project. If a higher efficiency heating system is to be installed, the savings from increased efficiency should be included in the payback analysis.
Note on E124: If the current heating system is >20 years old consideration should be given to replacing it as part of the CHP project. Credit may be taken on a like-for-like bases in the financial assessment of the CHP project, depending on the planned operating schedule of the generator. If a higher efficiency heating system is to be installed, the savings from increased efficiency should be included in the payback analysis.
Note on E134: Include units to the right of the box.
Note on E135: Include units to the right of the box.
Note on E136: Include units to the right of the box.
Note on E137: Include units to the right of the box.
Note on E138: Include units to the right of the box.
Note on D143: Central chilled water facilities or cooling distribution systems make it more cost effective to install CHP.
Note on E145: Running chilling lines adds to the cost of a CHP project and should be added to the estimate if only average numbers are used.
Note on E147: If the current chillers are >20 years old consideration should be given to replacing them as part of the CHP project. Credit should be taken on a like-for-like bases in the financial assessment of the CHP project. If a higher COP chilling system is to be installed, the savings from increased efficiency should be included in the payback analysis.
Note on E168: This can generally be found in the utility rate book.
Note on D170: It might be possible to find out information on eligibility through the Midwest CHP Application Center or from the State Energy Office.
Note on F138: Include units here
Note on F137: Include units here
Note on F136: Include units here
Note on F135: Include units here
Note on F134: Include units here
Note on E126: If the current heating system is >20 years old consideration should be given to replacing it as part of the CHP project. Credit may be taken on a like-for-like bases in the financial assessment of the CHP project, depending on the planned operating schedule of the generator. If a higher efficiency heating system is to be installed, the savings from increased efficiency should be included in the payback analysis.
Note on E128: If the current heating system is >20 years old consideration should be given to replacing it as part of the CHP project. Credit may be taken on a like-for-like bases in the financial assessment of the CHP project, depending on the planned operating schedule of the generator. If a higher efficiency heating system is to be installed, the savings from increased efficiency should be included in the payback analysis.
Note on D134: Please Input the Type of Heating System Here
Note on D135: Please Input the Type of Heating System Here
Note on D136: Please Input the Type of Heating System Here
Note on D137: Please Input the Type of Heating System Here
Note on D138: Please Input the Type of Heating System Here
Note on D150: Please Input the Type of Chiller System Here
Note on D151: Please Input the Type of Chiller System Here
Note on D152: Please Input the Type of Chiller System Here
Note on D153: Please Input the Type of Chiller System Here
Note on D154: Please Input the Type of Chiller System Here
Note on E157: Generating Systems produce noise which can be silenced to as great a level as needed, within limits. However, there may be some added costs for such applications.
Note on E160: Engine Generators tend to produce far more vibration than turbine systems. Therefore, vibration requirements can occasionally effect system selection.
Note on E150: If a large number of rooftop units (>5) are being used, you may put the total capacity on a single line.
Note on E151: If a large number of rooftop units (>5) are being used, you may put the total capacity on a single line.
Note on E152: If a large number of rooftop units (>5) are being used, you may put the total capacity on a single line.
Note on E153: If a large number of rooftop units (>5) are being used, you may put the total capacity on a single line.
Note on E154: If a large number of rooftop units (>5) are being used, you may put the total capacity on a single line.