## DC Powering 1U Server Rack
Calculating Energy Savings Using High Efficiency DC Power Architecture in a Server Application; Rev 0.0, 04/10/2004 Pls send comments to amansoor@epri-peac.com | [9 empty] | Calculations
Calculations Based on Typical Power Budget for a Dual 2.4 GHz Xeon Processor based 1U Server Rack | [10 empty] | AC | DC
Input Data (Fill in Values (Blue Boxes) for the Data and Assumptions Used for the Analysis) |  |  | Results of Energy Savings Estimate | [6 empty] | VRM Out | 60
|  |  | Only Energy Relating Savings Considered; Other Savings such as Size, Heat Sink Cost not considered | [6 empty] | VRM In | 71.4286
| Power Conversion Efficiency |  |  | Energy Savings Estimate for One RACK of 1U Servers with High Efficiency Power Conversion | [5 empty] | AC/DC PS Out | 131.4286
| AC Power Architecture | DC Power Architecture |  | Total input Power(Watt) | Reduction in Air Conditioning Power (Watt) | Total Savings (Watt) | Yearly Energy Savings (MWh) | Yearly Energy Savings ($) | NPV of Savings ($) | AC/DC PS in | 182.5397
UPS | 85% | NA | AC Powering | 8590.1027 |  | 8590.1027 | 75.2493 | 9029.916 | 31289.6125 | UPS Out | 182.5397
AC/DC PS | 72% | NA | DC Powering | 6137.0818 |  | 6137.0818 | 53.7608 | 6451.3004 | 22354.4373 | UPS in | 214.7526
DC/DC VRM (12V-1.75V) | 84% | 84% | Net Savings | 2453.0209 | 836.9707 | 3289.9916 | 28.8203 | 3458.4392 | 11983.857
DC/DC (48V-12V) | NA | 95% | Total Savings Per Server |  |  | 82.2498 | 0.72051 | 86.461 | 299.5964 | 12V Out | 83.4286
DC/DC (48V-5V/3.3V) | NA | 90% | [7 empty] | 12V In | 87.8195
Nextek Power Module (AC/DC Rectifier) | NA | 92% | [7 empty] | 5V/3.3V Out | 48
[10 empty] | 5V/3.3V In | 53.3333
1U Dual Processor Server Power Budget | Typical (W) | Maximum (W) | [7 empty] | Nextek Out | 141.1529
Dual Processor Power (@1.75V DC) | 60 | 130 | [7 empty] | Nextek in | 153.427
Mother Board, PCI Card, DDR Memory and Other Peripheral DC Power Consumption (@12V, 5V and 3.3V DC) | 60 | 220
Electricity Cost | 0.12 | Cents/Kwh
Life Time | 4 | years
Discount Rate | 6% | percent
Overall Cooling System Efficiency | 1200 | Watt/Ton
Number of 1U Servers Per Rack | 40
Total AC Input Power Consumption for one 1U dual Processor Server
|  | Base Case | High Efficiency Case |  | Reduction in Power Loss
VRM Output Power |  | 60 | 60 |  | 0 |  |  |  | Dual 2.4GHz Xeon 1U Server Power Budget
VRM Input Power |  | 71.4286 | 71.4286
Total DC Power |  | 131.4286 | 131.4286 |  | #VALUE!
PS Input AC Power |  | 182.5397 | #VALUE! |  | #VALUE!
UPS Input Power |  | 214.7526 | #VALUE!
2.4 GHz Dual Xeon Processor Based 1U Server Power Budget
2.4 GHz Dual Xeon Processor Based 1U Server Power Budget
Industry Partners (There are other potential technologies that can be used as part of the DC Powering Architecture Demonstration)
1 Nextek Power System; Product Spec: http://www.nextekpower.com/Products.htm#specs
2 Taxaco Cobasys NiMh Stationery Battery; Product Spec: http://www.txobattery.com/product_information/prodInfo_stationary.htm
3 Artesyn Intermediate 12V Output DC-DC Converter; Product Spec: http://www.artesyn.com/powergroup/int_bus_conv.htm
4 Artesyn Dual Output (5V/3.3V)Quarter Brick; Product Spec http://www.artesyn.com/powergroup/quarter_brick.htm
Note on A1: Work Funded by CEC PIER Program on Data Center Efficiency Administered by LBNL
Note on B14: 100% duty Cycle; Very Conservative Estimate of Typical Power Consumption
120V AC
120V AC
Floppy Drive 0.5A CDROM Drive 0.8A Hard Drives, IDE, 4X 2.4A Blowers, 4X 6.6A
Mother Board 8.0A PCI Card 5A Hard Drives, IDE, 4X 1.2A Blowers, 4X 6.6A Keyboard & Mouse 0.5A Floppy Drive 0.2A CD ROM Drive 0.2A
Mother Board 1.5A DDR Memory 8.5A
Xeon 2.4HHz, 2X 14A@12V
208/277V AC
48V DC
Floppy Drive 0.5A CDROM Drive 0.8A Hard Drives, IDE, 4X 2.4A Blowers, 4X 6.6A
Mother Board 8.0A PCI Card 5A Hard Drives, IDE, 4X 1.2A Blowers, 4X 6.6A Keyboard & Mouse 0.5A Floppy Drive 0.2A CD ROM Drive 0.2A
Mother Board 1.5A DDR Memory 8.5A
Xeon 2.4HHz, 2X 14A@12V
Option for Direct DC PV Coupling
AC Powering Architecture
DC Powering Architecture