## Participant A
Participant A
Reactor Pressure Vessel
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | Developed from service history | 1.2097e-06 | 3.6292e-06 | 1.0888e-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 2 (> 1,500) |  | 1.2097e-06 | 3.6292e-06 | 1.0888e-05 | 0.015 | 0.3 | 0.585 | 0.015 | 0.3 | 0.585 | 0.015 | 0.3 | 0.585
| 3 (> 5,000) |  | 1.2097e-06 | 3.6292e-06 | 1.0888e-05 | 0.005 | 0.1 | 0.195 | 0.005 | 0.1 | 0.195 | 0.005 | 0.1 | 0.195
| 4 (> 25,000) |  | 1.2097e-06 | 3.6292e-06 | 1.0888e-05 | 0.0015 | 0.03 | 0.0585 | 0.0015 | 0.03 | 0.0585 | 0.0015 | 0.03 | 0.0585
| 5 (> 100,000) |  | 1.2097e-06 | 3.6292e-06 | 1.0888e-05 | 0.0005 | 0.01 | 0.0195 | 0.0005 | 0.01 | 0.0195 | 0.0005 | 0.01 | 0.0195
| 6 (> 500,000) |  | 1.2097e-06 | 3.6292e-06 | 1.0888e-05 | 0.00015 | 0.003 | 0.00585 | 0.00015 | 0.003 | 0.00585 | 0.00015 | 0.003 | 0.00585
CRDM | 1 (> 100) | Developed from service history | 1.5726e-05 | 4.7179e-05 | 0.00014154 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 2 (> 1,500) |  | 1.5726e-05 | 4.7179e-05 | 0.00014154 | 0.015 | 0.3 | 0.585 | 0.015 | 0.3 | 0.585 | 0.015 | 0.3 | 0.585
| 3 (> 5,000) |  | 1.5726e-05 | 4.7179e-05 | 0.00014154 | 0.005 | 0.1 | 0.195 | 0.005 | 0.1 | 0.195 | 0.005 | 0.1 | 0.195
| 4 (> 25,000) |  | 1.5726e-05 | 4.7179e-05 | 0.00014154 | 3.6e-05 | 0.00072 | 0.001404 | 3.6e-05 | 0.00072 | 0.001404 | 3.6e-05 | 0.00072 | 0.001404
| 5 (> 100,000) |  | 1.5726e-05 | 4.7179e-05 | 0.00014154 | 1.815e-05 | 0.000363 | 0.00070785 | 1.815e-05 | 0.000363 | 0.00070785 | 1.815e-05 | 0.000363 | 0.00070785
| 6 (> 500,000) |  | 1.5726e-05 | 4.7179e-05 | 0.00014154 | 1.815e-05 | 0.000363 | 0.00070785 | 1.815e-05 | 0.000363 | 0.00070785 | 1.815e-05 | 0.000363 | 0.00070785
CRDM Connections | 1 (> 100) | Developed from service history | 1.2097e-05 | 3.6292e-05 | 0.00010888 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 2 (> 1,500) |  | 1.2097e-05 | 3.6292e-05 | 0.00010888 | 0.015 | 0.3 | 0.585 | 0.015 | 0.3 | 0.585 | 0.015 | 0.3 | 0.585
| 3 (> 5,000) |  | 1.2097e-05 | 3.6292e-05 | 0.00010888 | 0.005 | 0.1 | 0.195 | 0.005 | 0.1 | 0.195 | 0.005 | 0.1 | 0.195
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzles | 1 (> 100) | Developed from service history
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
In-Core Instrumentation | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Head Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Other penetrations | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Pumps
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | developed from service data | 1.21e-06 | 3.63e-06 | 1.089e-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 2 (> 1,500) |  | 1.21e-06 | 3.63e-06 | 1.089e-05 | 0.015 | 0.3 | 0.585 | 0.015 | 0.3 | 0.585 | 0.015 | 0.3 | 0.585
| 3 (> 5,000) |  | 1.21e-06 | 3.63e-06 | 1.089e-05 | 0.005 | 0.1 | 0.195 | 0.005 | 0.1 | 0.195 | 0.005 | 0.1 | 0.195
| 4 (> 25,000) |  | 1.21e-06 | 3.63e-06 | 1.089e-05 | 0.0015 | 0.03 | 0.0585 | 0.0015 | 0.03 | 0.0585 | 0.0015 | 0.03 | 0.0585
| 5 (> 100,000) |  | 1.21e-06 | 3.63e-06 | 1.089e-05 | 0.0005 | 0.01 | 0.0195 | 0.0005 | 0.01 | 0.0195 | 0.0005 | 0.01 | 0.0195
6 (> 500,000)
Bonnet Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzle | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Flywheel | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Valves
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Bonnet Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Bonnet | 1 (> 100) | developed from service data | 1.21e-06 | 3.63e-06 | 1.089e-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 2 (> 1,500) |  | 1.21e-06 | 3.63e-06 | 1.089e-05 | 0.015 | 0.3 | 0.585 | 0.015 | 0.3 | 0.585 | 0.015 | 0.3 | 0.585
| 3 (> 5,000) |  | 1.21e-06 | 3.63e-06 | 1.089e-05 | 0.005 | 0.1 | 0.195 | 0.005 | 0.1 | 0.195 | 0.005 | 0.1 | 0.195
| 4 (> 25,000) |  | 1.21e-06 | 3.63e-06 | 1.089e-05 | 0.0015 | 0.03 | 0.0585 | 0.0015 | 0.03 | 0.0585 | 0.0015 | 0.03 | 0.0585
| 5 (> 100,000) |  | 1.21e-06 | 3.63e-06 | 1.089e-05 | 0.0005 | 0.01 | 0.0195 | 0.0005 | 0.01 | 0.0195 | 0.0005 | 0.01 | 0.0195
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Total Percent Contributions all Components
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100

## Participant B
Participant B
Reactor Pressure Vessel
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | BWR-3 | 1e-08 | 1e-08 | 1e-08 | 0.2 | 1 | 5 | 0.596 | 2.98 | 14.9 | 0.914 | 4.57 | 22.85
| 2 (> 1,500) |  | 2.32e-09 | 2.32e-09 | 2.32e-09 | 0.2 | 1 | 5 | 0.534 | 2.67 | 13.35 | 2.448 | 12.24 | 61.2
| 3 (> 5,000) |  | 1.21e-09 | 1.21e-09 | 1.21e-09 | 0.2 | 1 | 5 | 0.516 | 2.58 | 12.9 | 3.802 | 19.01 | 95.05
| 4 (> 25,000) |  | 5.04e-10 | 5.04e-10 | 5.04e-10 | 0.2 | 1 | 5 | 0.494 | 2.47 | 12.35 | 6.866 | 34.33 | 171.65
| 5 (> 100,000) |  | 2.38e-10 | 2.38e-10 | 2.38e-10 | 0.2 | 1 | 5 | 0.474 | 2.37 | 11.85 | 11.428 | 57.14 | 285.7
| 6 (> 500,000) |  | 9.86e-11 | 9.86e-11 | 9.86e-11 | 0.2 | 1 | 5 | 0.47 | 2.35 | 11.75 | 20.69 | 103.45 | 517.25
CRDM | 1 (> 100) | BWR-5 | 0.000127 | 0.000127 | 0.000127 | 0.2 | 1 | 5 | 0.044 | 0.22 | 1.1 | 0.044 | 0.22 | 1.1
| 2 (> 1,500) |  | 2.5e-05 | 2.5e-05 | 2.5e-05 | 0.2 | 1 | 5 | 0.04 | 0.2 | 1 | 0.04 | 0.2 | 1
| 3 (> 5,000) |  | 4e-09 | 4e-09 | 4e-09 | 0.2 | 1 | 5 | 0.01 | 0.05 | 0.25 | 0.01 | 0.05 | 0.25
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
CRDM Connections | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
| 6 (> 500,000) | [6 empty] | 0.006 |  |  | 0.006 |  |  | 0.006
Nozzles | 1 (> 100) | BWR-4 | 1e-06 | 1e-06 | 1e-06 | 0.2 | 1 | 5 | 0.294 | 1.47 | 7.35 | 0.25 | 1.25 | 6.25
| 2 (> 1,500) |  | 2e-07 | 2e-07 | 2e-07 | 0.2 | 1 | 5 | 0.294 | 1.47 | 7.35 | 0.25 | 1.25 | 6.25
| 3 (> 5,000) |  | 4e-08 | 4e-08 | 4e-08 | 0.2 | 1 | 5 | 0.294 | 1.47 | 7.35 | 0.25 | 1.25 | 6.25
| 4 (> 25,000) |  | 8e-09 | 8e-09 | 8e-09 | 0.2 | 1 | 5 | 0.294 | 1.47 | 7.35 | 0.25 | 1.25 | 6.25
5 (> 100,000)
6 (> 500,000)
In-Core Instrumentation | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Head Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Other penetrations | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Pumps
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | PWR-1 | 3e-07 | 3e-07 | 3e-07 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1
| 2 (> 1,500) |  | 1.2e-07 | 1.2e-07 | 1.2e-07 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1
| 3 (> 5,000) |  | 4.8e-08 | 4.8e-08 | 4.8e-08 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1
| 4 (> 25,000) |  | 1.92e-08 | 1.92e-08 | 1.92e-08 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1
| 5 (> 100,000) |  | 7.68e-09 | 7.68e-09 | 7.68e-09 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1
| 6 (> 500,000) |  | 3.07e-09 | 3.07e-09 | 3.07e-09 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1
Bonnet Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzle | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
| 6 (> 500,000) | [6 empty] | 0.006 |  |  | 0.006 |  |  | 0.006
Flywheel | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
Valves
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | PWR-1 | 3e-07 | 3e-07 | 3e-07 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1
| 2 (> 1,500) |  | 1.2e-07 | 1.2e-07 | 1.2e-07 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1
| 3 (> 5,000) |  | 4.8e-08 | 4.8e-08 | 4.8e-08 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1
| 4 (> 25,000) |  | 1.92e-08 | 1.92e-08 | 1.92e-08 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1
| 5 (> 100,000) |  | 7.68e-09 | 7.68e-09 | 7.68e-09 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1
| 6 (> 500,000) |  | 3.07e-09 | 3.07e-09 | 3.07e-09 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1 | 0.01 | 0.1 | 1
Bonnet Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Bonnet | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
| 6 (> 500,000) | [6 empty] | 0.006 |  |  | 0.006 |  |  | 0.006
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
Total Percent Contribution all Components
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100

## Participant C
Participant C
Reactor Pressure Vessel
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | Pete's BWR-3 base case for LTOP | 1e-08 | 1e-08 | 1e-08 | 0.03 | 1 | 30 | 0.0894 | 2.98 | 89.4 | 0.1371 | 4.57 | 137.1
| 2 (> 1,500) |  | 2.32e-09 | 2.32e-09 | 2.32e-09 | 0.03 | 1 | 30 | 0.0801 | 2.67 | 80.1 | 0.3672 | 12.24 | 367.2
| 3 (> 5,000) |  | 1.21e-09 | 1.21e-09 | 1.21e-09 | 0.03 | 1 | 30 | 0.0774 | 2.58 | 77.4 | 0.5703 | 19.01 | 570.3
| 4 (> 25,000) |  | 5.04e-10 | 5.04e-10 | 5.04e-10 | 0.03 | 1 | 100 | 0.0741 | 2.47 | 247 | 1.0299 | 34.33 | 3433
| 5 (> 100,000) |  | 2.38e-10 | 2.38e-10 | 2.38e-10 | 0.03 | 1 | 1000 | 0.0711 | 2.37 | 2370 | 1.7142 | 57.14 | 57140
| 6 (> 500,000) |  | 9.86e-11 | 9.86e-11 | 9.86e-11 | 0.03 | 1 | 1000 | 0.0705 | 2.35 | 2350 | 3.1035 | 103.45 | 103450
CRDM | 1 (> 100) | Pete's BWR-5 base case for CRDM | 0.000127 | 0.000127 | 0.000127 | 0.03 | 1 | 30 | 0.0066 | 0.22 | 6.6 | 0.0066 | 0.22 | 6.6
| 2 (> 1,500) |  | 2.5e-05 | 2.5e-05 | 2.5e-05 | 0.03 | 1 | 30 | 0.006 | 0.2 | 6 | 0.006 | 0.2 | 6
| 3 (> 5,000) |  | 4e-09 | 4e-09 | 4e-09 | 0.03 | 1 | 30 | 0.0015 | 0.05 | 1.5 | 0.0015 | 0.05 | 1.5
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
CRDM Connections | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzles | 1 (> 100) | Pete's base case for FW Nozzles. | 1e-06 | 1e-06 | 1e-06 | 0.03 | 1 | 30 | 0.03 | 1.47 | 30 | 0.03 | 1.25 | 30
| 2 (> 1,500) |  | 2e-07 | 2e-07 | 2e-07 | 0.03 | 1 | 30 | 0.03 | 1.47 | 30 | 0.03 | 1.25 | 30
| 3 (> 5,000) |  | 4e-08 | 4e-08 | 4e-08 | 0.03 | 1 | 30 | 0.03 | 1.47 | 30 | 0.03 | 1.25 | 30
| 4 (> 25,000) |  | 8e-09 | 8e-09 | 8e-09 | 0.03 | 1 | 100 | 0.03 | 1.47 | 100 | 0.03 | 1.25 | 100
5 (> 100,000)
6 (> 500,000)
In-Core Instrumentation | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Head Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Other penetrations | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 60 | 80 | 100 | 60 | 80 | 100 | 60 | 80 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 60 | 80 | 100 | 60 | 80 | 100 | 60 | 80 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 60 | 80 | 100 | 60 | 80 | 100 | 60 | 80 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 60 | 80 | 100 | 60 | 80 | 100 | 60 | 80 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Pumps
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | Recirculation Line | 0.001 | 0.001 | 0.001 | 5e-05 | 0.001 | 0.01 | 5e-05 | 0.001 | 0.01 | 5e-05 | 0.001 | 0.01
| 2 (> 1,500) |  | 0.0006 | 0.0006 | 0.0006 | 4e-05 | 0.001 | 0.01 | 4e-05 | 0.001 | 0.01 | 4e-05 | 0.001 | 0.01
| 3 (> 5,000) |  | 0.0005 | 0.0005 | 0.0005 | 4e-05 | 0.001 | 0.02 | 4e-05 | 0.001 | 0.02 | 4e-05 | 0.001 | 0.02
| 4 (> 25,000) |  | 0.0004 | 0.0004 | 0.0004 | 3e-05 | 0.001 | 0.02 | 3e-05 | 0.001 | 0.02 | 3e-05 | 0.001 | 0.02
| 5 (> 100,000) |  | 3e-06 | 3e-06 | 3e-06 | 3e-05 | 0.001 | 0.03 | 3e-05 | 0.001 | 0.03 | 3e-05 | 0.001 | 0.03
6 (> 500,000)
Bonnet Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzle | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
| 6 (> 500,000) | [6 empty] | 0.006 |  |  | 0.006 |  |  | 0.006
Flywheel | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 60 | 80 | 90 | 60 | 80 | 90 | 60 | 80 | 90
2 (> 1,500) |  |  |  |  | Total (input) | 60 | 80 | 90 | 60 | 80 | 90 | 60 | 80 | 90
3 (> 5,000) |  |  |  |  | Total (input) | 60 | 80 | 100 | 60 | 80 | 100 | 60 | 80 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 60 | 80 | 100 | 60 | 80 | 100 | 60 | 80 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Valves
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | surge line and hot leg | 6e-05 | 6e-05 | 6e-05 | 0.03 | 1 | 30 | 0.03 | 1 | 30 | 0.03 | 1 | 30
| 2 (> 1,500) |  | 5e-06 | 5e-06 | 5e-06 | 0.03 | 1 | 30 | 0.03 | 1 | 30 | 0.042 | 1.4 | 42
| 3 (> 5,000) |  | 2e-06 | 2e-06 | 2e-06 | 0.03 | 1 | 30 | 0.03 | 1 | 30 | 0.045 | 1.5 | 45
| 4 (> 25,000) |  | 3e-07 | 3e-07 | 3e-07 | 0.03 | 1 | 100 | 0.05 | 1.6667 | 166.6667 | 0.08 | 2.6667 | 266.6667
5 (> 100,000)
6 (> 500,000)
Bonnet Bolts | 1 (> 100) | surge line adjusted to get correct contribution | 6e-05 | 6e-05 | 6e-05 | 0.03 | 1 | 30 | 0.03 | 1 | 30 | 0.03 | 1 | 30
| 2 (> 1,500) |  | 5e-06 | 5e-06 | 5e-06 | 0.03 | 1 | 30 | 0.03 | 1 | 30 | 0.042 | 1.4 | 42
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Bonnet | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
| 6 (> 500,000) | [6 empty] | 0.006 |  |  | 0.006 |  |  | 0.006
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 30 | 60 | 95 | 30 | 60 | 95 | 30 | 60 | 95
2 (> 1,500) |  |  |  |  | Total (input) | 60 | 80 | 100 | 60 | 80 | 100 | 60 | 80 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 60 | 80 | 100 | 60 | 80 | 100 | 60 | 80 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 50 | 80 | 100 | 50 | 80 | 100 | 50 | 80 | 100
Total Percent Contributions all Components
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100

## Participant D
Participant D
Reactor Pressure Vessel
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | Lydell's BWR-1 values | 3.1667e-06 | 9.5e-06 | 2.85e-05 | 0.11 | 0.176 | 0.44 | 0.11 | 0.22 | 0.44 | 0.1025 | 0.23 | 0.59
| 2 (> 1,500) |  | 4e-07 | 1.2e-06 | 3.6e-06 | 0.11 | 0.176 | 0.44 | 0.11 | 0.22 | 0.44 | 0.1025 | 0.23 | 0.59
| 3 (> 5,000) |  | 1.5333e-07 | 4.6e-07 | 1.38e-06 | 0.17 | 0.34 | 0.68 | 0.14 | 0.27 | 0.76 | 0.11 | 0.22 | 0.44
| 4 (> 25,000) |  | 5e-08 | 1.5e-07 | 4.5e-07 | 0.17 | 0.34 | 0.68 | 0.14 | 0.27 | 0.76 | 0.11 | 0.22 | 0.44
| 5 (> 100,000) |  | 1e-08 | 3e-08 | 9e-08 | 0.17 | 0.34 | 0.68 | 0.14 | 0.27 | 0.76 | 0.11 | 0.22 | 0.44
| 6 (> 500,000) |  | 3.3333e-09 | 1e-08 | 3e-08 | 0.25 | 0.5 | 1 | 0.18 | 0.35 | 1 | 0.15 | 0.3 | 0.6
CRDM | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
CRDM Connections | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzles | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
In-Core Instrumentation | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Head Bolts | 1 (> 100) | Lydell's BWR-1 values | 3.1667e-06 | 9.5e-06 | 2.85e-05 | 0.033 | 0.0561 | 0.099 | 0.0165 | 0.033 | 0.066 | 0.004125 | 0.0165 | 0.066
| 2 (> 1,500) |  | 4e-07 | 1.2e-06 | 3.6e-06 | 0.033 | 0.0561 | 0.099 | 0.0165 | 0.033 | 0.066 | 0.004125 | 0.0165 | 0.066
| 3 (> 5,000) |  | 1.5333e-07 | 4.6e-07 | 1.38e-06 | 0.0495 | 0.099 | 0.165 | 0.033 | 0.066 | 0.132 | 0.033 | 0.0495 | 0.099
| 4 (> 25,000) |  | 5e-08 | 1.5e-07 | 4.5e-07 | 0.0495 | 0.099 | 0.165 | 0.033 | 0.066 | 0.132 | 0.033 | 0.0495 | 0.099
| 5 (> 100,000) |  | 1e-08 | 3e-08 | 9e-08 | 0.0495 | 0.099 | 0.165 | 0.033 | 0.066 | 0.132 | 0.033 | 0.0495 | 0.099
| 6 (> 500,000) |  | 3.3333e-09 | 1e-08 | 3e-08 | 0.15 | 0.3 | 0.5 | 0.1 | 0.2 | 0.4 | 0.1 | 0.15 | 0.3
Other penetrations | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Pumps
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | Lydell's BWR-1 values | 3.1667e-06 | 9.5e-06 | 2.85e-05 | 0.045 | 0.072 | 0.18 | 0.045 | 0.09 | 0.18 | 0.03 | 0.08 | 0.205
| 2 (> 1,500) |  | 4e-07 | 1.2e-06 | 3.6e-06 | 0.045 | 0.072 | 0.18 | 0.045 | 0.09 | 0.18 | 0.03 | 0.08 | 0.205
| 3 (> 5,000) |  | 1.5333e-07 | 4.6e-07 | 1.38e-06 | 0.065 | 0.13 | 0.26 | 0.06 | 0.115 | 0.32 | 0.045 | 0.09 | 0.18
| 4 (> 25,000) |  | 5e-08 | 1.5e-07 | 4.5e-07 | 0.065 | 0.13 | 0.26 | 0.06 | 0.115 | 0.32 | 0.045 | 0.09 | 0.18
| 5 (> 100,000) |  | 1e-08 | 3e-08 | 9e-08 | 0.065 | 0.13 | 0.26 | 0.06 | 0.115 | 0.32 | 0.045 | 0.09 | 0.18
6 (> 500,000)
Bonnet Bolts | 1 (> 100) | Lydell's BWR-1 values | 3.1667e-06 | 9.5e-06 | 2.85e-05 | 0.033 | 0.0561 | 0.099 | 0.0165 | 0.033 | 0.066 | 0.004125 | 0.0165 | 0.066
| 2 (> 1,500) |  | 4e-07 | 1.2e-06 | 3.6e-06 | 0.033 | 0.0561 | 0.099 | 0.0165 | 0.033 | 0.066 | 0.004125 | 0.0165 | 0.066
| 3 (> 5,000) |  | 1.5333e-07 | 4.6e-07 | 1.38e-06 | 0.0495 | 0.099 | 0.165 | 0.033 | 0.066 | 0.132 | 0.033 | 0.0495 | 0.099
| 4 (> 25,000) |  | 5e-08 | 1.5e-07 | 4.5e-07 | 0.0495 | 0.099 | 0.165 | 0.033 | 0.066 | 0.132 | 0.033 | 0.0495 | 0.099
| 5 (> 100,000) |  | 1e-08 | 3e-08 | 9e-08 | 0.0495 | 0.099 | 0.165 | 0.033 | 0.066 | 0.132 | 0.033 | 0.0495 | 0.099
6 (> 500,000)
Nozzle | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Flywheel | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Valves
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | Lydell's BWR-1 values | 3.1667e-06 | 9.5e-06 | 2.85e-05 | 0.045 | 0.072 | 0.18 | 0.045 | 0.09 | 0.18 | 0.03 | 0.08 | 0.205
| 2 (> 1,500) |  | 4e-07 | 1.2e-06 | 3.6e-06 | 0.045 | 0.072 | 0.18 | 0.045 | 0.09 | 0.18 | 0.03 | 0.08 | 0.205
| 3 (> 5,000) |  | 1.5333e-07 | 4.6e-07 | 1.38e-06 | 0.065 | 0.13 | 0.26 | 0.06 | 0.115 | 0.32 | 0.045 | 0.09 | 0.18
| 4 (> 25,000) |  | 5e-08 | 1.5e-07 | 4.5e-07 | 0.065 | 0.13 | 0.26 | 0.06 | 0.115 | 0.32 | 0.045 | 0.09 | 0.18
| 5 (> 100,000) |  | 1e-08 | 3e-08 | 9e-08 | 0.065 | 0.13 | 0.26 | 0.06 | 0.115 | 0.32 | 0.045 | 0.09 | 0.18
6 (> 500,000)
Bonnet Bolts | 1 (> 100) | Lydell's BWR-1 values | 3.1667e-06 | 9.5e-06 | 2.85e-05 | 0.033 | 0.0561 | 0.099 | 0.0165 | 0.033 | 0.066 | 0.004125 | 0.0165 | 0.066
| 2 (> 1,500) |  | 4e-07 | 1.2e-06 | 3.6e-06 | 0.033 | 0.0561 | 0.099 | 0.0165 | 0.033 | 0.066 | 0.004125 | 0.0165 | 0.066
| 3 (> 5,000) |  | 1.5333e-07 | 4.6e-07 | 1.38e-06 | 0.0495 | 0.099 | 0.165 | 0.033 | 0.066 | 0.132 | 0.033 | 0.0495 | 0.099
| 4 (> 25,000) |  | 5e-08 | 1.5e-07 | 4.5e-07 | 0.0495 | 0.099 | 0.165 | 0.033 | 0.066 | 0.132 | 0.033 | 0.0495 | 0.099
| 5 (> 100,000) |  | 1e-08 | 3e-08 | 9e-08 | 0.0495 | 0.099 | 0.165 | 0.033 | 0.066 | 0.132 | 0.033 | 0.0495 | 0.099
6 (> 500,000)
Bonnet | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Total Percent Contributions all Components
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 70 | 95 | 100 | 65 | 90 | 100 | 65 | 90 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 70 | 95 | 100 | 65 | 90 | 100 | 65 | 90 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 50 | 95 | 100 | 45 | 90 | 100 | 40 | 90 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 50 | 95 | 100 | 45 | 90 | 100 | 40 | 90 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 50 | 95 | 100 | 45 | 90 | 100 | 40 | 90 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 50 | 95 | 100 | 45 | 90 | 100 | 40 | 90 | 100

## Participant E
Partcipant E
Reactor Pressure Vessel
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | CRDM nozzle leaks from non-piping database.
2 (> 1,500)
| 3 (> 5,000) |  | 0.0033333 | 0.01 | 0.03 | 5e-06 | 0.0001 | 0.001 | 5e-06 | 0.0001 | 0.001 | 5e-06 | 0.0001 | 0.001
| 4 (> 25,000) |  | 0.0033333 | 0.01 | 0.03 | 1e-07 | 1e-05 | 0.0001 | 1e-07 | 1e-05 | 0.0001 | 1e-07 | 1e-05 | 0.0001
| 5 (> 100,000) |  | 0.0033333 | 0.01 | 0.03 | 2e-09 | 1e-06 | 5e-05 | 2e-09 | 1e-06 | 5e-05 | 2e-09 | 1e-06 | 5e-05
| 6 (> 500,000) |  | 0.0033333 | 0.01 | 0.03 | 5e-10 | 1e-07 | 5e-06 | 5e-10 | 1e-07 | 5e-06 | 5e-10 | 1e-07 | 5e-06
CRDM | 1 (> 100) | CRDM nozzle leaks from non-piping database. | 0.0033333 | 0.01 | 0.03 | 0.0015 | 0.0075 | 0.015 | 0.0015 | 0.0075 | 0.015 | 0.0015 | 0.0075 | 0.015
| 2 (> 1,500) |  | 0.0033333 | 0.01 | 0.03 | 5e-05 | 0.001 | 0.005 | 5e-05 | 0.001 | 0.005 | 5e-05 | 0.001 | 0.005
| 3 (> 5,000) |  | 0.0033333 | 0.01 | 0.03 | 1.315e-06 | 2.63e-05 | 0.000263 | 1.315e-06 | 2.63e-05 | 0.000263 | 1.315e-06 | 2.63e-05 | 0.000263
| 4 (> 25,000) |  | 0.0033333 | 0.01 | 0.03 | 1e-10 | 1e-08 | 1e-07 | 1e-10 | 1e-08 | 1e-07 | 1e-10 | 1e-08 | 1e-07
5 (> 100,000)
6 (> 500,000)
CRDM Connections | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzles | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
In-Core Instrumentation | 1 (> 100) | CRDM nozzle leaks from non-piping database. | 0.0033333 | 0.01 | 0.03 | 0.00025 | 0.00125 | 0.0025 | 0.00025 | 0.00125 | 0.0025 | 0.00025 | 0.00125 | 0.0025
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Head Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Other penetrations | 1 (> 100) | CRDM nozzle leaks from non-piping database. | 0.0033333 | 0.01 | 0.03 | 0.00025 | 0.00125 | 0.0025 | 0.00025 | 0.00125 | 0.0025 | 0.00025 | 0.00125 | 0.0025
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Pumps
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Bonnet Bolts | 1 (> 100) | % contribution | 0.0033333 | 0.01 | 0.03 | 0.00011111 | 0.00055556 | 0.0011111 | 0.00011111 | 0.00055556 | 0.0011111 | 0.00011111 | 0.00055556 | 0.0011111
| 2 (> 1,500) |  | 0.0033333 | 0.01 | 0.03 | 2.7778e-06 | 5.5556e-05 | 0.00027778 | 2.7778e-06 | 5.5556e-05 | 0.00027778 | 2.7778e-06 | 5.5556e-05 | 0.00027778
| 3 (> 5,000) |  | 0.0033333 | 0.01 | 0.03 | 1e-05 | 0.0002 | 0.002 | 1e-05 | 0.0002 | 0.002 | 1e-05 | 0.0002 | 0.002
| 4 (> 25,000) |  | 0.0033333 | 0.01 | 0.03 | 3.3333e-08 | 3.3333e-06 | 3.3333e-05 | 3.3333e-08 | 3.3333e-06 | 3.3333e-05 | 3.3333e-08 | 3.3333e-06 | 3.3333e-05
5 (> 100,000)
6 (> 500,000)
Nozzle | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Flywheel | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Valves
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Bonnet Bolts | 1 (> 100) | % contribution | 0.0033333 | 0.01 | 0.03 | 0.00011111 | 0.00055556 | 0.0011111 | 0.00011111 | 0.00055556 | 0.0011111 | 0.00011111 | 0.00055556 | 0.0011111
| 2 (> 1,500) |  | 0.0033333 | 0.01 | 0.03 | 2.7778e-06 | 5.5556e-05 | 0.00027778 | 2.7778e-06 | 5.5556e-05 | 0.00027778 | 2.7778e-06 | 5.5556e-05 | 0.00027778
| 3 (> 5,000) |  | 0.0033333 | 0.01 | 0.03 | 1e-05 | 0.0002 | 0.002 | 1e-05 | 0.0002 | 0.002 | 1e-05 | 0.0002 | 0.002
| 4 (> 25,000) |  | 0.0033333 | 0.01 | 0.03 | 3.3333e-08 | 3.3333e-06 | 3.3333e-05 | 3.3333e-08 | 3.3333e-06 | 3.3333e-05 | 3.3333e-08 | 3.3333e-06 | 3.3333e-05
5 (> 100,000)
6 (> 500,000)
Bonnet | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Total Percent Contributions all Components
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 70 | 90 | 95 | 50 | 85 | 95 | 50 | 85 | 95
2 (> 1,500) |  |  |  |  | Total (input) | 70 | 90 | 95 | 50 | 85 | 95 | 50 | 85 | 95
3 (> 5,000) |  |  |  |  | Total (input) | 50 | 80 | 90 | 40 | 80 | 90 | 40 | 80 | 90
4 (> 25,000) |  |  |  |  | Total (input) | 50 | 80 | 90 | 40 | 80 | 90 | 40 | 80 | 90
5 (> 100,000) |  |  |  |  | Total (input) | 40 | 80 | 90 | 40 | 80 | 90 | 40 | 80 | 90
6 (> 500,000) |  |  |  |  | Total (input) | 40 | 80 | 90 | 40 | 80 | 90 | 40 | 80 | 90

## Participant F
Participant F
Reactor Pressure Vessel
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | geometric average of Bill and Bengt's updated Cat. 5 base case estimates; uncertainties are a small factor of 3.
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
| 6 (> 500,000) |  | 4.2032e-08 | 1.261e-07 | 3.7829e-07 | 0.00025 | 0.01 | 0.4 | 0.000125 | 0.01 | 0.8 | 8.3333e-05 | 0.01 | 1.2
CRDM | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
CRDM Connections | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzles | 1 (> 100) | geometric average of Bill and Bengt's updated base case estimates; uncertainties are a small factor of 3. | 7.4796e-06 | 2.2439e-05 | 6.7316e-05 | 0.0033333 | 0.01 | 0.03 | 0.002 | 0.01 | 0.05 | 0.001 | 0.01 | 0.1
| 2 (> 1,500) |  | 1.4606e-06 | 4.3818e-06 | 1.3145e-05 | 0.0011111 | 0.01 | 0.09 | 0.00066667 | 0.01 | 0.15 | 0.00033333 | 0.01 | 0.3
| 3 (> 5,000) |  | 5.2047e-07 | 1.5614e-06 | 4.6842e-06 | 0.001 | 0.01 | 0.1 | 0.0005 | 0.01 | 0.2 | 0.00025 | 0.01 | 0.4
| 4 (> 25,000) |  | 1.633e-07 | 4.899e-07 | 1.4697e-06 | 0.0005 | 0.01 | 0.2 | 0.00025 | 0.01 | 0.4 | 0.00016667 | 0.01 | 0.6
| 5 (> 100,000) |  | 4.2032e-08 | 1.261e-07 | 3.7829e-07 | 0.00025 | 0.01 | 0.4 | 0.000125 | 0.01 | 0.8 | 8.3333e-05 | 0.01 | 1.2
6 (> 500,000)
In-Core Instrumentation | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Head Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Other penetrations | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
Pumps
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | geometric average of Bill and Bengt's updated base case estimates; uncertainties are a small factor of 3. | 7.4796e-06 | 2.2439e-05 | 6.7316e-05 | 0.0016667 | 0.005 | 0.015 | 0.001 | 0.005 | 0.025 | 0.0005 | 0.005 | 0.05
| 2 (> 1,500) |  | 1.4606e-06 | 4.3818e-06 | 1.3145e-05 | 0.00055556 | 0.005 | 0.045 | 0.00033333 | 0.005 | 0.075 | 0.00016667 | 0.005 | 0.15
| 3 (> 5,000) |  | 5.2047e-07 | 1.5614e-06 | 4.6842e-06 | 0.0005 | 0.005 | 0.05 | 0.00025 | 0.005 | 0.1 | 0.000125 | 0.005 | 0.2
| 4 (> 25,000) |  | 1.633e-07 | 4.899e-07 | 1.4697e-06 | 0.00025 | 0.005 | 0.1 | 0.000125 | 0.005 | 0.2 | 8.3333e-05 | 0.005 | 0.3
| 5 (> 100,000) |  | 4.2032e-08 | 1.261e-07 | 3.7829e-07 | 0.000125 | 0.005 | 0.2 | 6.25e-05 | 0.005 | 0.4 | 4.1667e-05 | 0.005 | 0.6
6 (> 500,000)
Bonnet Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzle | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Flywheel | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
Valves
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | geometric average of Bill and Bengt's updated base case estimates; uncertainties are a small factor of 3. | 7.4796e-06 | 2.2439e-05 | 6.7316e-05 | 0.033333 | 0.1 | 0.3 | 0.02 | 0.1 | 0.5 | 0.01 | 0.1 | 1
| 2 (> 1,500) |  | 1.4606e-06 | 4.3818e-06 | 1.3145e-05 | 0.011111 | 0.1 | 0.9 | 0.0066667 | 0.1 | 1.5 | 0.0033333 | 0.1 | 3
| 3 (> 5,000) |  | 5.2047e-07 | 1.5614e-06 | 4.6842e-06 | 0.01 | 0.1 | 1 | 0.005 | 0.1 | 2 | 0.0025 | 0.1 | 4
| 4 (> 25,000) |  | 1.633e-07 | 4.899e-07 | 1.4697e-06 | 0.005 | 0.1 | 2 | 0.0025 | 0.1 | 4 | 0.0016667 | 0.1 | 6
| 5 (> 100,000) |  | 4.2032e-08 | 1.261e-07 | 3.7829e-07 | 0.0025 | 0.1 | 4 | 0.00125 | 0.1 | 8 | 0.00083333 | 0.1 | 12
6 (> 500,000)
Bonnet Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Bonnet | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 85 | 95 | 100 | 85 | 95 | 100 | 85 | 95 | 100
Total Percent Contributions all Components
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100

## Participant G
Participant G
Reactor Pressure Vessel
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | BWR-2 | 9.58e-09 | 4.79e-08 | 2.395e-07 | 0.07 | 0.35 | 1.75 | 0.074235 | 0.37117 | 1.8559 | 0.074676 | 0.37338 | 1.8669
| 2 (> 1,500) |  | 1.436e-09 | 7.18e-09 | 3.59e-08 | 0.07 | 0.35 | 1.75 | 0.074235 | 0.37117 | 1.8559 | 0.074676 | 0.37338 | 1.8669
| 3 (> 5,000) |  | 5.06e-10 | 2.53e-09 | 1.265e-08 | 0.07 | 0.35 | 1.75 | 0.074235 | 0.37117 | 1.8559 | 0.074676 | 0.37338 | 1.8669
| 4 (> 25,000) |  | 1.414e-10 | 7.07e-10 | 3.535e-09 | 0.07 | 0.35 | 1.75 | 0.074235 | 0.37117 | 1.8559 | 0.074676 | 0.37338 | 1.8669
| 5 (> 100,000) |  | 1.384e-11 | 6.92e-11 | 3.46e-10 | 0.07 | 0.35 | 1.75 | 0.074235 | 0.37117 | 1.8559 | 0.074676 | 0.37338 | 1.8669
| 6 (> 500,000) |  | 1.384e-11 | 6.92e-11 | 3.46e-10 | 0.04 | 0.2 | 1 | 0.04242 | 0.2121 | 1.0605 | 0.042672 | 0.21336 | 1.0668
CRDM | 1 (> 100) | BWR-1 | 2.7433e-06 | 8.23e-06 | 2.469e-05 | 0.016667 | 0.05 | 0.15 | 0.011519 | 0.057595 | 0.28797 | 0.00966 | 0.0966 | 0.966
| 2 (> 1,500) |  | 3.6e-07 | 1.08e-06 | 3.24e-06 | 0.016667 | 0.05 | 0.15 | 0.011519 | 0.057595 | 0.28797 | 0.00966 | 0.0966 | 0.966
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
CRDM Connections | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzles | 1 (> 100) | BWR-1 | 2.7433e-06 | 8.23e-06 | 2.469e-05 | 0.11667 | 0.35 | 1.05 | 0.080633 | 0.40316 | 2.0158 | 0.06762 | 0.6762 | 6.762
| 2 (> 1,500) |  | 3.6e-07 | 1.08e-06 | 3.24e-06 | 0.11667 | 0.35 | 1.05 | 0.080633 | 0.40316 | 2.0158 | 0.06762 | 0.6762 | 6.762
| 3 (> 5,000) |  | 1.3433e-07 | 4.03e-07 | 1.209e-06 | 0.07 | 0.35 | 1.75 | 0.040316 | 0.40316 | 4.0316 | 0.03381 | 0.6762 | 13.524
| 4 (> 25,000) |  | 4.3e-08 | 1.29e-07 | 3.87e-07 | 0.035 | 0.35 | 3.5 | 0.020158 | 0.40316 | 8.0633 | 0.02254 | 0.6762 | 20.286
| 5 (> 100,000) |  | 7.3e-09 | 2.19e-08 | 6.57e-08 | 0.035 | 0.35 | 3.5 | 0.020158 | 0.40316 | 8.0633 | 0.02254 | 0.6762 | 20.286
6 (> 500,000)
In-Core Instrumentation | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Head Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Other penetrations | 1 (> 100) | BWR-1 | 2.7433e-06 | 8.23e-06 | 2.469e-05 | 0.033333 | 0.1 | 0.3 | 0.023038 | 0.11519 | 0.57595 | 0.01932 | 0.1932 | 1.932
| 2 (> 1,500) |  | 3.6e-07 | 1.08e-06 | 3.24e-06 | 0.033333 | 0.1 | 0.3 | 0.023038 | 0.11519 | 0.57595 | 0.01932 | 0.1932 | 1.932
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 75 | 90 | 100 | 75 | 90 | 100 | 75 | 90 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 75 | 90 | 100 | 75 | 90 | 100 | 75 | 90 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 75 | 90 | 100 | 75 | 90 | 100 | 75 | 90 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 75 | 90 | 100 | 75 | 90 | 100 | 75 | 90 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 75 | 90 | 100 | 75 | 90 | 100 | 75 | 90 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 75 | 90 | 100 | 75 | 90 | 100 | 75 | 90 | 100
Pumps
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | BWR-2 | 1.5967e-08 | 4.79e-08 | 1.437e-07 | 0.066667 | 0.2 | 0.6 | 0.04242 | 0.2121 | 1.0605 | 0.021336 | 0.21336 | 2.1336
| 2 (> 1,500) |  | 2.3933e-09 | 7.18e-09 | 2.154e-08 | 0.066667 | 0.2 | 0.6 | 0.04242 | 0.2121 | 1.0605 | 0.021336 | 0.21336 | 2.1336
| 3 (> 5,000) |  | 8.4333e-10 | 2.53e-09 | 7.59e-09 | 0.04 | 0.2 | 1 | 0.02121 | 0.2121 | 2.121 | 0.010668 | 0.21336 | 4.2672
| 4 (> 25,000) |  | 2.36e-10 | 7.08e-10 | 2.124e-09 | 0.02 | 0.2 | 2 | 0.010605 | 0.2121 | 4.242 | 0.007112 | 0.21336 | 6.4008
| 5 (> 100,000) |  | 2.3067e-11 | 6.92e-11 | 2.076e-10 | 0.02 | 0.2 | 2 | 0.010605 | 0.2121 | 4.242 | 0.007112 | 0.21336 | 6.4008
6 (> 500,000)
Bonnet Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzle | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Flywheel | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 75 | 90 | 100 | 75 | 90 | 100 | 75 | 90 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 75 | 90 | 100 | 75 | 90 | 100 | 75 | 90 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 75 | 90 | 100 | 75 | 90 | 100 | 75 | 90 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 75 | 90 | 100 | 75 | 90 | 100 | 75 | 90 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 75 | 90 | 100 | 75 | 90 | 100 | 75 | 90 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 75 | 90 | 100 | 75 | 90 | 100 | 75 | 90 | 100
Valves
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | BWR-2 | 1.5967e-08 | 4.79e-08 | 1.437e-07 | 0.033333 | 0.1 | 0.3 | 0.02121 | 0.10605 | 0.53025 | 0.010668 | 0.10668 | 1.0668
| 2 (> 1,500) |  | 2.3933e-09 | 7.18e-09 | 2.154e-08 | 0.033333 | 0.1 | 0.3 | 0.02121 | 0.10605 | 0.53025 | 0.010668 | 0.10668 | 1.0668
| 3 (> 5,000) |  | 8.4333e-10 | 2.53e-09 | 7.59e-09 | 0.02 | 0.1 | 0.5 | 0.010605 | 0.10605 | 1.0605 | 0.005334 | 0.10668 | 2.1336
| 4 (> 25,000) |  | 2.36e-10 | 7.08e-10 | 2.124e-09 | 0.01 | 0.1 | 1 | 0.0053025 | 0.10605 | 2.121 | 0.003556 | 0.10668 | 3.2004
| 5 (> 100,000) |  | 2.3067e-11 | 6.92e-11 | 2.076e-10 | 0.01 | 0.1 | 1 | 0.0053025 | 0.10605 | 2.121 | 0.003556 | 0.10668 | 3.2004
6 (> 500,000)
Bonnet Bolts | 1 (> 100) | BWR-2 | 1.5967e-08 | 4.79e-08 | 1.437e-07 | 0.033333 | 0.1 | 0.3 | 0.02121 | 0.10605 | 0.53025 | 0.010668 | 0.10668 | 1.0668
| 2 (> 1,500) |  | 2.3933e-09 | 7.18e-09 | 2.154e-08 | 0.033333 | 0.1 | 0.3 | 0.02121 | 0.10605 | 0.53025 | 0.010668 | 0.10668 | 1.0668
| 3 (> 5,000) |  | 8.4333e-10 | 2.53e-09 | 7.59e-09 | 0.02 | 0.1 | 0.5 | 0.010605 | 0.10605 | 1.0605 | 0.005334 | 0.10668 | 2.1336
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Bonnet | 1 (> 100) | BWR-2 | 1.5967e-08 | 4.79e-08 | 1.437e-07 | 0.033333 | 0.1 | 0.3 | 0.02121 | 0.10605 | 0.53025 | 0.010668 | 0.10668 | 1.0668
| 2 (> 1,500) |  | 2.3933e-09 | 7.18e-09 | 2.154e-08 | 0.033333 | 0.1 | 0.3 | 0.02121 | 0.10605 | 0.53025 | 0.010668 | 0.10668 | 1.0668
| 3 (> 5,000) |  | 8.4333e-10 | 2.53e-09 | 7.59e-09 | 0.02 | 0.1 | 0.5 | 0.010605 | 0.10605 | 1.0605 | 0.005334 | 0.10668 | 2.1336
4 (> 25,000)
5 (> 100,000)
| 6 (> 500,000) | [6 empty] | 0.006 |  |  | 0.006 |  |  | 0.006
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 75 | 100 | 100 | 75 | 100 | 100 | 75 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 75 | 100 | 100 | 75 | 100 | 100 | 75 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 75 | 100 | 100 | 75 | 100 | 100 | 75 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 75 | 100 | 100 | 75 | 100 | 100 | 75 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 75 | 100 | 100 | 75 | 100 | 100 | 75 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 75 | 100 | 100 | 75 | 100 | 100 | 75 | 100 | 100
Total Percent Contributions all Components
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100

## Participant H
Participant H
Reactor Pressure Vessel
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100) | Calculated from BWR piping total contributions
2 (> 1,500)
| 3 (> 5,000) |  | 2.5466e-06 | 7.6399e-06 | 2.292e-05 | 1e-05 | 0.001 | 0.1 | 4.6391e-05 | 0.0046391 | 0.46391 | 1.1439e-05 | 0.011439 | 11.4387
| 4 (> 25,000) |  | 2.397e-07 | 7.1909e-07 | 2.1573e-06 | 1e-05 | 0.001 | 0.1 | 5.3151e-05 | 0.0053151 | 0.53151 | 2.0951e-05 | 0.020951 | 20.9512
| 5 (> 100,000) |  | 7.4856e-08 | 2.2457e-07 | 6.737e-07 | 1e-05 | 0.001 | 0.1 | 4.5552e-05 | 0.0045552 | 0.45552 | 1.786e-05 | 0.01786 | 17.8601
| 6 (> 500,000) |  | 2.9363e-10 | 8.8088e-10 | 2.6426e-09 | 1e-06 | 0.0001 | 0.01 | 5.0949e-06 | 0.00050949 | 0.050949 | 3.4965e-06 | 0.0034965 | 3.4965
CRDM | 1 (> 100) | Pete Riccardella's estimates for PWR CRDMs | 0.00025 | 0.00025 | 0.00025 | 0.025 | 0.5 | 10 | 0.025 | 0.5 | 10 | 0.025 | 0.5 | 10
| 2 (> 1,500) |  | 0.00025 | 0.00025 | 0.00025 | 0.025 | 0.5 | 10 | 0.025 | 0.5 | 10 | 0.025 | 0.5 | 10
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
CRDM Connections | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzles | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
In-Core Instrumentation | 1 (> 100) | BWR piping probabilities | 5.5826e-05 | 0.00016748 | 0.00050243 | 0.1 | 1 | 10 | 0.37716 | 3.7716 | 37.7164 | 0.13026 | 13.0256 | 1302.5599
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Head Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Other penetrations | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Pumps
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Bonnet Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Nozzle | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Flywheel | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Valves
Component | LOCA Category (gpm) | Base Case | LOCA Frequency for System |  |  | 25 Years of Plant Operation |  |  | 40 Years of Plant Operation |  |  | 60 Years of Plant Operation
|  |  | 5% LB (cal-yr-1) | Mid Value (cal-yr-1) | 5% UB (cal-yr-1) | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio | 5% LB Ratio | Mid Value Ratio | 5% UB Ratio
Body | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Bonnet Bolts | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
Bonnet | 1 (> 100)
2 (> 1,500)
3 (> 5,000)
4 (> 25,000)
5 (> 100,000)
6 (> 500,000)
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
2 (> 1,500) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
3 (> 5,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 (> 25,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 (> 100,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
6 (> 500,000) |  |  |  |  | Total (input) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Total Percent Contributions all Components
LOCA Category (gpm) | [5 empty] | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%) | 5% LB (%) | Mid Value (%) | 5% UB (%)
1 (> 100) |  |  |  |  | Total (input) | 70 | 80 | 90 | 70 | 80 | 90 | 70 | 80 | 90
2 (> 1,500) |  |  |  |  | Total (input) | 70 | 80 | 90 | 70 | 80 | 90 | 70 | 80 | 90
3 (> 5,000) |  |  |  |  | Total (input) | 70 | 80 | 90 | 70 | 80 | 90 | 70 | 80 | 90
4 (> 25,000) |  |  |  |  | Total (input) | 70 | 80 | 90 | 70 | 80 | 90 | 70 | 80 | 90
5 (> 100,000) |  |  |  |  | Total (input) | 70 | 80 | 90 | 70 | 80 | 90 | 70 | 80 | 90
6 (> 500,000) |  |  |  |  | Total (input) | 70 | 80 | 90 | 70 | 80 | 90 | 70 | 80 | 90