TENNESSEE VALLEY AUTHORITY

WATTS BAR NUCLEAR PLANT

CHEMISTRY MANUAL

CHAPTER 3.01

SYSTEM CHEMISTRY SPECIFICATIONS

Revision 30

Unit 0,1,2

QUALITY RELATED

PREPARED BY:		Keith Riggle

SPONSORING ORGANIZATION:		Chemistry

APPROVED BY:		Betsy Eiford-Lee		DATE:	3/8/01

EFFECTIVE DATE: 		3/9/01

LEVEL OF USE:	INFORMATION

REVISION LOG

| REVISION OR CHANGE NUMBER | EFFECTIVE DATE |  | AFFECTED PAGE NUMBERS |  | DESCRIPTION OF REVISION/CHANGE |
| --- | --- | --- | --- | --- | --- |
| Rev 29 | 11/22/00 | 1,2,7,8,21, 25, 26, 41 |  | This revision incorporates Amendment 22 to the Facility Operating License NPF-90. The change establishes ice condenser sampling frequency at 1/54 months and refers the performer to 1-SI-61-1 for ice condenser limits. Revises Appendix E to limit at temperature pH swings in the RCS to 0.05 pH units (WBPER 00-011278-000). Provides instruction for the utilization of the Computer Automated Laboratory System (CALS). Change the upper limit for condensate/feedwater pH from 10.0 to 10.5 to accommodate increased amines in the secondary systems. WBPER 00-015718. Intent Change. |  |
| Rev 30 | 3/9/01 | 1,2,5, 8,10, 14,15,16,22,23,24,26,29,30, 34,36 |  | Intent Change. WBPER 00-015001 addresses polisher rinse specs. Update method of making remarks for OOL parameters. Incorporate changes in rev 5 of EPRI PWR Secondary Water Chemistry Guidelines. Add admin target hydrazine of 25 ppm on chilled water systems. Make target for hydrazine in Aux Bldg Vent and TB heat systems 9 ppm. Remove limit for MIC from TN river. Remove TOC limit from the BAT and also from RCS. Correct minor errors. Listed TI-7.004 as a performance reference, revised the OOL notification to include use of CALS, changed PAI-7.04 to TI-7.004, and included a general note on RCS DGA and DEI explaining what is required by TI-7.004. |  |

TABLE OF CONTENTS

Section	Title	Page

1.0	INTRODUCTION	4

2.0	REFERENCES	5

3.0	PRECAUTIONS AND LIMITATIONS	5

4.0	PREREQUISITE ACTIONS	6

5.0	ACCEPTANCE CRITERIA	6

6.0	PERFORMANCE	6

7.0	POST PERFORMANCE ACTIVITY	12

8.0	RECORDS	12

APPENDIXES

Appendix A, Chemistry Specifications	13

Appendix B, Chemistry Logsheet	38

Appendix C, Chemistry Logsheet Remarks	39

Appendix D, Action Level Waiver	40

Appendix E, RCS Lithium Control	41

SOURCE NOTES	42

1.0	INTRODUCTION

1.1	Purpose

This instruction provides parameters, monitoring frequencies, specifications, corrective actions, and logsheets used to evaluate and document chemistry conditions in plant systems.  This program reflects the guidance presented in the EPRI PWR Secondary Water Chemistry Guidelines, PWR Primary Water Chemistry Guidelines, and PWR Primary to Secondary Leak Guidelines.

1.2	Scope

This instruction is applicable to plant systems that require sampling and monitoring during Modes 1 through 6 as well as no mode status.

1.3	Frequency and Conditions Source Note 11

Frequencies and conditions are listed in Appendix A.  The listed frequencies are applicable as follows:

A.	Frequencies required only if system contains normal system fluid.

B.	Frequencies applied as described with consideration of General Notes.

C.	Frequencies listed are minimum frequencies and are considered satisfied as long as performance is completed within the calendar day, week, month etc., as appropriate.  Efforts should be made to collect samples at regular intervals within the sampling frequency, e.g., daily samples should be collected at about the same time each day when possible.

- Documentation of deviation from sampling/analysis frequency requirements is detailed in Section 6.2.1.

E.	Sampling and analysis requirements for mode 6 are to be implemented when plant 	is in no mode status, as appropriate.

1.4	Description

The following is a list of appendixes found in this instruction and brief description of the information found in each appendix:

Appendix A, Chemistry Specifications contains specifications tables for primary, secondary and auxiliary systems’ chemistry control.  Included in the specification tables are “Control” parameter tables for Primary and Secondary, these are parameters which have associated plant actions (e.g. shutdown, cooldown etc.).

1.4	Description (Continued)

Appendix B, Chemistry Logsheet is the chemistry logsheet for parameter data recording.

Appendix C, Chemistry Logsheet Remarks is a form for recording remarks related to parameter data recorded on an Appendix B logsheet.

Appendix D, Action Level Waiver is a waiver form to be used to document planned acceptable deviation(s) to action level limits or their required corrective actions.

Appendix E, RCS Lithium Control contains the RCS lithium specifications.

2.0	REFERENCES

2.1	Performance References

A.	CM 5.04, “Condenser Inleakage Detection”.

- CM 6.02, “MIC Sampling”.

- 1-SI-61-1, “Determination of Boron and pH On Ice Condenser Ice”.

- 0-SI-77-3, “WDS Waste Gas Oxygen Determination”.

E.	TI-7.004, “Fuel Integrity Assessment Program”.

2.2	Developmental References

A.	EPRI TR-105714, “PWR Primary Water Chemistry Guidelines”.

- EPRI TR-102134, “PWR Secondary Water Chemistry Guidelines”.

- EPRI TR-104788, “PWR Primary-to-Secondary Leak Guidelines”.

D.	EPRI TR-107396, “Closed Cooling Water Chemistry Guideline”.

E.	SPP 9.7,  “Corrosion Control Program”.

2.3	Commitments

None.

3.0	PRECAUTIONS AND LIMITATIONS

None.

4.0	PREREQUISITE ACTIONS

None.

5.0	ACCEPTANCE CRITERIA

Acceptance Criteria are provided in Appendix A.

6.0	PERFORMANCE

NOTE 1	Forms generated by this procedure may be replaced by computer generated forms, provided that all principal attributes are retained.

NOTE 2	Sections 6.5 and 6.6 provide only general guidance for performance of Action Level Waivers and Technical Evaluations. These steps may be deviated from at the discretion of the individual performing the action.

6.1	Scheduling of Analysis

6.1.1	Chemistry Supervisor Responsibilities

[1]	ENSURE that the sampling and analysis requirements of this Instruction are consistently met.

NOTE	The abbreviations listed below are used in the Appendix A specification tables to define sample frequency requirements.  Additionally, the abbreviations may be used with a number of samples to be collected in the given frequency (e.g. 3/W would describe 3 samples per week, or 1/4M would describe 1 sample per 4 months)

ABBREVIATION	DEFINITION

(1)	C	Continuously Monitored (On-line)

(2)	Hr	Hourly

(3)	S	Shiftly

(4)	D	Daily

(5)	W	Weekly

(6)	M	Monthly

(7)	Q	Quarterly

(8)	SA	Semiannually

(9)	A	Annually

(10)	PR	Per Request

6.1.2	Radiochemistry Laboratory Analyst (RLA) Responsibilities

NOTE	Efforts should be made to collect samples at regular intervals within the sampling frequency, e.g., daily samples should be collected at about the same time each day when possible.

[1]	PERFORM sampling and analyses as specified in Appendix A, and

MAINTAIN an awareness of changing plant conditions that may affect sample frequency requirements.

6.2	Recording and Review of Analytical Results

6.2.1	Radiochemistry Laboratory Analyst (RLA) Responsibilities

NOTE	Typically analytical results will be recorded in the Computer Automated Laboratory System (CALS).  Parameters to be trended and the system to be trended, may be added to Appendix B as necessary.

[1]	RECORD analytical results as soon as practical in CALS, on the appropriate Appendix B Chemistry Logsheet and other datasheet, logsheet or laboratory journal, as appropriate.

[2]	EVALUATE the data for out-of-limit (OOL) conditions as well as for system trends.

[3]	REMARK in the CALS Comment Field or Notepad, and/or on Appendix C Chemistry Logsheet Remarks (as appropriate), results that are:

[a]	OOL.

[b]	Indicative of a significant increasing or decreasing trend if not previously noted.

[c]	Obtained from other than a normally used sample point.

6.2.1	Radiochemistry Laboratory Analyst (RLA) Responsibilities (Continued)

[4]	IF using Appendix C, THEN

DETERMINE the Remark # as follows:

[a]	USE two digit numbers for the year, month and day.

NOTE	The second comment entry for April 2, 2001 would be listed as 010402-02.

[b]	USE the next sequential number starting with -01 each day determined by reviewing the appropriate Chemistry Logsheet Remarks form.

[c]	ENSURE the remark is entered into CALS.

[5]	DOCUMENT a probable cause or statement that cause is unknown and actions taken or to be taken in CALS.

[6]	IF OOL Notification is required by the appropriate Appendix A Chemistry Specification table, THEN

PERFORM Out-Of-Limit Notification actions per Section 6.3.

NOTE	The CALS/Appendix C entry should include an explanation of the reason why the sampling/analysis requirement could not be met (e.g. systems may be out of service, clearances may be in place, etc.), actions ongoing to enable sampling, and other relevant information (e.g., WR number, hold order number, etc.).

[7]	IF a sampling/analysis requirement cannot be performed, THEN

RECORD relevant information in CALS, and/or on Appendix C Chemistry Logsheet Remarks (as appropriate), using Supervisory guidance.

6.2.2	Chemistry Supervisor Responsibilities

[1]	REVIEW chemistry results and OOL Notifications as soon as practical, and

TAKE appropriate follow-up action as necessary.

6.3	RLA Responsibilities for Out-of-Limit (OOL) Conditions Source Note 3

NOTE 1	The response to chemistry excursions is a series of progressive steps which are commensurate with the recognized potential for corrosion damage to plant equipment.  These responses are based upon typical plant values and industry accepted practices. Where appropriate, Limits and Actions Levels are consistent with Technical Specifications (TS), and the Technical Requirements (TR).

NOTE 2	The actions described below for OOL conditions are only required if directed by the Corrective Actions for the parameter from the appropriate Appendix A specification table. Additionally, if the General Notes provide additional latitude, an OOL notification may not be required.

[1]	IF results exceed the appropriate Limit value, THEN

[a]	EVALUATE the result against the system chemistry trends and plant conditions at the time of sampling, and

ASSESS any sampling or analytical errors that may have occurred.

[b]	IF the result was for a TS, TR, NPDES analysis, or exceeds an Action Level, THEN

IMMEDIATELY NOTIFY the Operations Unit Supervisor (US)/Shift Manager (SM) of the initial sample result, and

DISCUSS plans with the US/SM for confirmatory sampling 
(follow-up sampling).

[c]	EVALUATE the need for a follow-up sample, and

OBTAIN sample(s) as appropriate.

NOTE	Notification of confirmed OOL conditions typically include discussion of the probable cause for the condition and  recommended corrective actions.

6.2.1	Radiochemistry Laboratory Analyst (RLA) Responsibilities (Continued)

[d]	IF the result is confirmed to be OOL, THEN

NOTIFY the US/SM of the OOL condition, and

RECORD in CALS, and/or on Appendix C Chemistry Logsheet Remarks (as appropriate) the person notified and details discussed related to probable cause and recommended corrective actions, and

CIRCLE the OOL result in red if using Appendix B Chemistry  Logsheet.

NOTE	The decision as to how to notify the Chemistry Supervisor, is based upon the RLA's judgment with consideration given to the severity of the condition.

[e]	NOTIFY the appropriate Chemistry Supervisor of the OOL condition by telephone, pager, by the normal data review, or other method as appropriate for the severity of the condition.

NOTE	The decision as to the appropriate corrective actions for an OOL is  based upon the RLA's judgment with consideration given to the severity of the condition or other pertinent factors.

[f]	PERFORM appropriate recommended corrective action(s) in accordance with the Appendix A 	specification table for the OOL parameter, actions as directed by Chemistry Supervision or other corrective action as appropriate.

NOTE	Two consecutive follow-up samples are typically appropriate to clear an OOL unless otherwise directed by the Chemistry Supervisor.

[g]	NOTIFY the US/SM that the OOL parameter is within limits when appropriate follow-up samples indicate that the parameter is within limits.

6.4	RLA Responsibilities for Parameters Exceeding Action Level (AL) Limits

NOTE	Action Levels may only be waived if the waiver is recommended by the Chemistry Superintendent and approved by the Plant Manager in accordance with section 6.5.

[1]	RECORD the time the sample was obtained that identified the Action Level condition as Action Level time of initiation in the Laboratory Journal.

[2]	PERFORM notifications in accordance with the appropriate Appendix A specification table, and

RECORD the name of the US/SM notified in the Chemistry Logbook.

[3]	INCREASE the surveillance frequency depending upon the severity of the excursion or as directed by the appropriate Chemistry Supervisor.

6.5	Action Level Waivers

NOTE	Action Level Waivers may be completed and approved via telephone conference call.

6.5.1	Chemistry Superintendent Responsibilities

[1]	IF an Action Level Limit has been exceeded and the corrective action(s) are to be waived, THEN

PERFORM the following:

[a]	RECORD the Action Level Parameter, Action Level, relevant Action Level Limit, Action Level Time of Initiation, the most recent result for the Action Level parameter and the Trend for the Action Level parameter on an Appendix D Action Level Waiver form.

[b]	DESCRIBE the justification for waiving corrective action(s).

[c]	SIGN the Action Level Waiver Recommendation line, and

FORWARD to the Plant Manager (or designee) for approval.

6.5.2	Plant Manager (or designee) Responsibilities

[1]	DISCUSS Action Level condition with Chemistry personnel as necessary, and

DETERMINE whether waiver is approved.

[2]	IF the Action Level Waiver is approved, THEN

SIGN the Action Level Waiver Approval.

6.6	Technical Evaluation

6.6.1	Chemistry Supervisor Responsibilities

[1]	PERFORM technical evaluation as directed by the appropriate Appendix A specification table, and

INCLUDE the following as appropriate:

[a]	A description of the consequences of continued operation with Action Level condition.

[b]	An impact review on system materials by Nuclear Engineering.

[c]	Summary of discussion with technical experts (i.e. INPO personnel, Westinghouse representatives, other vendor technical experts etc.).

[2]	FORWARD the technical evaluation to the Chemistry Superintendent for review.

7.0	POST PERFORMANCE ACTIVITY

None.

8.0	RECORDS

8.1	QA Records

Appendixes B, C and D are QA records and are processed in accordance with SPP-2.4, Records Management.

8.2	Non-QA Records

None

| APPENDIX A CHEMISTRY SPECIFICATIONS - PRIMARY CHEMISTRY - RCS CONTROL PARAMETERS |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| RCS Power Operation (Reactor Critical) |  |  |  |  |  |  |  |  |
| Parameter | Action Level 1 | Action Level 1 Corrective Actions | Action Level 2 | Action Level 2 Corrective Actions | Action Level 3 | Action Level 3 Corrective Actions | Frequency |  |
| Fluoride, ppb | >50 ppb | 1,2 | >150 ppb | 1,3 | >1500 ppb | 1,4 | 3/W |  |
| Chloride, ppb | >50 ppb | 1,2 | >150 ppb | 1,3 | >1500 ppb | 1,4 | 3/W |  |
| Sulfate, ppb | >50 ppb | 1,2 | >150 ppb | 1,3 | >1500 ppb | 1,4 | 3/W |  |
| Lithium, ppm | In Accordance with Appendix E a | 1,2 |  |  |  |  | D |  |
| Dissolved Oxygen, ppb | >5 ppb | 1,2 |  |  | >100 ppb | 1,4 | 3/W |  |
| Dissolved Hydrogen cc(@STP)/Kg H2O | <25 or >50 cc(@STP)/Kg H2O | 1,2 e | <15 cc(@STP)/Kg H2O | 1,3 b | <5 cc(@STP)/Kg H2O | 1,4 | 3/W |  |
| RCS Cold Shutdown (Reactor < 250F) |  |  |  |  | RCS Startup (Reactor Subcritical and >250F) |  |  |  |
| Parameter | Value Prior to Exceeding 180 F | Value Prior to Exceeding 250 F | Frequency |  | Parameter | Value Prior to Criticality | Frequency |  |
| Fluoride, ppb |  | 150 ppb | 3/W |  | Fluoride, ppb | 150 ppb | 3/W |  |
| Chloride, ppb |  | 150 ppb | 3/W |  | Chloride, ppb | 150 ppb | 3/W |  |
| Sulfate, ppb |  | 150 ppb | 3/W |  | Sulfate, ppb | 150 ppb | 3/W |  |
| Dissolved Oxygen, ppb | 2000 ppb | 100 ppb | 3/W |  | Dissolved Oxygen, ppb | 100 ppb | 3/W d |  |
| Dissolved Hydrogen cc(@STP)/Kg H2O |  |  | 3/W c |  | Dissolved Hydrogen cc(@STP)/Kg H2O | 15 cc(@STP)/Kg H2O | 3/W c |  |
| RCS Pressurizer |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Value Prior to Exceeding 250 F Pressurizer Temperature |  |  |  |  |
| Dissolved Oxygen, ppb | <100 | D f | 1,5 | <100 |  |  |  |  |
| Corrective Actions |  |  |  |  | General Notes |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  | a. Apply Appendix E limits, after establishing lithium control (established within 24 hours of criticality). |  |  |  |
| 2. If the parameter has not been restored within seven days, a technical review should be performed and a program for implementing corrective measures instituted. |  |  |  |  | b. Corrective action and technical evaluation should be performed, but no plant shutdown is required. |  |  |  |
| 3. If the parameter has not been restored to within AL2 limits within 24 hours, an orderly shutdown should be initiated and the plant should be brought to a cold shutdown as quickly as permitted by other plant constraints. If the parameter is restored to within AL2 limits prior to shutdown, full power operation may be resumed. Following a unit shutdown caused by exceeding the time limit on AL 2, a technical review should be performed and appropriate corrective measures taken before the unit is restarted. |  |  |  |  | c. Frequency only applies after hydrogen overpressure has been placed on the VCT (hydrogen addition established). |  |  |  |
| 4. An orderly unit shutdown should be initiated immediately with reduction of RCS temperature to < 250 F as rapidly as other plant constraints permit. Following unit shutdown caused by entering AL 3 condition, a technical review should be performed and appropriate corrective measures taken before the unit is restarted. If chemistry is improved to within requirements of AL3 limits prior to plant shutdown, power operation may be resumed, subject to the requirements of other Action Levels and plant Technical Specifications/Requirements. |  |  |  |  | d. Frequency only applies after heatup above ambient temperature has begun. |  |  |  |
| 5. Add hydrazine as necessary to reduce concentration. |  |  |  |  | e. Hydrogen levels may be reduced to 15 cc/kg 24 hours before shutdown without instituting AL 1. |  |  |  |
|  |  |  |  |  | f. Frequency applies after heatup above ambient temperature has began. Monitoring can be terminated when specification is met. |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - PRIMARY CHEMISTRY - RCS CHEMISTRY DIAGNOSTIC PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MODES 1 & 2 |  |  |  |  | MODES 3 & 4 |  |  |  |  |  | MODES 5 & 6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit |  | Frequency | Corrective Actions | Limit | Frequency | Corrective Actions |  |  |  |  |  |  |  |  |  |  |
| Boron, ppm | As Required e for Reactivity Control | D | 1 | As Required e for Reactivity Control |  | D | 1 | As Required e for Reactivity Control | D | 1 |  |  |  |  |  |  |  |  |  |  |
| Lithium, ppm a |  |  |  | 1 - 3.50 ppm 1.5 ppm target a |  | D | 1,6,7 |  | W |  |  |  |  |  |  |  |  |  |  |  |
| Conductivity, S/cm @ 25C | 10% of Calc. Conductivity | D | 2 | 10% of Calc. Conductivity |  | D | 2 |  | D |  |  |  |  |  |  |  |  |  |  |  |
| Calc. Conductivity, S/cm @ 25C |  | D |  |  |  | D |  |  | D |  |  |  |  |  |  |  |  |  |  |  |
| pH @ 25C |  0.2 of Calc. pH | D | 2 | 0.2 of Calc. pH |  | D | 2 |  | D |  |  |  |  |  |  |  |  |  |  |  |
| Calculated pH @ 25C |  | D |  |  |  | D |  |  | D |  |  |  |  |  |  |  |  |  |  |  |
| Letdown Flow, gpm |  | D |  |  |  | D |  |  | D |  |  |  |  |  |  |  |  |  |  |  |
| RCS Tave, F |  | D |  |  |  | D |  |  | D |  |  |  |  |  |  |  |  |  |  |  |
| pH @ RCS Tave |  | D |  |  |  | D |  |  | D |  |  |  |  |  |  |  |  |  |  |  |
| Sodium, ppb | 50 ppb | M | 1,3,4,5 | 50 ppb |  | M | 1,3,4,5 | 50 ppb | M | 1,3,4,5 |  |  |  |  |  |  |  |  |  |  |
| TSS as Iron Oxide, ppb | 10 ppb | W | 2,3 | 350 ppb |  | W | 2 | 350 ppb | W | 2 |  |  |  |  |  |  |  |  |  |  |
| Silica, ppb | 1000 ppb | W | 1,4,5 | 1000 ppb |  | W | 1,4,5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TOC, ppb |  | PR |  |  |  | PR |  |  | PR |  |  |  |  |  |  |  |  |  |  |  |
| Ammonia, ppb | 500 ppb | PR | 2 | 500 ppb |  | PR | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydrazine, ppm b,d |  |  |  |  |  |  |  | 2 X RCS DO | 2/D | 2,6 |  |  |  |  |  |  |  |  |  |  |
| Hydrogen Peroxide, ppm c,d |  |  |  |  |  |  |  | 0.1 - 10 ppm 5 ppm target | 2/D | 2,6 |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  | a. Lithium is a control parameter in Modes 1 and 2. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Notify the Chemistry Supervisor to evaluate. |  |  |  |  | b. Hydrazine specification and frequency only apply after addition (typically occurs during heatup, following completion of RCS fill and vent). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. Consider increased cleanup flowrate through the demineralizers, if not a suspected impurity source. |  |  |  |  | c. Hydrogen Peroxide specification and frequency only apply after addition. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. Consider establishing feed and bleed to reduce concentration. |  |  |  |  | d. Chemistry Supervisor will determine when sampling is no longer required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. Identify impurity source and isolate, if possible. |  |  |  |  | e. An unexpected change in RCS boron concentration of greater than  5 ppm boron would be considered out of limits and would require an out of limits notification. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6. Add chemical as necessary to increase concentration. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7. Place CVCS cation demineralizer in service to reduce lithium concentration. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - PRIMARY CHEMISTRY - RCS RADIOCHEMISTRY PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MODES 1 & 2 |  |  |  |  |  | MODES 3 & 4 |  |  |  |  | MODES 5 & 6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions |  | Limit | Frequency | Corrective Actions | Limit | Frequency | Corrective Actions |  |  |  |  |  |  |  |  |  |  |
| DEI-131, Ci/gmb |  a | D | 1,3,4 |  |  a | D | 1,3,4 |  | W |  |  |  |  |  |  |  |  |  |  |  |
| Gross Activity, Ci/gm |  a  | W | 1,4 |  | a | W | 1,4 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tritium, Ci/gm |  | W |  |  |  | W |  |  | PR |  |  |  |  |  |  |  |  |  |  |  |
| Fluorine-18, Ci/gm |  | W |  |  |  | W |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RCS Gas. Activity Ci/gm |  | W |  |  |  | W |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RCS Xe-133 Activity Ci /cc |  | W | 2,3,4 |  |  | W | 2,3,4 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RCS Degas. Activity Ci /gmb |  | D |  |  |  | D |  |  | W |  |  |  |  |  |  |  |  |  |  |  |
| RCS I-131 Activity Ci /gm |  | D | 2,3,4 |  |  | D | 2,3,4 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RCS CRUD Activity, Ci /gm |  | W |  |  |  | W |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RCS E-bar Determination |  | 1/6M |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Primary to Secondary Leak Rate |  | W | 2,5 |  |  | W | 2,5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  | a. Evaluate actions required in Technical Specification 3.4.16. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Notify the Chemistry Supervisor to evaluate. |  |  |  | b. When defects are suspected, the minimum requirements are to sample for I-131, I-132, I-133, I-134, Cs-134, and Cs-137 every 4 hours beginning at the start of a controlled shutdown or reactor trip and continuing for at least 16 hours ( 8 hours if no increase in I-131, i.e., Iodine spiking). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. Perform required notifications in accordance with TI-7.004, Fuel Integrity Assessment Program. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. Investigate changes in plant conditions that could have impacted these values. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. Ensure steam generator samples purging. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  | APPENDIX A CHEMISTRY SPECIFICATIONS - PRIMARY CHEMISTRY - PRIMARY STORAGE TANKS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | PWST |  |  |  |  |  |  | RWST |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Cold Leg Accumulator |  |  |  |  |  |  |  |  |  |  |  |  |  | BAT |  |  |  |  |  |  |  |  |  |  |  |  | Boric Acid Batch Tank |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter |  | Limit | Frequency | Corrective Actions |  | Limit |  |  |  | Frequency |  |  | Corrective Actions |  |  |  |  |  |  |  |  | Limit |  |  |  |  | Frequency |  |  |  | Corrective Actions |  |  | Limit | Frequency |  |  |  | Corrective Actions |  |  |  | Limit |  |  |  | Frequency |  |  |  | Corrective Actions |  |  |  |  |  |  |  |
| Boron, ppm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fluoride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dissolved Oxygen, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Calc. Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| pH @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Calculated pH @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TSS as Iron Oxide, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Silica, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TOC, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Aluminum, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Calcium, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Magnesium, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fe, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Gamma Activity, Ci/gm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Gamma + Tritium, ECL |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | a. Feed and bleed for borated water source storage tanks may be limited by Technical Specifications or Technical Requirements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Notify the Chemistry Supervisor to evaluate. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | constraints. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. Consider increased cleanup flowrate through the demineralizer, if not a suspected impurity source. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | b. Notify US/SM to evaluate necessary actions if results are outside Administrative Limits (i.e. 6665-6880 ppm). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. Consider establishing feed and bleed to reduce concentration. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | c. Boric acid batch tank concentrations should be adjusted to control the boric acid storage tanks within the administrative limit. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. Identify impurity source and isolate, if possible. 6. Add chemical as necessary to increase concentration. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - PRIMARY CHEMISTRY - PRIMARY DEMINERALIZERS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | CVCS MIXED BED DEMINERALIZER |  |  |  |  | SPENT FUEL POOL DEMINERALIZER |  |  |  |  | WASTE DISPOSAL VENDOR DEMINERALIZER |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit | Frequency | Corrective Actions | Limit |  | Frequency | Corrective Actions |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Fluoride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Boron, ppm |   |  |  |  |  |  |  |  |  |  |  |  |
| Lithium, ppm |   |  |  |  |  |  |  |  |  |  |  |  |
| Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |
| pH @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |
| Sodium, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Ammonia, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Gamma DF a |  |  |  |  |  |  |  |  |  |  |  |  |
| Gamma Activity (Ci/gm) |  |  |  |  |  |  |  |  |  |  |  |  |
|  | CVCS MIXED BED (Deborating) DEMINERALIZER |  |  | CVCS CATION BED DEMINERALIZER |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit | Frequency | Corrective Actions |  |  |  |  |  |  |
| Boron, ppm |  |  |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Lithium, ppm |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  |  | General Notes |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  |  | - DF includes all ionic isotopes, except cesium, yttrium and molybdenum. |  |  |  |  |  |  |
| 2. Notify the Chemistry Supervisor to evaluate. |  |  |  |  |  | b. Performed weekly when demineralizer is being utilized for deboration. |  |  |  |  |  |  |
|  |  |  |  |  |  | c. Performed if lithium reduction is significantly less than projected. |  |  |  |  |  |  |

|  | APPENDIX A CHEMISTRY SPECIFICATIONS - PRIMARY CHEMISTRY - WASTE DISPOSAL SYSTEM GAS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | SPENT RESIN |  |  |  |  | PRESSURIZER |  |  |  |  |  |  |
|  | WASTE GAS DECAY TANK |  |  |  |  | VOLUME CONTROL TANK |  |  |  |  |  |  | STORAGE TANK |  |  |  |  | RELIEF TANK |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit |  | Frequency |  | Corrective Actions | Limit | Frequency | Corrective Actions | Limit | Frequency | Corrective Actions |  |  |
| Oxygen, Vol% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydrogen, Vol% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Noble Gases, Curies (as Xe-133) |   |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | GAS DECAY TANK |  |  |  |  |  |  |  |  |  |  |  |
|  | REACTOR COOLANT DRAIN TANK |  |  |  |  | CVCS HOLDUP TANK |  |  |  |  |  |  | VENT HEADER |  |  |  |  | WASTE GAS COMPRESSOR |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit |  | Frequency |  | Corrective Actions | Limit | Frequency | Corrective Actions | Limit | Frequency | Corrective Actions |  |  |
| Oxygen, Vol% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydrogen, Vol% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Noble Gases, Curies (as Xe-133) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  | - Administrative limit. If the administrative limit is exceeded, sampling/analysis required every 24 hours. Corrective Action 1 applies when administrative limit is exceeded. |  |  |  |  |  |  |  |  |  |  |  |
| 2. Identify oxygen source and isolate, if possible. |  |  |  |  | b. When either 0-XIC-43-450 or 0-O2AN-43-227 is inoperable, sampling will be performed in accordance with 0-SI-77-3. Grab samples will be collected from the inservice WGDT at least once during a batch transfer (WGC operation) to a WGDT and at least once every four hours during periods of continued WGC operation. These samples will be analyzed within four hours following collection. |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | c. Oxygen is determined by daily grab sample whenever the Waste Gas Analyzer (WGA) oxygen analyzer is inoperable. |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | d. No additional monitoring or recording required if WGA is inoperable or if points are not selected. |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | e. Weekly frequency applies to all Waste Gas Decay Tanks that have been in service during the previous week. |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - PRIMARY CHEMISTRY - COMPONENT COOLING WATER SYSTEM |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CCS CONTROL PARAMETERS |  |  |  |  | CCS DIAGNOSTIC PARAMETERS |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions |  | Parameter | Limit | Frequency | Corrective Actions |  |  |
| pH@25C | - - 10.5 b 9.5 target | W | 1,3,5 |  | Conductivity /Corrosion Inhibitor Ratio d |  | W |  |  |  |
| Conductivity, S/cm @ 25C |  | W |  |  | TOC, ppb |  | PR |  |  |  |
| Sodium Molybdate, ppm (as Mo) | 150 - 300 ppm a 250 ppm target | W | 1,3,5 |  | Dissolved Oxygen, ppm |  | M |  |  |  |
| Tolyltriazole, ppm | 5 - 30 ppm c 25 ppm target | W | 1,3,5 |  | Total Alkalinity |  | PR |  |  |  |
|  |  |  |  |  | Fluoride, ppb |  150 ppb | M | 1,3,4 |  |  |
|  |  |  |  |  | Chloride, ppb |  150 ppb | M | 1,3,4 |  |  |
|  |  |  |  |  | Sulfate, ppb |  | Q |  |  |  |
|  |  |  |  |  | Calcium, ppb |  | PR |  |  |  |
|  |  |  |  |  | Magnesium, ppb |  | PR |  |  |  |
|  |  |  |  |  | Iron, ppb |  1000 ppb | M | 2,3 |  |  |
|  |  |  |  |  | Copper, ppb |  350 ppb | M | 2,3 |  |  |
|  |  |  |  |  | Bacteria (Total Aerobic), CFU/ml |  104 | Me | 2 |  |  |
|  |  |  |  |  | Bacteria (SRB), CFU/ml |  1 | Me | 2 |  |  |
|  |  |  |  |  | Gamma Activity, Ci/gm | < LLD | W | 2 |  |  |
| Corrective Actions |  |  |  |  | General Notes |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  | a. Target value used for chemical additions whenever concentration is more than 75 ppm below target. |  |  |  |  |  |
| 2. Notify Chemistry Supervisor to evaluate. |  |  |  |  | b. Target value used for chemical additions whenever pH is more than 0.5 units below target. |  |  |  |  |  |
| 3. Consider establishing feed and bleed to reduce concentration. |  |  |  |  | c. Target value used for chemical additions whenever concentration is more than 10 ppm below target. |  |  |  |  |  |
| 4. Identify impurity source and isolate, if possible. |  |  |  |  | d. Equals conductivity divided by the molybdate concentration. (Molybdate equals Mo times 1.67) |  |  |  |  |  |
| 5. Add chemical as necessary to increase concentration. |  |  |  |  | e. See CM 6.02 for instructions. |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - PRIMARY CHEMISTRY - AUXILIARY SYSTEMS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | REFUELING CANAL |  |  |  |  |  |  |  |  |  |  |  | SPENT FUEL POOL |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit |  |  | Frequency |  | Corrective Actions |  |  |  |  | Limit |  | Frequency | Corrective Actions |  |  |  |  |  |  |
| Boron, ppm |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fluoride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Calc. Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| pH @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Calculated pH @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Silica, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TSS as Iron Oxide, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Gamma Activity, Ci/gm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  |  |  |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  |  |  |  |  |  | a. Frequency applicable only during Mode 6. |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Notify the Chemistry Supervisor to evaluate. |  |  |  |  |  |  |  |  |  | b. Frequency applicable only during fuel movement, otherwise routine frequency is weekly.. |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. Consider increased cleanup flowrate through the demineralizers, if not a suspected impurity source. |  |  |  |  |  |  |  |  |  |  |  | c. Typically the refueling canal activity will be less than 0.01 Ci/gm before commencing fuel movement. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. Consider establishing feed and bleed to reduce concentration. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. Identify impurity source and isolate, if possible. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - PRIMARY CHEMISTRY - ICE CONDENSER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | BORAX SOLUTION MIXING TANK |  |  |  |  | ICE STORAGE BIN ICE |  |  |  |  |  | ICE CONDENSER ICE |  |  |  |  | GLYCOL MIXING TANK |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit | Frequency | Corrective Actions |  | Limit | Frequency | Corrective Actions | Limit | Frequency | Corrective Actions |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY CONTROL PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| STEAM GENERATORS MODE 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Action Level 1 | Action Level 1 Corrective Actions | Action Level 2 | Action Level 2 Corrective Actions | Action Level 3 | Action Level 3 Corrective Actions | Frequency | Value Prior to 30% Rx Power |  |  |
| Cation Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |
| Sodium, ppb |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |
| Na:Cl Molar Ratiof |  |  |  |  |  |  |  |  |  |  |
| Boron (ppm) |  |  |  |  |  |  |  |  |  |  |
| CONDENSATE/FEEDWATER MODE 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Action Level 1 | Action Level 1 Corrective Actions | Action Level 2 | Action Level 2 Corrective Actions | Action Level 3 | Action Level 3 Corrective Actions | Frequency | Value Prior to >5% Rx Power | Value Prior to >30% Rx Power |  |
| Hotwell DO, ppb |  |  |  |  |  |  |  |  |  |  |
| Feedwater DO, ppb |  |  |  |  |  |  |  |  |  |  |
| Feedwater Hydrazine, ppb |   |  |  |  |  |  |  |  |  |  |
| Feedwater ETA, ppm |  |  |  |  |  |  |  |  |  |  |
| Feedwater Iron, ppb |  |  |  |  |  |  |  |  |  |  |
| Feedwater Copper, ppb |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  |  |  |  |  |  |  |
| 2. Implement corrective actions as soon as possible to return parameter to within Action Level 1 controls. |  |  |  |  |  |  |  |  |  |  |
| 3. If the parameter is not restored to below Action Level 1 value within 7 days, go to Action Level 2 for those parameters having Action Level 2 values. A technical evaluation should be performed for operating above Action Level 1 for an extended period of time for those parameters not having an Action Level 2 value. |  |  |  |  |  |  |  |  |  |  |
| 4. If the contaminant ingress has been identified as a condenser tube leak, then advise the SM to take immediate actions, due to Action Level 2 values to reduce power to a level which will permit removal of the affected condenser waterbox from service. This power reduction is to be completed within 8 hours of initiation of Action Level 2 conditions. Following tube leak identification activities, power level is to be reduced to 30%. Power reduction may be terminated prior to reaching 30% if the source of impurity ingress is eliminated and parameters are restored below Action Level 2 values. Escalation to full power may be resumed once parameters are below Action Level 1 values. Source Note 12 |  |  |  |  |  |  |  |  |  |  |
| 5. If the contaminant ingress has not been identified as a condenser tube leak, then advise the SM to take immediate actions, due to Action Level 2 values to reduce power to 30% within 8 hours of initiation of Action Level 2 conditions. Power reduction may be terminated prior to reaching 30% if the source of impurity ingress is eliminated and parameters are restored to below Action Level 2 values. Escalation to full power may be resumed once parameters are below Action Level 1 values. Source Note 12 |  |  |  |  |  |  |  |  |  |  |
| 6. Return parameter to below Action Level 1 value within 100 hours of exceeding Action Level 2 values (or if Action Level 2 was entered due to exceeding Action Level 1 criteria for more than 7 days) or go to Action Level 3 for those parameters having Action Level 3 values. |  |  |  |  |  |  |  |  |  |  |
| 7. After an Action Level 2 excursion, consideration should be given to a hot soak or further reductions in power. |  |  |  |  |  |  |  |  |  |  |
| 8. Consult with Chemistry Supervision to determine if power reduction to  30% power within 8 hours is advisable. In some cases, power reduction may not be appropriate since greater air inleakage may occur at reduced power levels. If power reduction to  30% is determined to be necessary, then advise the SM to take immediate actions, due to Action Level 2 values to reduce power to 30% within 8 hours of initiation of Action Level 2 conditions. Power reduction may be terminated prior to reaching 30% if the source of impurity ingress is eliminated and parameters are restored to below Action Level 2 values. Escalation to full power may be resumed once parameters are below Action Level 1 values. |  |  |  |  |  |  |  |  |  |  |
| 9. If power reduction to  30% is determined to not be necessary, then document Chemistry Supervision recommendations in the laboratory journal and notify SM of recommendations. Initiate an Action Level 2 waiver in accordance with this instruction. |  |  |  |  |  |  |  |  |  |  |
| 10. Advise the SM that exceeding Action Level 3 values requires plant shutdown to Mode 4, as quickly as safe plant operation permits, to allow cleanup by feed and bleed or drain and refill as appropriate until parameters are restored to below Action Level 1 values. Regardless of the duration of the excursion into Action Level 3, the plant should be taken to hot or cold shutdown (Mode 4 or Mode 5). The unit may be restarted when a technical evaluation has been performed to determine the cause and impact of the parameter excursion, when actions to clean up secondary systems have been performed, and when chemistry parameters are within startup specifications. |  |  |  |  |  |  |  |  |  |  |
| General Notes |  |  |  |  |  |  |  |  |  |  |
| a. Perform grab sample analysis once per day if on-line instrument is inoperable. |  |  |  |  |  |  |  |  |  |  |
| b. Sample following steam generator fill and drain operations to verify specification is satisfied. |  |  |  |  |  |  |  |  |  |  |
| c . D.O. here is referring to that measured in the condensate system. |  |  |  |  |  |  |  |  |  |  |
| d. Specification applies only when the plant has operated at greater than 30% power for two weeks with no power changes greater than 20% in magnitude. |  |  |  |  |  |  |  |  |  |  |
| e. Operation above this limit is permissible with Chemistry Supervisor approval, provided that the calculated cation conductivity due to chloride and sulfate is less than the limit. OOL notification required. |  |  |  |  |  |  |  |  |  |  |
| f. The equation for molar ratio is: (Na * 35.453)/(Cl * 22.98977) = sodium to chloride molar ratio. |  |  |  |  |  |  |  |  |  |  |

APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY CONTROL PARAMETERS

STEAM GENERATORS

|  | MODES 2, 3, & 4 |  |  | MODES 5 & 6 Startup |  |  | MODES 5 & 6 Layup d |  |  |  | MODES 5 & 6 S/G Fill Source e |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Parameter | Frequency | Value Prior to >5% Rx Power | Frequency | Value Prior to Exceeding 200 F |  | Frequency | Limit | Frequency |  | Limit |  |  |
| Sodium, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Boron, ppm |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydrazine, ppm |  |  |  |  |  |  |  |  |  |  |  |  |
| pH, @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |
| Dissolved Oxygen, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  |  |  |  |  |  |  |  |  |
| General Notes |  |  |  |  |  |  |  |  |  |  |  |  |
| a. Perform grab sample analysis once per day if on-line instrument is inoperable. It is acceptable to align one SG to on-line instrumentation instead of sequencing between all four SGs. |  |  |  |  |  |  |  |  |  |  |  |  |
| b. Sample following steam generator fill and drain operations to verify specification is satisfied. |  |  |  |  |  |  |  |  |  |  |  |  |
| c. During initial layup period, sample 3 times per week until stable, then once per week. |  |  |  |  |  |  |  |  |  |  |  |  |
| d. If the duration for layup is short term (i.e., < 7 days), then hydrazine should be maintained > 5 ppm and pH should be controlled from 8.8 to 10.0. |  |  |  |  |  |  |  |  |  |  |  |  |
| e. The fill source refers to either the CSTs or Main Feedwater, whichever is being used as the source of water for the steam generators. f. Only required prior to and during fill of steam generators. |  |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY STEAM GENERATOR DIAGNOSTIC PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MODE 1 |  |  |  |  | MODES 2 - 4 |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit |  | Frequency | Corrective Actions |  |  |  |
| pH, @ 25C |  |  |  |  |  |  |  |  |  |  |
| Specific Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |
| Cation Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |
| Sodium, ppb |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |
| S/G Blowdown Flowrate, gpm |  |  |  |  |  |  |  |  |  |  |
| Hydrazine, ppb |  |  |  |  |  |  |  |  |  |  |
| Silica, ppb |  |  |  |  |  |  |  |  |  |  |
| Ammonia, ppm |  |  |  |  |  |  |  |  |  |  |
| ETA, ppm |  |  |  |  |  |  |  |  |  |  |
| Calculated Cation Conductivity |  |  |  |  |  |  |  |  |  |  |
| Calculated Specific Conductivity |  |  |  |  |  |  |  |  |  |  |
| Calculated pH |  |  |  |  |  |  |  |  |  |  |
| Gross Activity (gamma), Ci/g |  |  |  |  |  |  |  |  |  |  |
| Dose Equivalent I-131, Ci/g |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  | General Notes |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  | a. Perform grab sample analysis once per day if on-line instrument is inoperable. It is acceptable to align one SG to on-line instrumentation instead of sequencing between all four SGs. |  |  |  |  |  |
| 2. Notify the Chemistry Supervisor to evaluate. |  |  |  |  | b. If S/G Blowdown is not available, sample feedwater (note sample location on logsheet remarks). |  |  |  |  |  |
| 3. Maximize S/G Blowdown flowrate. |  |  |  |  | c. Operation above this limit is permissible with Chemistry Supervisor approval, provided that the |  |  |  |  |  |
| 4. Identify impurity source and isolate if possible. Consider Heater Drains & Vents, Condensate |  |  |  |  | calculated cation conductivity due to chloride and sulfate is less than the limit. |  |  |  |  |  |
| Demineralizers, chemical addition, and condenser inleakage as potential contaminant sources. |  |  |  |  | d. Operation above this limit for greater than 7 days is an adverse condition and should be documented |  |  |  |  |  |
| 5. Check chemical feed and adjust as necessary. |  |  |  |  | appropriately. |  |  |  |  |  |
| 6. Verify on-line instrument operation. |  |  |  |  | e. Decreases in the chloride concentration, decreases in pH, increases in the sodium:chloride molar |  |  |  |  |  |
| 7. Initiate performance of 1-ODI-90-2, 1-ODI-90-19, and 1-ODI-90-25 as necessary. |  |  |  |  | ratio, and decreases in specific conductivity can be caused by loss of chemical feed. |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY CONDENSATE DIAGNOSTIC PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CONDENSATE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | MODE 1 |  |  |  |  | MODES 2, 3, & 4 |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit | Frequency | Corrective Actions |  |  |  |  |  |
| pH, @ 25C |  |  |  |  |  |  |  |  |  |  |  |
| Specific Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |
| Cation Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |
| Sodium, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Dissolved Oxygen, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Hydrazine, ppm |  |  |  |  |  |  |  |  |  |  |  |
| ETA, ppm |  |  |  |  |  |  |  |  |  |  |  |
| Boron, ppm |  |  |  |  |  |  |  |  |  |  |  |
| Ammonia, ppm |  |  |  |  |  |  |  |  |  |  |  |
| Raw Water Inleakage, gpm e, f |  |  |  |  |  |  |  |  |  |  |  |
| Condenser Air Inleakage, scfm |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  |  |  | General Notes |  |  |  |  |
| 1. Perform OOL Notification |  |  |  |  |  |  | a. Perform grab sample analysis once per day if on-line instrument is inoperable. |  |  |  |  |
| 2. Notify the Chemistry Supervisor to evaluate. |  |  |  |  |  |  | b. Perform grab sample analysis as directed by the Chemistry Supervisor, if on-line |  |  |  |  |
| 3. Identify impurity source and isolate if possible. Heater Drains & Vents, Condensate Demineralizers, |  |  |  |  |  |  | instrument is inoperable Source Note 8. |  |  |  |  |
| chemical addition and condenser inleakage are areas to be examined as contaminant sources. |  |  |  |  |  |  | c. This concentration may be lowered as directed by the Chemistry Supervisor or designee. |  |  |  |  |
| 4. Check chemical feed and adjust as necessary. |  |  |  |  |  |  | d. Operation above this limit for greater than 7 days is an adverse condition and |  |  |  |  |
| 5. Verify on-line instrument operation. |  |  |  |  |  |  | should be documented appropriately. |  |  |  |  |
| 6. Perform ammonia, hydrazine, chloride, and sulfate analyses as required. Check Chromatograms for unknown peaks. |  |  |  |  |  |  | e. If leak rate >1.5 gpm per CM 5.04, increase polishing and identify which water box is leaking. Source Note 10 |  |  |  |  |
| 7. Adjust flow through C/D's as recommended by Chemistry Supervision. |  |  |  |  |  |  | f. Sample per CM 5.04 1/Day if leak rate >1 gpm. |  |  |  |  |
| 8. Request US/SM to establish feed and bleed to reduce concentration. |  |  |  |  |  |  |  |  |  |  |  |
| 9. Check for sources of air ingress. |  |  |  |  |  |  |  |  |  |  |  |
| 10. Notify System Engineering if a condenser tube leak is identified. Source Note 2 |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY FEEDWATER DIAGNOSTIC PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| FEEDWATER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | MODE 1 |  |  |  |  | MODES 2, 3, & 4b |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit |  | Frequency | Corrective Actions |  |  |  |  |
| pH, @ 25C |  |  |  |  |  |  |  |  |  |  |  |
| Specific Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |
| Cation Conductivity, S/cm @ 25C |  |  |  |  |  |  |   |  |  |  |  |
| Sodium, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Dissolved Oxygen, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Hydrazine, ppb |  |  |  |  |  |  |  |  |  |  |  |
| ETA, ppm |   |  |  |  |  |  |  |  |  |  |  |
| TSS as Iron Oxide, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Feedwater Iron, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Feedwater Copper, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Feedwater Fractional Iron, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Calculated pH, SU |  |  |  |  |  |  |  |  |  |  |  |
| Calculated Specific Conductivity |  |  |  |  |  |  |  |  |  |  |  |
| Boron, ppm |  |  |  |  |  |  |  |  |  |  |  |
| Ammonia, ppm |  |  |  |  |  |  |  |  |  |  |  |
| Tritium, Ci/gm |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  | General Notes |  |  |  |  |  |  |
| 1. Perform OOL Notification |  |  |  |  | a. Perform grab sample analysis once per day if on-line instrument is inoperable. |  |  |  |  |  |  |
| 2. Notify the Chemistry Supervisor to evaluate. |  |  |  |  | b. These specifications apply when on long cycle with vacuum established. |  |  |  |  |  |  |
| 3. Identify impurity source and isolate if possible. Heater Drains & Vents, Condensate Demineralizers, Chemical addition and condenser inleakage are areas to be examined as contaminant sources. |  |  |  |  | c. D.O. here is referring to that measured in the condensate system. |  |  |  |  |  |  |
| 4. Check chemical feed and adjust as necessary. |  |  |  |  | d. Perform grab sample analysis as directed by the Chemistry Supervisor, if on-line instrument is inoperable Source Note 8. |  |  |  |  |  |  |
| 5. Verify on-line instrument operation. |  |  |  |  | e. This concentration may be lowered as directed by the Chemistry Supervisor or designee. |  |  |  |  |  |  |
| 6. Recheck ammonia, hydrazine, chloride, and sulfate analyses as required. Check Chromatograms for unknown peaks. |  |  |  |  | f. Applicable during modes 2 and 3. Specification must be satisfied prior to use as a steam generator feed source. |  |  |  |  |  |  |
| 7. Adjust flow through C/D's or change C/D’s in service as recommended by Chemistry Supervision. |  |  |  |  | g. Applicable during mode 4. Specification must be satisfied prior to use as a steam generator feed source. |  |  |  |  |  |  |
| 8. Request US/SM to establish feed and bleed to reduce concentration. |  |  |  |  | h. Whichever specification is greater is to be applied. |  |  |  |  |  |  |
| 9. Notify System Engineering if a condenser tube leak is identified. Source Note 2 |  |  |  |  | i. Operation above this limit for greater than 14 days is an adverse condition and should be documented appropriately. |  |  |  |  |  |  |
| 10. Maximize flow through Red Iron Filters as necessary. |  |  |  |  | j. Decreases in pH, ETA, or specific conductivity can be caused by a loss of chemical feed. |  |  |  |  |  |  |
|  |  |  |  |  | k. Chemical concentrations should be controlled to within + 10% of the target value. |  |  |  |  |  |  |
|  |  |  |  |  | l. Applicable when feedwater is in service. |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY CONDENSATE & FEEDWATER DIAGNOSTIC PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | CONDENSATE/FEEDWATER |  |  |  |  |  | CONDENSATE |  |  |  |  |  |  |  |  |  |  |  |  | FEEDWATER |  |  |  |  |  |  |  |  |  |  |
|  | MODES 3 - 6 (Intermittent Operation) |  |  |  |  |  | MODES 5 & 6 (Intermittent Operation) |  |  |  |  |  |  |  |  |  |  |  |  | MODES 5 & 6 (Intermittent Operation) |  |  |  |  |  |  |  |  |  |  |
|  | (No Condenser Vacuum) |  |  |  |  |  | (Condenser Vacuum Present) |  |  |  |  |  |  |  |  |  |  |  |  | (Condenser Vacuum Present) |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency |  | Corrective Actions | Limit | Frequency |  |  |  | Corrective Actions |  |  | Limit |  |  |  |  |  | Frequency |  |  | Corrective Actions |  |  |  |
| pH, @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydrazine, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sodium, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Specific Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cation Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dissolved Oxygen, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tritium, Ci/gm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  |  |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. Identify impurity source and isolate if possible. Heater Drains & Vents, Condensate Demineralizers, chemical |  |  |  |  |  |  |  |  |  |  |  |  | a. Hydrazine and pH should be maintained at the upper end of their ranges unless transition to upper |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| addition and condenser inleakage are areas to be examined as contaminant sources. |  |  |  |  |  |  |  |  |  |  |  | modes is near. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Check chemical feed and adjust as necessary. |  |  |  |  |  |  |  |  |  | b. Perform grab sample analysis once per day if on-line instrument is inoperable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. Verify on-line instrument operation. |  |  |  |  |  |  |  |  |  | c. D.O. here is referring to that measured in the condensate system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. Recheck ammonia, hydrazine, chloride, and sulfate analyses as required. Check chromatograms for unknown peaks. |  |  |  |  |  |  |  |  |  |  |  |  | d. Hydrazine specification applies if hydrazine is being added for dissolved oxygen removal or lay-up. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. Adjust flow through C/D's as directed by Chemistry Supervision. |  |  |  |  |  |  |  |  |  | e. Applicable when feedwater is in service. Sampling frequency applies to feedwater only. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6. Request US/SM to establish feed and bleed to reduce concentration. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7. Notify the Chemistry Supervisor to evaluate. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8. Check for sources of air inleakage. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9. Notify System Engineering if a condenser tube leak is identified. Source Note 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY MISCELLANEOUS SECONDARY CYCLE SYSTEMS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | CBP INLET - MODES 1,2,3,4 |  |  |  |  | #3 HEATER DRAIN TANK - MODE 1 |  |  |  |  |  |  |  |  | #7 HEATER DRAIN TANK - MODE 1 |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit |  | Frequency |  | Corrective Actions |  |  | Limit |  | Frequency |  | Corrective Actions |  |  |  |  |
| pH, @25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Specific Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cation Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sodium, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Silica, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ammonia, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ETA, ppm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dissolved Oxygen, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TSS as Iron Oxide, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Iron, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Copper, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  |  |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  |  |  |  |  |  | a. Perform grab sample analysis as directed by Chemistry Supervisor if the monitor is out of service. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Route pump discharge to waste or hotwell until specifications are satisfied or Chemistry Supervisor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| gives approval to pump discharge forward. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS SECONDARY CHEMISTRY CONDENSATE PREFILTERS, DEMINERALIZERS, & TANKS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | CONDENSATE DEMINERALIZER EFFLUENT |  |  |  |  |  |  |  | CONDENSATE DEMINERALIZER RECEIVING TANK |  |  |  |  |  |  |  |  | CONDENSATE DEMINERALIZER ANION TANK |  |  |  |  |  |  |  |  |  |  |  |  |  | CONDENSATE DEMINERALIZER STORAGE TANK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency |  |  | Corrective Actions |  | Limit |  | Frequency |  | Corrective Actions |  |  |  | Limit |  |  | Frequency |  | Corrective Actions |  |  | Limit |  |  |  |  |  |  | Frequency |  | Corrective Actions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Specific Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |   |  |  |   |  |   |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sodium, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | CONDENSATE PREFILTER INLET |  |  |  |  |  |  |  | CONDENSATE PREFILTER OUTLET |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency |  |  | Corrective Actions |  | Limit |  | Frequency |  |  |  | Corrective Actions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TSS as Iron Oxide, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | HIGH CRUD TANKS |  |  |  |  |  |  |  | NEUTRALIZATION TANK |  |  |  |  |  |  |  |  |  |  | NONRECLAIMABLE WASTE TANK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit |  | Frequency | Corrective Actions |  | Limit |  |  |  | Frequency |  | Corrective Actions |  | Limit |  |  | Frequency |  |  |  |  | Corrective Actions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| pH, @25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  |  |  |  | a. Perform grab sample analysis once per day if on-line instrument is inoperable Source Note 8. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Notify the Chemistry Supervisor to evaluate. |  |  |  |  |  |  |  | b. Specifications apply to rinse prior to placing vessel in service and to vessels that are in service. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. Verify on-line instrument operation. |  |  |  |  |  |  |  | c. Sample individual filter vessel at drain upon initial operation with new filters. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. Request condensate demineralizer to be removed from service. |  |  |  |  |  |  |  | d. Source Note 9. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. Request US/SM to rinse one additional cycle. Regeneration is to be repeated if second rinse is unsuccessful. |  |  |  |  |  |  |  | e. Log results in laboratory journal. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6. Request US/SM to neutralize tank contents. |  |  |  |  |  |  |  | f. Monitoring not required if red iron filter(s) not in service. g. The anion tank rinse limit is <5S/cm if the polishers are in service. If the rinse is being performed while the polishers are out of service, then the anion tank effluent must be within +1S/cm of the condensate conductivity. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY STORAGE TANKS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 500K DEMINERALIZED WATER STORAGE TK |  |  |  |  |  |  |  | DEMINERALIZED WATER HEAD TK |  |  |  |  |  |  | CONDENSATE STORAGE TANKS |  |  |  |  |  |  | GLAND SEAL WATER STORAGE TANK |  |  |  |  |  |  |  |
| Parameter |  | Limit |  | Frequency |  | Corrective Actions | Limit |  | Frequency |  | Corrective Actions | Limit | Frequency |  | Corrective Actions |  | Limit |  |  | Frequency |  | Corrective Actions |
| Specific Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sodium, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Silica, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dissolved Oxygen, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydrazine, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TOC, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bacteria (Total Aerobic), CFU/ml |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bacteria (SRB), CFU/ml |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Gamma & Tritium Activity (Ci/gm) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  |  |  |  |  |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  |  |  |  |  |  |  |  | a. Limit only applies if results are not consistent with concentration of chemical additives (NH3, ETA, N2H4, etc.). |  |  |  |  |  |  |  |  |  |  |
| 2. Notify the Chemistry Supervisor to evaluate. |  |  |  |  |  |  |  |  |  |  |  | b. Limit applies only for makeup directly to the steam generators. |  |  |  |  |  |  |  |  |  |  |
| 3. Request US/SM to drain and refill tank if requested to do so by the Chemistry Supervisor. |  |  |  |  |  |  |  |  |  |  |  | c. Limit applies when reverse osmosis unit is in service. |  |  |  |  |  |  |  |  |  |  |
| 4. Notify Chemistry Supervision to review IE Bulletin 80-10 and IN 91-40 and to specify appropriate actions. |  |  |  |  |  |  |  |  |  |  |  | d. Monitoring shall be performed prior to feeding the steam generators and once per day while feeding the steam generators. |  |  |  |  |  |  |  |  |  |  |
| 5. Identify impurity source and isolate, if possible. |  |  |  |  |  |  |  |  |  |  |  | e. See CM 6.02 for instructions. |  |  |  |  |  |  |  |  |  |  |
| 6. Request US/SM to increase nitrogen sparge. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7. Add hydrazine to the CST as needed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY ECOLOCHEM EFFLUENT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ECOLOCHEM EFFLUENT |  |  |  |  | ECOLOCHEM AUXILIARY EQUIPMENT EFFLUENT |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit |  | Frequency | Corrective Actions |  |  |  |  |  |
| Specific Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |
| Sodium, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Silica, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| TOC, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Dissolved Oxygen, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Fluoride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |
| Bacteria (Total Aerobic), CFU/ml |  |  |  |  |  |  |  |  |  |  |  |  |
| Bacteria (SRB), CFU/ml |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  | General Notes |  |  |  |  |  |  |  |
| 1. Notify the Chemistry Supervisor to evaluate. |  |  |  |  |  | a. Parameter verified within specifications prior to sending water to 500k |  |  |  |  |  |  |  |  |  |
| 2. Notify vendor to terminate makeup to 500k Demineralized Water Storage Tank or CST's. |  |  |  |  |  |  |  | Demineralized Water Storage Tank or CST's. |  |  |  |  |  |  |  |
|  |  |  |  |  | b. Monitor once per day if online instrument is inoperable Source Note 8. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | c. See CM 6.02 for instructions. |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY AUXILIARY SYSTEMS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | AUXILIARY BOILER- OPERATION |  |  | AUXILIARY BOILER- LAYUP a |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit |  | Frequency | Corrective Actions |  |  |  |  |
| pH @ 25C, SU |  |  |  |  |  |  |  |  |  |  |  |
| Dissolved Oxygen, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Hydrazine, ppm |  |  |  |  |  |  |  |  |  |  |  |
| Cation Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |
| TSS as Iron Oxide, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Gamma & Tritium Activity Source Note 4 |  |  |  |  |  |  |  |  |  |  |  |
| Bacteria, (Total Aerobic), CFU/ml |  |  |  |  |  |  |  |  |  |  |  |
| Bacteria (SRB), CFU/ml |  |  |  |  |  |  |  |  |  |  |  |
|  | STATOR COOLING WATER - CE-35-85 (CELL CC1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions |  |  |  |  |  |  |  |  |
| Dissolved Oxygen, ppb |  |  |  |  |  |  |  |  |  |  |  |
| Specific Conductivity, S/cm @ 25C |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  | General Notes |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  | a. Layup of the Auxiliary Boiler is required only if the shutdown period exceeds seven days. |  |  |  |  |  |  |
| 2. Notify the Chemistry Supervisor to evaluate. |  |  |  |  | b. Perform grab sample analysis as directed by Chemistry Supervisor. |  |  |  |  |  |  |
| 3. Check chemical feed and adjust as necessary. |  |  |  |  | c. See CM 6.02 for instructions. |  |  |  |  |  |  |
| 4. Increase sample frequency to once per shift. |  |  |  |  |  |  |  |  |  |  |  |
| 5. Increase Auxiliary Boiler blowdown flowrate. |  |  |  |  |  |  |  |  |  |  |  |
| 6. Notify US/SM to investigate for the source of activity. |  |  |  |  |  |  |  |  |  |  |  |
| 7. Notify Chemistry Supervision to review IE Bulletin 80-10 and to specify appropriate actions. |  |  |  |  |  |  |  |  |  |  |  |
| 8. Notify US/SM to replace demineralizer resin. |  |  |  |  |  |  |  |  |  |  |  |
| 9. Feed/bleed or add chemicals as required. |  |  |  |  |  |  |  |  |  |  |  |
| 10. Evaluate sampling main generator gas for hydrogen and or oxygen concentration. |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY RAW WATER, POTABLE WATER, YARD PONDS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RAW COOLING WATER |  |  |  |  | ESSENTIAL RAW COOLING WATER |  |  |  |  |  | CONDENSER CIRCULATING WATER |  |  |  |  |  |  |  |  |  | CONTAINMENT SPRAY HEAT EXCHANGER (ERCW SIDE) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit | Frequency | Corrective Actions |  | Limit |  | Frequency |  |  | Corrective Actions |  |  | Limit |  |  | Frequency |  |  | Corrective Actions |  |  |  |  |  |  |  |  |  |  |
| Total Residual Oxidant, ppm Source Notes 6,7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Phosphorous, ppm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Zinc, ppm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Iron a, ppm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Langelier Saturation Index |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydrazine, ppm Source Note 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| pH @ 25C, Source Note 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chloride, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sodium, ppm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sulfate, ppm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bacteria, (Total Aerobic), CFU/ml |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bacteria, (SRB), CFU/ml |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | YARD HOLDING POND |  |  |  |  | LOW VOLUME WASTE TREATMENT POND |  |  |  |  |  | POTABLE WATER SYSTEM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit | Frequency | Corrective Actions |  | Limit |  | Frequency |  |  | Corrective Actions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Gamma & Tritium Activity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  |  |  | a. Samples from an untreated and a treated source are to be collected and analyzed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Notify the Chemistry Supervisor to evaluate. |  |  |  |  |  |  | b. Monitoring required only if BCDMH is being added to the system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. Notify Chemistry Supervision to review IE Bulletin 80-10 and IN 91-40 and to specify appropriate actions. |  |  |  |  |  |  | c. Sample the containment spray heat exchanger when chloride ingress is suspected into the lay-up solution. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. Check chemical feed and adjust as necessary. |  |  |  |  |  |  | d. See CM 6.02 for instructions. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. Establish feed and bleed or drain and fill to reduce concentration as directed by Chemistry Supervisor. |  |  |  |  |  |  | e. Analysis required only if zinc/phosphate compounds are being injected. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6. Identify impurity source and isolate, if possible. |  |  |  |  |  |  | f. Target 0.2 to 0.3 ppm TRO unless otherwise directed by the Chemistry Supervisor/designee. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7. Add chemical as necessary to increase concentration. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8. Circulate through portable demineralizer as needed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9. Notify vendor to adjust chemical feed as necessary. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - TENNESSEE RIVER AND HIGH PRESSURE FIRE PROTECTION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | TENNESSEE RIVER |  |  |  |  | HIGH PRESSURE FIRE PROTECTION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions | Limit | Frequency | Corrective Actions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bacteria, (Total Aerobic), CFU/ml |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bacteria, (SRB), CFU/ml |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. Notify the Chemistry Supervisor to evaluate. |  |  |  |  |  |  | a. See CM 6.02 for instructions. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY DIESEL GENERATOR STORAGE TANK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | BACKUP SECURITY LIGHTING |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Water, inches | None Detected | M | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | MAIN FUEL OIL STORAGE TANKS #1 AND #2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameter | Limit | Frequency | Corrective Actions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Water, inches | None Detected | M | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. Initiate actions to have water removed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

APPENDIX A CHEMISTRY SPECIFICATIONS - SECONDARY CHEMISTRY CLOSED COOLING SYSTEMS

|  |  |  |  | CHILLED WATER SYSTEMSa |  |  |  |  |  |  |  |  |  |  |  | TURBINE BUILDING HEATING SYSTEM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Parameter |  |  | Limit | Frequency |  |  |  | Corrective Actions |  |  |  |  |  | Limit |  |  |  | Frequency |  |  |  |  |  |  |  | Corrective Actions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | pH @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hydrazine, ppm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Dissolved Oxygen, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Bacteria (Total Aerobic) CFU/ml |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Bacteria (SRB) CFU/ml |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | AUX BUILDING GENERAL VENT CHILLER |  |  |  |  |  |  |  |  |  |  | ELECTRICAL BOARD ROOM CHILLER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Parameter |  |  | Limit | Frequency |  |  | Corrective Actions |  |  |  |  |  | Limit |  |  |  |  | Frequency |  |  |  |  |  |  | Corrective Actions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | pH @ 25C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hydrazine, ppm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Dissolved Oxygen, ppb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Bacteria (Total Aerobic) CFU/ml |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Bacteria (SRB) CFU/ml |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Corrective Actions |  |  |  |  |  |  |  |  |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 1. Add chemical to increase concentration as necessary. |  |  |  |  |  |  |  |  |  |  |  | a. These specifications apply to the following systems: Main Control Room Chiller, Incore Instrument Rm Chiller, Shutdown Board Room Chiller, Office Building Heating and Cooling. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 2. Establish feed and bleed to reduce concentration as necessary. |  |  |  |  |  |  |  |  |  |  |  | b. See CM 6.02 for instructions. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | c. Hydrazine concentration is directly related to pH. The target hydrazine concentration should be 25 ppm in order to maintain pH within limits. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3. Notify the Chemistry Supervisor to evaluate. |  |  |  |  |  |  |  |  |  |  |  | d. The target hydrazine concentration should be 9 ppm. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

APPENDIX A CHEMISTRY SPECIFICATIONS -

SECONDARY CHEMISTRY DIESEL GENERATOR JACKET COOLING SYSTEM

| CONTROL PARAMETERS |  |  |  |  | DIAGNOSTIC PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Parameter | Limit | Frequency | Corrective Actions |  | Parameter | Limit | Frequency | Corrective Actions |  |  |  |  |  |  |  |  |  |
| pH@25C | 8.5 - 10.5 | M | 1,3,5 |  | Conductivity /Corrosion Inhibitor Ratio |  | Qc |  |  |  |  |  |  |  |  |  |  |
| Conductivity, S/cm @ 25C |  | M |  |  | Nitrate, ppm |  | Q |  |  |  |  |  |  |  |  |  |  |
| Corrosion Inhibitor, Ounces Nalco 39/gal | 2 - 5 | M | 1,3,5 |  | Nitrite, ppm |  600 | Q | 5 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Total Dissolved Solids, ppm |  340 | PRa | 6 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Total Hardness, ppm |  170 | PRa | 6 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Total Alkalinity |  | PRa |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | TOC, ppb |  | PRa |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Calcium, ppb |  | PRa |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Magnesium, ppb |  | PRa |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Chloride, ppm |  10 | PRa | 1,3,4,6 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Fluoride, ppm |  10 | PRa | 1,3,4,6 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Sulfate, ppm |  10 | PRa | 1,3,4,6 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Ammonia, ppm |  | Q |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Iron, ppb |  | Q |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Copper, ppb |  | Q |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Bacteria (Total Aerobic), CFU/ml |  104 | Mb | 2 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Bacteria (SRB), CFU/ml |  1 | Mb | 2 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Dissolved Oxygen |  | PR |  |  |  |  |  |  |  |  |  |  |
| Corrective Actions |  |  |  |  | General Notes |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. Perform OOL Notification. |  |  |  |  | a. Analysis required for makeup water, if demineralized water is not used for makeup. |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Notify Chemistry Supervisor to evaluate. |  |  |  |  | b. See CM 6.02 for instructions. |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. Consider establishing feed and bleed to reduce concentration. |  |  |  |  | c. The conductivity/corrosion inhibitor ratio is calculated by dividing the conductivity value by the nitrite concentration. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. Identify impurity source and isolate, if possible. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. Add chemical as necessary to increase concentration. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6. Do not use for makeup if specification is not satisfied. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  | APPENDIX B CHEMISTRY LOGSHEET - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Parameter |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sampled By, Initials |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Remark # |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Database Entry (Initials) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| QA RECORD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CHEMISTRY SUPERVISOR: |  |  |  |  |  | / |  |  |  |

| APPENDIX C CHEMISTRY LOGSHEET REMARKS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Remark # | Initials |  | Date | Time | System |  |  | Parameter |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| QA RECORD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CHEMISTRY SUPERVISOR: |  |  |  |  | / |  |  |  |  |  |

| Action Level Waiver |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| APPENDIX D |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Page 1 of 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Action Level Parameter: |  |  |  |  |  |  |  |  |  |
|  | Action Level (i.e. 1,2,3): |  |  |  |  |  |  |  |  |  |
|  | Action Level Limit: |  |  |  |  |  |  |  |  |  |
|  | Action Level Time of Initiation: |  |  |  |  |  |  |  |  |  |
|  | Most Recent Result for Action Level Parameter: |  |  |  |  |  |  |  |  |  |
|  | Trend for Action Level Parameter: (Increasing, Steady or Decreasing) |  |  |  |  |  |  |  |  |  |
|  | Justification For Waiver: |  |  |  |  |  |  |  |  |  |

| Chemistry Superintendent Recommendation |  |
| --- | --- |
| Plant Manager Approval |  |

QA Record

APPENDIX E

Page 1 of 1

RCS Lithium Control

RCS lithium concentration should be established within 24 hours of entering mode 2 from a shutdown condition using the guidelines below. All attempts should be made to control lithium during a plant transient (i.e., >20% Reactor Thermal Power change). However, lithium control should be re-established within 8 hours of reaching stable conditions following a plant transient.

Determine the RCS Lithium control band as follows:

- Obtain the current RCS Tave.

- Determine the RCS lithium concentration limits for pH(t)=7.1.

- If the RCS lithium value for pH(t)=7.1 is greater than 3.5 ppm, then use 3.5 ppm as the RCS lithium target and 
RCS lithium maximum, and -0.15 ppm for the RCS lithium minimum.

- If  the RCS lithium value for pH(t)=7.1  is less than 3.5 ppm, then use the pH(t)= 7.1 value as the RCS lithium target, +0.15 ppm for the RCS lithium maximum (not to exceed 3.5 ppm), and -0.15 ppm for the RCS lithium minimum.

3.	Limit pH changes to  0.05 pH units above or below target pHt to minimize potential CRUD releases.

4.	As an administrative control to minimize pH swings in the RCS, use the following guidance as a goal for lithium control.  Operation outside of this guidance is not considered to be out of limits. However, actions should be taken to maintain the lithium concentration within the following control bands whenever achievable:

- When the RCS lithium target is 0 - 1 ppm, use the target  0.05 ppm as the control band

- When the RCS lithium target is 1.01 - 2 ppm, use the target  0.10 ppm as the control band

- When the RCS lithium target is 2.01 - 3.5 ppm, use the target  0.13 ppm as the control band, not to exceed 3.5 ppm as an upper limit

5.	When directed by the Chemistry Supervisor for planned shutdowns to modes 5 and 6 the lithium concentration may be reduced prior to shutdown to aid in establishing acid reducing conditions in the RCS.

SOURCE NOTES

| Source Note | Source Document | Summary |
| --- | --- | --- |
| 1 | TVA Memorandum L29 800108 810 | WBNP Containment Spray Heat Exchangers |
| 2 | ESS-91-004 | Notification of Technical Support of Condenser Tube Leaks |
| 3 | GL 85-02 | Incorporate Revision 3 of the Secondary Water Chemistry Guidelines With Progressively More Stringent Actions for Out-of Limit Conditions |
| 4 | NRC IE 80-10 | Check for cross-contamination between radioactive and non-radioactive systems |
| 5 | SCAR WBSCA930212 | Nitrite analysis for diesel generator cooling water |
| 6 | NRC IEB-81-03 | Raw Water Fouling |
| 7 | NRC GL-89-13 | Raw Water Fouling |
| 8 | WBPER960342 | Compensatory samples when on-line analyzers are not qualified for use. |
| 9 | WBPER960510 | Condensate demineralizer effluent limits. |
| 10 | FSAR Commitment # FSR-10-048 | Condenser inleakage. |
| 11 | WBPER970237 | Removes ability to change limits/frequencies with standing order. |
| 12 | WBPER970084 | Action level requirements with respect to condenser inleakage (CCW). |