# Technical Specifications

for

INtake Weir Modification

at the

kooskia National Fish Hatchery,

kooskia, id

Prepared by

JACOBS

February 14, 2008

Part I – The Schedule

Section B – Bidding Schedule

# Bidding Schedule

for

INTAKE WEIR MODIFICATIONS

at the

kooskia National Fish Hatchery

in

kooskia, id

Bidding SChedule ALTERNATE 1:

(Selective Demolition of Existing Weir Utilizing Existing Buried Cutoff Walls In New Construction)

Item No.	Description	Amount

| 1. | Dewatering of a portion of Clear Creek to enable construction of a new weir section while ensuring continued hatchery process water supply. Selective demolition of an existing cast-in-place concrete weir leaving existing buried concrete cutoff walls at weir in place for use in construction of new concrete apron and weir walls. Construction of a new cast-in-place concrete weir section, apron, upstream and downstream weir walls, and two wing walls. Construction is to include embedded conduits and anchors for installation of an inflatable weir section. Construction and installation of timber stop logs. Install rip rap downstream of the weir. Additional Work as shown on the drawings and specified for the above described Work for a lump sum price of | $ |
| --- | --- | --- |
| 2. | Replacement of an existing electrical service box and associated conduits, wiring and connections. Connection to existing service without interruption of existing service. Installation of new electrical service and associated service boxes, conduits, wiring and connections. Installation of a new inflatable weir section including pneumatic and electrical piping and conduits and controls. Installation of a new prefabricated service building and connection of all associated pneumatic and electrical components. Additional work not specifically stated to provide a complete and functional pneumatically operated weir as shown on the drawings and specified for the above described Work for a lump sum price of | $ |
| 3. | Private Property Access Fee, described in Amendment No. 4. | $500.00 |
| 4. | Replace two power service poles. Demolish and dispose of light post, conduit, box and related overhead cable. Restore Lower Access Road with approximately 60 cubic yards of material.. Dredge and dispose approximately 400 cubic yards. Work as described in Addendum No. 4 for a lump sum price of……………………………………………………... | $ |
|  | Total Items 1 through 4 (inclusive) | $ |

Bidding SChedule ALTERNATE 2:

(Selective Demolition of Existing Weir Including Removal of Existing Buried Cutoff Walls)

Item No.	Description	Amount

| 1. | As in Bidding Alternate 1 Item 1 except selective demolition of existing cast-in-place concrete weir to include removal of existing buried concrete cutoff walls at weir (existing cutoff walls not used in construction of new weir structure) and construction of new concrete cutoff walls. Work as shown on the drawings and specified for the above described Work for a lump sum price of | $ |
| --- | --- | --- |
| 2. | As in Bidding Alternate 1 Item 2. Work as shown on the drawings and specified for the above described Work for a lump sum price of | $ |
| 3. | Private Property Access Fee, described in Amendment No. 4. | $500.00 |
| 4. | Replace two power service poles. Demolish and dispose of light post, conduit, box and related overhead cable. Restore Lower Access Road with approximately 60 cubic yards of material.. Dredge and dispose approximately 400 cubic yards. Work as described in Addendum No. 4 for a lump sum price of……………………………………………………... | $ |
|  | Total Items 1 through 4 (inclusive) | $ |

Incomplete bids will not be considered.

52.217-5	Evaluation Of Options

Except when it is determined in accordance with FAR 17.206 (b) not to be in the Government’s best interests, the Government will evaluate offers for award purposes by selecting the lowest responsive and responsible bid.  At the sole discretion of the Government, either Option 1, Option 2, or Option 2 plus Option 3 may be awarded.  Evaluation of options will not obligate the Government to exercise the option(s).

Name of Bidder/Company

Address (Include Zip Code)

Telephone (Include Area Code)

E-mail Address

Part I – The Schedule

Section C – Project Description and Technical Specifications

# Index

## TECHNICAL SPECIFICATIONS

Title	Page

DIVISION 1 - GENERAL REQUIREMENTS

010000	General Requirements	C-4

013300	Submittals		C-13

017700	Contract Closeout	C-25

DIVISION 2 – EXISTING CONDITIONS

024119	Demolition	C-27

DIVISION 3 – CONCRETE

032000	Concrete Reinforcement	C-31

033000	Cast-in-Place Concrete	C-37

DIVISION 11 - EQUIPMENT

110000	Pneumatic Crest Gates	C-47

DIVISION 13 – SPECIAL CONSTRUCTION

133423	Pre-Engineered Fiberglass Buildings	C-57

DIVISION 26 - ELECTRICAL

260500	Basic Electrical Requirements	C-65

DIVISION 31 – EARTHWORK

312316	Excavating and Backfilling	C-83

312319	Dewatering	C-89

DIVISION 35 – WATERWAY AND MARINE CONSTRUCTION

354337	Streambed Protection	C-91

# Section 010000

## General Requirements

## SUMMARY OF WORK

### DESCRIPTION OF WORK

#### The work to be performed under this contract consists of furnishing all labor, equipment, materials, and supplies to partially dewater Clear Creek, selectively demolish the existing concrete intake weir, install embedded piping for a pneumatic weir, construction of a new cast-in-place concrete weir section and two wing walls, install rip rap downstream of the weir, and miscellaneous other Work as described in the Drawings and Specifications.  Work also includes furnishing all labor, equipment, materials and supplies to install a pneumatically operated weir including all enclosures, electrical, controls, plant and mechanical portions of the Work as described in the Drawings and Specifications.

### LOCATION OF WORK

#### All work to be performed is immediately near the Kooskia National Fish Hatchery (Hatchery) located in Kooskia, Idaho.

### INQUIRIES

#### Questions regarding the work should be directed to the Regional Engineer, U.S. Fish and Wildlife Service, 911 NE 11th Ave., Portland, Oregon  97232.  Phone:  (503) 231-6145.

### APPLICABLE CODES

#### In instances where these specifications do not state exact materials or methods of construction, the applicable minimum requirements of the 2003 International Building Code shall govern.

### ENGINEERING SERVICES

#### No control points or benchmarks were established for this project.  This project is designed to match existing elevations, grades structure match points.  The Contractor shall furnish and place all stakes, marks and templates required for the performance and completion of the work.

### SPECIAL NOTICES

#### Prebid Conference.  A prebid conference will be held to afford all bidders an opportunity to request information or interpretations of the Drawings and Specifications and to visit the site.  The time of this meeting and inspection of the construction site is given on Government Standard Form 1442.  Bidders are strongly encouraged to attend the pre-bid site visit.

#### Fish Hatchery Operations.  Construction at the site is constrained by the operational requirements of the Fish Hatchery intake, around which the construction described in these documents is to take place.  The Engineer shall have the right to halt any construction activities that are deemed by the Engineer or Fish Hatchery personnel to be detrimental to the operation of the Fish Hatchery.

## CONTRACT DOCUMENTS

### DRAWINGS

#### The following drawings are hereby made a part of this invitation by reference:

| DRAWING NO. | TITLE | SHEET NO. |
| --- | --- | --- |
| IF-ID-733-181-1.0 | Vicinity Map, Index, and Site Plan | 1 of 10 |
| IF-ID-733-181-2.0 | General Notes and Abbreviations | 2 of 10 |
| IF-ID-733-181-3.0 | Intake Weir Dewatering and Riprap Plan | 3 of 10 |
| IF-ID-733-181-4.0 | Demolition Plan and Existing Conditions | 4 of 10 |
| IF-ID-733-181-5.0 | Intake Weir Plan 1 | 5 of 10 |
| IF-ID-733-181-6.0 | Intake Weir Plan 2 | 6 of 10 |
| IF-ID-733-181-7.0 | Intake Weir Sections | 7 of 10 |
| IF-ID-733-181-8.0 | Intake Weir Sections and Detail | 8 of 10 |
| IF-ID-733-181-9.0 | Intake Weir Sections and Details | 9 of 10 |
| IF-ID-733-181-10.0 | Intake Weir Electrical Plan & One Line Diagram | 10 of 10 |

### COORDINATION OF DOCUMENTS GOVERNING THE WORK

#### The standard Government forms, specifications, associated plans, solicitation provisions and contract clauses, made a part of the contract are essential parts thereof and the requirements in one are as binding as though contained in all.  They are intended to be mutually supplementary to describe and provide for a complete work.

#### All discrepancies in the drawings shall be brought to the attention of the Engineer for resolution.  Drawings shall not be scaled to obtain missing or conflicting dimensions.  The Contractor shall keep a check on dimensions and details as the work progresses and any errors or discrepancies discovered shall be promptly reported to the Engineer.

#### In cases of conflict between drawings, specifications, contract provisions, supplemental agreements and provisions of Standard Government Forms, the provisions of Standard Government Forms shall govern.  In all cases of dispute in respect to such conflict or as to what part or parts of the specifications apply to any given parts of the work; decisions shall be made by the Contracting Officer.

### COPIES OF DRAWINGS AND SPECIFICATIONS

#### Copies of the engineering drawings are furnished with the Invitation for Bids.  These drawings are intended to be used for construction.  The Contractor will be furnished with a reasonable number of additional paper copies of the drawings and specifications he may require to carry on the work in a satisfactory manner.

#### Electronic copies of the drawings and specifications will not be made available.

## SUBMITTALS

### EQUIPMENT, MATERIALS AND COMPONENTS

#### All equipment, materials and components furnished by the Contractor shall be stock models for which parts are readily available and shall be products which shall have performed satisfactorily in an installation independent of the manufacturer's facilities for a consecutive period of not less than two (2) years as of the date of the bid opening.

### SUBMITTAL PROCEDURE

#### All submittals shall be made utilizing the government furnished Submittal Form R1-67 which shall be used as the document for approving or disapproving the material.  Written approval must be obtained from the Government before items requiring submittal are installed.  Submittals not in accordance with the drawings and specifications shall be accompanied by a written statement indicating in detail all parts which deviate from the drawings and specifications.  See Technical Specification Section 013300 for additional requirements.

#### All submittals shall be made to the Engineer by the Contractor only.  Submittals received by the Engineer without the Contractor's signature shall be returned to the Contractor without action.

#### Literature, shop drawings, etc., fully describing the items which the Contractor proposes to install shall be submitted in six (6) copies.  Material or finish samples shall be submitted in three (3) sets.  Items submitted shall be plainly marked to indicate which options, models etc. are proposed.

### REQUIRED SUBMITTALS

#### Construction Schedule.  The Contractor shall furnish the Contracting Officer his proposed work schedule within 15 days after award of contract.  He shall also advise the Contracting Officer of revisions of the schedule as modifications may become necessary, or as may be required after commencement of work. Such outlines and revisions shall be in sufficient detail to enable the Contracting Officer to judge as to the adequacy of the Contractor's operations and to anticipate such conditions as may tend to impair or retard the progress and completion of the work.  The proposed work schedule shall include a Work Breakdown structure with sufficient tasks and activities to accurately determine scheduled milestone dates, define critical path activities, and show anticipated float for all non-critical activities.  No work may commence until the Contractor’s schedule is approved by the Engineer.

#### Payment Schedule.  The Contractor shall furnish the Contracting Officer a detailed payment schedule within 15 days of award of contract.  This schedule shall be based upon the Contract Bidding Schedule but with sufficient additional detail to allow accurate calculation of the Monthly Progress Payment.  Lump sum bid items shall be broken down into their component parts, i.e., mobilization, bond and insurance, excavation, backfill, concrete work, etc. with a cost figure for each.  Each component part shall be identified on the Construction Schedule identified above.  The list of component parts will vary depending upon the type of contract and the above list shall not be construed as complete or incomplete.

#### Submittals are required on the items as listed individually in each section of the Technical Specifications (Divisions 2 through 33).  The description of submittal data required is contained in the individual section.  A summary is provided in Technical Specification Section 013300.

#### As-built drawings:  One (1) complete set of the Contract Drawings will be furnished to the Contractor for use in preparing as-built drawings.  The Contractor shall keep this set of prints on the job site and record all changes to contract drawings including Contract Modifications, with a red pencil.  Submit marked up as-built blueline prints to the Engineer at the completion of the job.

#### The Contractor shall furnish to the Engineer three (3) complete bound sets of typewritten or printed operation and maintenance instructions for those items as listed individually in each section of the Technical Specifications (Divisions 2 through 33).  Each set shall contain manufacturer's specifications, operation, maintenance, performance and dimensional data.  Sets shall be neatly segregated, indexed and labeled.

#### See Technical Specification Section 013300 for additional requirements.

## CONSTRUCTION SUPPORT

### UTILITY SERVICES AND CONSTRUCTION SUPPORT FACILITIES

#### The Contractor shall furnish all facilities and utilities needed for his operations under this contract, including all temporary heat, light, power, water, telephone, sanitary facilities and job offices and shops.  Electric power will be made available to the Contractor from existing Hatchery facilities at the power drop to the existing intake.

### ACCESS TO SITE

#### Access to the work from existing roads shall be provided by the Contractor at his own expense.  The Government assumes no responsibility for the condition or maintenance of any road or structure thereon that may be used by the Contractor in performing the work under these specifications or in traveling to and from the site of the work.  No payment will be made to the Contractor by the Government for any work done in improving, repairing, or maintaining any road or structure thereon for use in the performance of the work under these specifications.  Roads subject to interference by the work shall be kept open.

### PROTECTION OF PROPERTY

#### The Contractor shall not enter upon private property for any purpose without first obtaining permission from the owner or his duly authorized representative, shall be responsible for the preservation of all public and private property along and adjacent to work contemplated under the contract, and shall use every precaution necessary to prevent damage or injury thereto.  He shall exercise due care in preventing, and shall be responsible for damages to structures of all kinds, whether owned by the Government or privately, and shall protect from disturbance or damage all land monuments until they have been properly referenced by the Engineer.

### PROTECTION OF ENVIRONMENT

#### All contract operations shall be conducted within compliance of all federal, state and local environmental laws and regulations, and the project permits.  This condition applies to, but is not limited to, laws and regulations governing noise levels, air and water quality standards, and cultural resources.  Compliance with cultural resources requirements will be approved by the Regional Archaeologist, designated elsewhere in this contract.

#### If the Contractor fails or refuses to promptly comply with the requirements of subparagraph A. above, the Contracting Officer or his authorized representative, shall notify the Contractor of any noncompliance and indicate to the Contractor the action to be taken.  The Contractor shall, after receipt of such notice, immediately correct the conditions to which attention has been directed.  Such notice, either oral or written, when served on the Contractor or his representative(s) at the site of the work, shall be deemed sufficient.

#### In the event the Contractor fails or refuses to promptly comply with the compliance directive issued under subparagraph above, the Contracting Officer may issue an order to suspend all or any part of the work.

#### When satisfactory corrective action is taken, an order to resume work will be issued.  The Contractor shall not be entitled to any extension of time, nor to any claim for damage or to excess costs by reason of either the directive or the suspension order.

### ADDITIONAL SAFETY REQUIREMENT

#### In addition to the Safety and Health requirements of clause 52.236-13 of Part 2, Section I of the Contract, roll-over protection and seat belts required by 29 CFR 1926 shall be extended to include equipment regardless of year of manufacture.

## CONTRACT ADMINISTRATION

### AUTHORITY OF THE CONTRACTING OFFICER'S TECHNICAL REPRESENTATIVE (ENGINEER)

#### For purposes of execution of this project, the terms ‘Contracting Officer’s Technical Representative’ and ‘Engineer’ are understood to mean the same thing.

#### The authority of the Contracting Officer's Technical Representative for technical contract administration and inspection of the work is limited to the following functions:

##### Inspect and accept or reject work and materials including approval or disapproval of material submittals and shop drawings.

##### Insure compliance with all technical contract terms and conditions.

##### Clarify specifications and drawings where clarification does not involve contract cost or time.  Any disagreements with the Contractor over clarification of specifications and drawings are to be immediately referred to the Contracting Officer.

##### Verify, prepare, and recommend payment estimates on progress payments; forward to the Contracting Officer for approval.

##### Conduct "Labor Standards Interviews" in accordance with instructions from the Contracting Officer.  All known or suspected violations of the Labor Standards Provisions shall be reported immediately to the Contracting Officer.

##### Enforce safety requirements in accordance with the Federal Acquisition Regulations and Technical Specifications.

#### The Contracting Officer's Technical Representative (Engineer) is not authorized to take the following actions, all of which remain the sole responsibility of the Contracting Officer.

##### Make changes to the contract provisions, period of performance, or change any contract terms or conditions.

##### Make decisions concerning any claims and disputes under this contract.

#### Close liaison will be maintained by the Contracting Officer's Technical Representative, the Contracting Officer and the Contractor.  The Contracting Officer's Technical Representative shall notify the Contracting Officer immediately of any problems encountered, including but not restricted to maintaining completion of the Construction Schedule.

### AUTHORITY OF THE INSPECTOR

#### An Inspector employed by the Government will assist the Contracting Officer's Technical Representative (Engineer) in making inspections and measurements and will enforce strict compliance with the terms of the contract.

#### The Inspector shall have free access to the job site at all times while construction is in progress, and the Contractor shall furnish such information and assistance as may be necessary.

#### The Inspector shall, on a daily basis, record the work being accomplished, the trades working, materials delivered and/or installed, reasons for delays, and other pertinent information.

#### The Inspector may reject unsuitable materials or work not performed in accordance with the terms of the contract until the situation has been referred to and resolved by the Engineer and/or Contracting Officer.

#### The Inspector shall observe that all construction is performed in conformance with the contract health and safety requirements.

#### The Inspector shall conduct wage rate interviews and report suspected labor standard violations to Contracting and General Services.

#### The Inspector shall check and verify the Contractor's progress payment requests, if progress payments have been included in the contract.

#### No decisions or instructions of an Inspector will at any time relieve the Contractor from the responsibility of complying fully with all the requirements of the contract.  In cases of difference arising between an Inspector and the Contractor or his agent, appeal shall be taken to the Engineer.

#### Inspectors are not authorized to waive or alter in any respect any of the terms or requirements of the contract, to make additional requirements, to grant extensions of time or delays, or to waive forfeitures.  The Contractor shall not be entitled to payment for any work improperly performed with or without an Inspector's approval.

### PERFORMANCE OF WORK BY CONTRACTOR

#### The Contractor's procedure and methods of construction may, in general, be of his own choosing, provided they follow best general practice and are calculated to secure results which will satisfy the requirements of these specifications and the drawings.

#### The Contractor shall furnish the Engineer all reasonable facilities for obtaining such information as he may desire respecting the character of the materials and the progress of the work.

### PAYMENTS

#### Payments for work performed by the Contractor shall be made in accordance with the provisions of Clause 52.232-05 of Part 2, Section I of the Contract.

### DELIVERY, STORAGE, AND HANDLING

#### Contractor shall receive, unload, store in a secure place, and deliver from storage to the site all materials and equipment required for the performance of the work.  The storage facilities and methods of storing shall be designed to keep such materials and equipment in a new condition, free from deterioration and protected from damage by weather or construction activities.  Such facilities and methods are subject to the Contracting Officer's approval and the Contracting Officer shall have the right to inspect all storage facilities and stored materials and equipment at reasonable times.  Materials and equipment subject to degradation by outside exposure or the elements, such as mechanical equipment, building insulation, ornamental metal fabrications, gypsum board or case work, shall be suitably stored by Contractor in an indoor weather tight enclosure provided by the Contractor.  Contractor shall keep complete and accurate records of all materials and equipment received, stored, and delivered for use in the work.  Such records shall be made available for inspection by the Contracting Officer.  No payment will be made for materials purchased but not installed.  No additional expense shall be incurred by the Government for storage of materials.

## CONTRACT COMPLETION

### CLEANING UP

#### Rubbish shall not be allowed to accumulate on the site and the Contractor shall collect and remove, from time to time, such rubbish and debris incident to the execution of the contract as, in the opinion of the Engineer, may be undesirable or disfiguring on the premises.

#### Upon completion of the work, the Contractor shall remove from the vicinity thereof all plant, buildings, unused materials, concrete forms, rubbish, and other materials belonging to him or used under his direction during construction, as may be required by the Engineer, and in case of his failure to do so, the same may be removed by the Government at the expense of the Contractor, and the Contractor and his surety shall be liable therefore.

### FINAL INSPECTION

#### The Contractor shall notify the Engineer at least ten (10) days prior to the anticipated date of completion of all work specified in the contract.  Upon completion of the work, the Engineer shall proceed with final inspection and shall complete such inspection as promptly as practicable.  The time required for such inspection and the making of any corrections as a result thereof shall be included in the contract performance time.  No additional time shall be allotted for correction of items identified in the project Punch List.

### ACCEPTANCE AND FINAL PAYMENT

#### Final acceptance is the allowance of final estimates by the Contracting Officer.  The Engineer shall certify to the Contracting Officer that the contract is complete and include with the certification the amount of the final payment due the Contractor.  All progress or partial payments made prior to the final payment are subject to correction in the final estimate and payment.

### RELEASE OF CLAIMS

#### After completion of work, and prior to final payment, the Contractor shall furnish to the Contracting Officer a release of claims Form DI-137, properly executed by the Contractor, releasing claims against the United States arising out of the contract, other than claims specifically excluded from the operation of the release.

### ARCHAEOLOGICAL AND HISTORICAL DISCOVERIES

#### The Contractor shall immediately stop work if paleological, archaeological or historical remains (including burials or skeletal material) are encountered during performance of this contract.  The Contractor shall promptly notify the designated Inspector or the Contracting Officer (if the Inspector is absent or one was not designated for this contract).

After receiving such notification, the Contracting Officer will contact the Regional Archaeologist so that the provisions of 36 CFR 800.7 (Resources Discovered During Construction) and other relevant laws are followed.  Work will cease in the immediate vicinity until permitted by written order from the Contracting Officer.  The Contractor may proceed with work in other areas as approved by the Regional Archaeologist.

-END OF GENERAL REQUIREMENTS-

# Section 013300

## Submittals

## General

### Summary

#### This section covers submittals presented by the Contractor for review and approval to demonstrate conformance with the design concept and the Contract Documents.  This section includes definitions of the types of submittals required by the project specifications and specifies the administrative and procedural requirements for submittals.

### Definitions

#### Submittals

Shop drawings, product data, samples, and administrative submittals presented for review and approval.

#### Types of Submittals

The submittals also are grouped as follows:

##### Shop Drawings:  As used in this section, drawings, schedules, diagrams, and other data prepared specifically for this Contract, by the Contractor or through the Contractor by way of a subcontractor, manufacturer, supplier, distributor, or other lower tier contractor, to illustrate a portion of the work.

##### Product Data:  Preprinted material such as illustrations, standard schedules, performance charts, instructions, brochures, diagrams, manufacturer's descriptive literature, catalog data, and other data to illustrate a portion of the work, but not prepared exclusively for this Contract.

##### Samples:  Physical examples of products, materials, equipment, assemblies, or workmanship that are physically identical to a portion of the work, illustrating a portion of the work or establishing standards for evaluating the appearance of the finished work or both.

##### Administrative Submittals:  Data presented for reviews and approval to ensure that the administrative requirements of the project are adequately met but not to ensure directly that the work is in accordance with the design concept and in compliance with the Contract Documents.

#### Approving Authority

The person authorized to approve a submittal.

#### Work

As used in this Section, on and off-site construction required by the Contract Documents, including labor necessary to produce the construction and materials, products, equipment, and systems incorporated or to be incorporated in such construction.

### SUBMITTALS

#### Submit the following in accordance with the requirements of this section:  Filled in Submittal register.  See Paragraph 1.04 for instructions.

### SUBMITTAL REGISTER PREPARATION

#### Prepare and submit the Submittal Register.  A sample form is attached at the end of this section.  The submittal register with column (f) completed by the Contractor is the required submittal under this section.

#### For column (c), the specification paragraph number which contains either the reference to the submittal requirements or performance requirements for the submittal item is indicated.  Not all requirements will be referenced in this column.  The Contractor shall review the specifications to determine the additional requirements.

#### Column (e) identifies the submittals by category.  Category definitions are as follows:

Category 1	A submittal required with the bid.

Category 2	A submittal required under the bid item for submittals.

Category 3	A submittal or documentation required at project close out.

#### State for each submittal the Contractor's planned submittal date.  Submit the register within 15 days after Notice to Proceed.

### PROCEDURES FOR SUBMITTALS

#### Reviewing, Certifying, Approving Authority

The Contractor shall be responsible for reviewing and certifying that submittals are in compliance with contract requirements.  The approving authority on submittals is the Engineer unless otherwise specified for the specific submittal.

#### Constraints

##### Submittals listed or specified in this Contract shall conform to the provisions of this Section, unless explicitly stated otherwise.

##### Submittals shall be complete for each definable feature of work; components of the definable feature interrelated as a system shall be submitted at the same time.

##### When acceptability of a submittal is dependent on conditions, items, or materials included in separate subsequent submittals, the submittal will be returned without review.

##### Approval of a separate material, product, or component does not imply approval of assembly in which the item functions.

#### Scheduling

##### Coordinate scheduling, sequencing, preparing and processing of submittals with performance of the work so that work will not be delayed by submittal processing.  Allow for potential requirements to resubmit.

##### Except as specified otherwise, allow a review period, beginning with receipt by the Government that includes at least 20 working days for approval of submittals.  The period of review for each resubmittal is the same as for the initial submittal.

#### Variations or Substitutions

Substitution requests shall be in accordance with the following requirements. Whenever a material, article or piece of equipment is identified on the Drawings or in the Specifications by reference to manufacturers' or vendors' names, trade names, catalog numbers, or the like, it is so identified for the purpose of establishing a standard, and any material, article or piece of equipment or other manufacturers or vendors which will perform adequately the duties imposed by the general design will be considered equally acceptable, provided the material, article, or piece of equipment so proposed is, in the opinion of the Engineer, of equal substance, appearance and function.  It shall not be purchased or installed by the Contractor without the Engineer's prior written approval.

Offers of substitution of materials or equipment shall include data to substantiate that the "or equal" product meets the following criteria applicable to the time submitted.

##### The change is adaptable to the design,

##### The functional performance will be equal to or better than the item specified,

##### Where appearance affects the end product, the appearance of the item will be as good as or better than the item specified,

##### The maintenance cost for the product or item will be equal to or less than the item specified including establishing and maintaining necessary stock at the Government's facilities,

##### The quality of materials used and the level of construction of the item will be as good as or better than the item specified,

##### The net price of the item will be within the same price range as the item specified, and

##### The cost to the Government of furnishing and installing the item, including any necessary redesign costs by the Engineer which shall be reimbursed to the Government by the Contractor will be equal to or less than that of the item specified.

When substitute materials or equipment necessitates changes to or coordination with other portions of the work, the data submitted shall include Shop Drawings showing all such changes.  As part of any acceptance of substitute materials or equipment, the Contractor shall furnish all materials, perform all installation and make all other modifications as may be required to incorporate such changes at no additional cost to the Government.

Variations from contract requirements require Government approval.  When proposing a variation, submit a written request to the Government, with documentation of the nature and features of the variation and why the variation is desirable and beneficial to the Government.

Identify the proposed variation separately and include the documentation for the proposed variation along with the required submittal for the item.  When submitting a variation for approval, the Contractor warrants the following:

###### Variation Is Compatible

The Contract has been reviewed to establish that the variation, if incorporated, will be compatible with other elements of the work.

###### Contractor Is Responsible

The Contractor shall take actions and bear the additional costs.

###### Review Schedule Is Modified

In addition to the normal submittal review period, a period of 10 working days will be allowed for consideration by the Government of submittals with variations.

#### Contractor's Responsibilities

##### Determine and verify field measurements, materials, field construction criteria; review each submittal; and check and coordinate each submittal with requirements of the work and Contract documents.

##### Transmit submittals to the Government in orderly sequence, in accordance with the Submittal Register, and to prevent delays in the work, delays to the Government, or delays to separate contractors.

##### Advise the Engineer of variation, as required by the contract.

##### Correct and resubmit submittal as directed by the approving authority.  Direct specific attention, in writing or on resubmitted submittal, to any revisions not requested by the approving authority on previous submissions.

##### Complete work which must be accomplished as a basis of a submittal in time to allow the submittal to occur as scheduled.

##### Ensure no work has begun until submittals for that work have been returned as "Approved," or "Approved as Noted".

#### Government Responsibilities

##### Note the date on which the submittal was received from the Contractor on each submittal for which the Government is the approving authority.

##### Review submittals for approval within the scheduling period specified and for conformance with project design concepts and compliance with the Contract documents.

##### Identify returned submittals with one of the actions defined in the paragraph entitled "Actions Possible" and with markings appropriate for the action indicated.

##### Retain three copies of each submittal, except "Samples," where one copy will be retained.

#### Actions Possible

Submittals will be returned with one of the following notations:

##### Submittals marked "Approved" or "Approved as submitted" authorize the Contractor to proceed with the work covered.

##### Submittals marked "Approved as Noted” authorize the Contractor to proceed with the work as noted provided the Contractor takes no exception to the notations.

##### Submittals marked “Revise and Resubmit" or "Not Approved" indicate the submittal is incomplete or does not comply with the design concept or the requirements of the Contract documents and shall be resubmitted with appropriate changes.

### FORMAT OF SUBMITTALS

#### Transmittal Form

Transmit each submittal to the Government for approval.  Transmit submittals using the government furnished submittal form.

#### Identifying Submittals

Identify submittals with the following information permanently adhered to or noted on each separate component of each submittal and noted on the transmittal form.  Mark each copy of each submittal identically, with the following:

##### Project title and location.

##### Construction contract number.

##### Contractor's name.

##### Submittal number.

##### The Section number of the specification Section by which the submittal is required.

##### A brief description of each component of the submittal.

##### When a resubmission, an alphabetic suffix on the submittal description, for example, 10A, to indicate the resubmission of submittal number 10.

##### The name, address, and telephone number of the subcontractor, supplier, manufacturer and any other second tier contractor associated with the submittal.

##### Product identification and location in project.

#### Format for Product Data

##### Present product data submittals for each Section as a complete, bound volume.  Include a table of contents listing page and catalog item numbers for product data.

##### Indicate, by prominent notation, each product which is being submitted; indicate the specification Section number and paragraph number to which it pertains.

##### Supplement product data with material prepared for the project to satisfy submittal requirements for which product data does not exist. Identify this material as developed specifically for the project.

#### Format for Shop Drawings

##### Shop drawings shall not be less than 8.5 by 11 inches nor more than 22 by 36 inches.

##### Present 8.5 by 11 inch sized shop drawings as a part of the bound volume for the submittals required by the Section.  Present larger drawings in sets.

##### Include on each drawing the drawing title, number, date, and revision numbers and dates, in addition to the information required in the paragraph entitled "Identifying Submittals."

##### Dimension drawings, except diagrams and schematic drawings; prepare drawings demonstrating interface with other trades to scale.  Identify materials and products for work shown.

##### When shop drawings are prepared electronically, the Government's preferred standard is AutoCAD.

#### Format of Samples

##### Furnish samples in the sizes below, unless otherwise specified or unless the manufacturer has prepackaged samples of approximately the same size as specified:

###### Sample of Equipment or Device:  Full size.

###### Sample of Materials Less Than 2 by 3 inches:  Built up to 8.5 by 11 inches.

###### Sample of Materials Exceeding 8.5 by 11 inches:  Cut down to 8.5 by 11 inches and adequate to indicate color, texture, and material variations.

###### Sample of Linear Devices or Materials: 10 inch length or length to be supplied, if less than 10 inches.  Examples of linear devices or materials are conduit and handrails.

###### Sample of Non-Solid Materials:  Pint.  Examples of non-solid materials are sand and paint.

###### Color Selection Samples:  2 by 4 inches.

###### Sample Panel:  4 by 4 feet.

###### Sample Installation:  100 square feet.

##### Samples Showing Range of Variation:  Where variations are unavoidable due to the nature of the materials, submit sets of samples of not less than three units showing the extremes and middle of the range.

##### Reusable Samples:  Incorporate returned samples into the work only if so specified or indicated.  Incorporated samples shall be in undamaged condition at the time of use.

##### Recording of Sample Installation:  Note and preserve the notation of the area constituting the sample installation but remove the notation at the final clean up of the project.

##### When a color, texture or pattern is specified in naming a particular manufacturer and style, include one sample of that manufacturer and style, for comparison.

#### Format of Administrative Submittals

##### When the submittal includes a document which is to be used in the project or become a part of the project record, other than as a submittal, do not apply the Contractor's approval stamp to the document, but to a separate sheet accompanying the document.

##### Operation and Maintenance Manual Data:  Submit in accordance with this section.  Include components required in the various technical sections.

### QUANTITY OF SUBMITTALS

#### Number of Copies of Product Data

Submit six copies of submittals of product data requiring review and approval.

#### Number of Copies of Shop Drawings

For shop drawings submit six copies of prints of each shop drawing prepared for this project.

#### Number of Samples

##### Submit three samples, or three sets of samples showing range of variation, of each required item.  Two approved samples or sets of samples will be retained by the Government and one will be returned to the Contractor.

##### Submit one sample panel.  Include components listed in technical section or as directed.

##### Submit one sample installation, where directed.

##### Submit one sample of non-solid materials.

#### Number of Copies of Administrative Submittals

##### Unless otherwise specified, submit six copies of administrative submittals which are 8.5 by 14 inches or smaller in size for product data.

##### Unless otherwise specified, submit six copies of administrative submittals larger than 8.5 by 14 inches for shop drawings.

##### Operation and Maintenance Manuals:  Submit in accordance with the requirements of applicable sections.

##### Guarantees, Warranties and Certificates:  Submit in accordance with the requirements of Section 017000.

##### As Built Drawings:  Submit in accordance with the requirements of Section 010000.

## SUBMITTAL REGISTER

| No. (a) | Spec. Sect. (b) | Spec. Paragraph (c) | Type of Submittal/Description of Submittal (d) | Category (e) | Planned Submit. Date (f) |
| --- | --- | --- | --- | --- | --- |
|  | 011000 | 1C.03.A | Construction Schedule | 2 |  |
|  | 011000 | 1C.03.B | Payment Schedule | 2 |  |
|  | 011000 | 1C.03.D | As-Built Drawings | 3 |  |
|  | 011000 | 1C.03.E | O&M Manuals | 3 |  |
|  | 011000 | 1F.04.A | Release of Claims Form | 3 |  |
|  | 013300 | 1.04 | Submittal Register | 2 |  |
|  | 017700 | 1.06.A | Assembled Warranty Documents | 3 |  |
|  | 017700 | 1.06.B | Final Application for Payment | 2 |  |
|  | 024119 | 1.04.A | Plan For Demolition Debris Control | 2 |  |
| 10 | 024119 | 1.04.B | Disposal Site Identification | 2 |  |
| 11. | 032000 | 1.04.A | Reinforcing Steel Shop Drawings | 2 |  |
| 12. | 033000 | 1.04.A | Concrete Mix Design | 2 |  |
| 13. | 033000 | 1.04.B | Concrete Curing Methods | 2 |  |
| 14. | 033000 | 1.04.C | Concrete Repair Methods | 2 |  |
| 15. | 033000 | 1.04.D | Construction Joints | 2 |  |
| 16. | 033000 | 1.04.E | Qualifications of Finishers | 2 |  |
| 17. | 033000 | 1.04.F | Records | 2 |  |
| 18. | 110000 | 1.02.A | Shop drawings/product data for crest gate. | 2 |  |
| 19. | 260500 | 1.03.A | Electrical Panel | 2 |  |
| 20. | 260500 | 1.03.B | Triplexed Overhead Wire | 2 |  |
| 21 | 260500 | 1.13.A | Certification | 3 |  |
| 22. | 260500 | 1.11 | As-Built Drawings | 2 |  |
| 23. | 260500 | 1.14 | Materials and Workmanship Guarantee | 2 |  |
| 24. | 260500 | 2.02 | Rigid Metal Conduit | 2 |  |
| 25. | 260500 | 2.03 | Rigid Non-Metallic Conduit | 2 |  |
| 26. | 260500 | 2.04 | Liquidtight Flex. Metal Conduit | 2 |  |
| 27. | 260500 | 2.05 | Expansion Fittings | 2 |  |
| 28. | 260500 | 2.06 | Insulated Bushings | 2 |  |
| 29. | 260500 | 2.07 | Power and Control Conductors | 2 |  |
| 30. | 260500 | 2.08 | Wiring Connectors | 2 |  |
| 31. | 260500 | 2.11 | Electrical Panels | 2 |  |
| 32. | 260500 | 2.12 | Pull and Junction Boxes | 2 |  |
| 33. | 260500 | 2.16 | Supporting Devices | 2 |  |
| 34. | 260500 | 2.18 | Circuit Breakers | 2 |  |
| 35. | 133423 | 1.4.B | Product Data | 2 |  |
| 36. | 133423 | 1.4.C | Shop Drawings | 2 |  |
| 37. | 133423 | 1.4.D | Calculations | 2 |  |
| 38. | 133423 | 1.4.E | Samples | 2 |  |
| 39. | 133423 | 1.4.F | Manufacturer’s Installation Instructions | 2 |  |
| 40. | 312319 | 1.4 | Dewatering Plan |  |  |
| 41. | 354337 | 1.4 | Gradation Report |  |  |

Notes:

Submittals listed in this register pertain only to the Technical Specifications.

Submittal requirements listed in the above table do not necessarily represent the complete submittal requirements of these Specifications.  Contractor is required to meet these and any other submittal requirements stated in these Specifications.

-END OF SUBMITTALS-

# Section 017700

## CONTRACT CLOSEOUT

## GENERAL

### SECTION INCLUDES

#### Closeout procedures.

#### Final cleaning.

#### Warranties.

### Related sections

#### Section 010000 – General Requirements

#### Section 013300 - Submittals

### CLOSEOUT PROCEDURES

#### Provide submittals to the Government that are required by governing or other authorities in accordance with Section 010000 and Section 013300.

#### Submit final Application for Payment identifying total adjusted Contract Sum, previous payments, and sum remaining due.

#### The Contractor or his project supervisor shall be at the jobsite during the final inspection.

### FINAL CLEANING

#### Execute final cleaning prior to final project assessment.  Refer to Section 010000, Paragraph 1F – CONTRACT COMPLETION.

### WARRANTIES

#### The Contractor agrees that all materials and equipment furnished pursuant to the Contract shall be free from all inherent defects in workmanship and material and shall give proper and continuous service under all conditions of service required and specified or which may be reasonably inferred from the Contract Documents.  The Contractor shall immediately upon receiving notice from the Government repair or replace any materials or equipment which, under normal and proper use, proves defective within one year from the date of acceptance by the Government.  The warranty provided herein is in lieu of all other warranties, express or implied, including without limitation any implied warranty of merchantability or fitness for a particular purpose, but is not intended to reduce the warranty periods of product manufacturer’s extended warranties which shall remain in effect in full.

#### Execute and assemble warranty documents from Subcontractors, suppliers, and manufacturers.

### Submittals

Submit the following in accordance with the requirements of this section, Section 010000, and Section 013300.

#### Assembled warranty documents:  Provide Table of Contents and assemble warranty documents in standard three-hole punch, D-ring style, and binder with durable plastic cover.  Submit prior to Final Application For Payment.

#### Final Application For Payment

## PRODUCTS

NOT USED

## EXECUTION

NOT USED

-END OF Contract CLOSEOUT-

### SECTION 024119

DEMOLITION

# PART 1 - GENERAL

1.01	RELATED WORK SPECIFIED ELSEWHERE

- The provisions and intent of the Contract, including the General Requirements, apply to this work as if specified in this section.

1.02	DESCRIPTION OF WORK

##### The extent and location of the "Demolition" work is indicated on the Drawings.  The work includes the requirements for the removal, wholly or in part, and satisfactory disposal of all concrete weir constituent portions (including reinforcing steel) and steel embedded items.

- The Demolition work is included on the Drawings for guidance only to indicate typical general construction features of the various types of structures and is not to be construed as definitive or adequate to supplant the actual on-site inspection by the Contractor.

- The Demolition work will occur in the watercourse of Clear Creek, a tributary to the Clearwater River.  The Contractor shall allow no products of demolition to enter the Clear Creek.

1.03	JOB CONDITIONS

The Contractor represents that it has visited the site to become familiar with the quantity and character of all materials to be demolished.  The Contractor agrees that the premises were made available prior to deadline for submission of bids for whatever inspection and tests the Contractor deemed appropriate.  The Contractor assumes full responsibility for the proper disposal of all demolition materials.

1.04	SUBMITTALS

A.	Contractor shall submit a plan for preventing debris from entering Clear Creek and shall submit the plan to the Engineer for approval prior to demolition.

B.	Two weeks prior to transport, the Contractor shall submit to the Engineer the name of recycling or disposal facilities and documentation that the facility is permitted to receive such materials.

PART 2 - PRODUCTS

2.01	GENERAL

Products that are required to accomplish, or to be incorporated into, the work of this section shall be as selected by the Contractor, subject to the approval of the Engineer.

2.02	SALVAGE ITEMS

No items are to be salvaged by the Government.  All products of demolition become the property of the Contractor.

2.03	WORK BY UTILITY

The Contractor shall contact all utilities within limits of this project and have them mark their utilities prior to the start of construction.  It shall be the Contractor’s responsibility to protect the utilities from damage during the construction of this project.

PART 3 - EXECUTION

3.01	DEMOLITION OF STRUCTURES

A.	The Contractor shall completely remove and dispose of designated structures, and other obstructions.  Adjacent materials designated to remain that are damaged by the Contractor due to his operations shall be replaced at no additional cost to USFWS.

B.	Blasting or other special operations necessary for the removal of an existing structure or obstruction shall be subject to the approval of the Engineer.

- During demolition operations, the Contractor shall allow no material to enter Clear Creek.  The Contractor shall be responsible for providing all scaffolding, falsework and debris capturing and containment devices to prevent debris from entering Clear Creek.

D.	Reinforced concrete members that will be partially demolished and modified require special consideration during demolition to prevent damage to the remaining concrete and reinforcement.  The Contractor shall be responsible for preventing damage to remaining concrete and reinforcement and shall repair damage at no additional cost to the USFWS.

Special demolition controls shall be used when demolition is within 6" of the finished demolished surface as shown on the Plans and within 2" of all reinforcement required to be incorporated into the work.  Power driven tools will be permitted.  Jack hammers and concrete chipping hammers heavier than 30 lb class and 15lb class respectively shall not be used.  Jack hammers and mechanical chipping tools shall not be operated at an angle in excess of 45o measured from concrete surfaces.

Saw cutting shall be accomplished to prevent damage to embedded reinforcement that will be incorporated into the work.  Damaged reinforcement shall be replaced as directed by the Engineer at no additional cost to the Port.

- In the case of concrete demolition work, the Contractor shall provide all work required for fugitive dust and potential silica-generating construction dust control activities in accordance with the latest applicable state and federal regulations.

3.02	DISPOSAL

- General:  All materials shall upon their demolition or severance become the property of the Contractor.  Such material shall be removed and promptly recycled or disposed of in accordance with all applicable laws and regulations at an industrial or commercially zoned facility permitted to receive such material.

- The USFWS encourages the salvage and recycling of materials from demolished structures.  The Contractor shall salvage or recycle, in an acceptable manner to environmental agencies and the USFWS, at its option and of the materials designated for disposal.

- No material shall be placed on property owned by the USFWS except as otherwise provided herein.  No material shall be disposed of in adjoining waterways.

- Upon request, the Contractor shall submit to the Engineer receiving tickets or other documentation demonstrating appropriate disposal of material.

PART 4- MEASUREMENT AND PAYMENT

A.	No separate measurement or payment will be made for Demolition.  The costs for this portion of the work shall be considered incidental to, and included in, the various lump sum and unit prices bid for the project.

-END OF DEMOLITION-

# SECTION 032000

CONCRETE REINFORCEMENT

PART 1 - GENERAL

1.01	RELATED WORK SPECIFIED ELSEWHERE

The provisions and intent of the Contract, including the General Requirements, apply to this work as if specified in this section.  Work related to this section is described in:

A.	Section 013300 - Submittals

B.	Section 033000 - Cast-in-Place Concrete

1.02	DESCRIPTION OF WORK

The Work includes the requirements for manufacture, detailing, cutting, bending, transporting, and placing of all concrete reinforcement and associated items required or indicated on the Drawings.

1.03	QUALITY ASSURANCE

A.	Qualifications of Workers:  Provide at least one (1) person who shall be present at all times during execution of this portion of the Work and who shall be thoroughly familiar with the type of materials being installed and the best methods for their installation and who shall direct all work performed under this section.

B.	Codes and Standards:  In addition to complying with all pertinent codes and regulations, comply with all pertinent recommendations contained in "Manual of Standard Practice for Detailing Reinforced Concrete Structures," publication ACI 315-80 of the American Concrete Institute.

1.04	SUBMITTALS

A.	Within fifteen days after award of Contract, and before any concrete reinforcement materials are delivered to the job site, submit shop drawings to the Engineer for review and approval.

B.	Do not deliver concrete reinforcement to the job site until receipt of Shop Drawings approval from the Engineer.

1.05	PRODUCT HANDLING

A.	Protection:

1.	Protect reinforcement before, during, and after installation and protect the installed work and materials of other trades.

2.	Store in a manner to prevent fouling with dirt, grease, and other bond-breaking coatings.

3.	Use all necessary precautions to maintain identification after the bundles are broken.

B.	Replacements:  In the event of damage, immediately make all repairs and replacements necessary to the approval of the Engineer at no additional cost to the USFWS.

PART 2 - PRODUCTS

2.01	GENERAL

All concrete reinforcement materials shall be new and free from rust, and shall comply with the following reference standards:

A.	Bars for reinforcement shall comply with the requirements of "Specifications for Deformed and Plain Billet-Steel Bars for Concrete Reinforcement," ASTM Designation A615, Grade 60.

B.	Wire for reinforcement shall comply with the requirements of "Specifications for Steel Wire, Plain, for Concrete Reinforcement," ASTM Designation A82.

C.	Wire fabric shall comply with the requirements of "Specifications for Steel Welded Wire, Fabric, Plain, for Concrete Reinforcement," ASTM Designation A185.

D.	Wire for spiral reinforcement shall be hot-rolled (Grade 60).

E.	Bar Supports:  In accordance with the CRSI Manual of Standard Practice; types and sizes as required for the conditions of the installation.

1.	For exposed to view concrete surfaces where legs of supports are in contact with forms, provide supports with legs that are plastic protected, or stainless steel, in accordance with CRSI Class 1 or Class 2 (Types A and B). Metal chairs, which are in contact with the exterior surface of the concrete, shall be plastic-coated or stainless steel.

2.	Provide precast concrete blocks not less than 4-inches square when supporting reinforcing steel on ground.  Precast concrete blocks shall have a compressive strength equal to that of surrounding concrete.

F.	Tie Wire: ASTM A82, No. 16-gage minimum, double annealed black wire.

2.02	OTHER MATERIALS

All other materials, not specifically described but required for a complete and proper installation of reinforcement, shall be selected by the Contractor, subject to the approval of the Engineer.

PART 3 - EXECUTION

3.01	GENERAL:

Prior to installation of this section, carefully inspect the installed work of other trades and verify that such work is complete to the point where this installation may properly commence.

3.02	REINFORCING STEEL BARS

A.	Order Lists:  Before ordering material, furnish all order lists and bending diagrams for approval by the Engineer; reinforcement placing drawings submitted for approval shall conform to CRSI detailing practice.  Do not order material until such lists and bending diagrams have been approved.  The approval of order lists and bending diagrams by the Engineer shall in no way relieve the Contractor of responsibility for the correctness of such lists and diagrams.

B.	Fabrication:  Bend all bars cold to the shapes indicated on the Drawings unless otherwise approved by the Engineer.  Do not field-bend bars partially embedded in concrete except as indicated on the Drawings or as approved by the Engineer.  Make bends and hooks in accordance with the applicable portions of the Concrete Reinforcing Steel Institute.

C.	Placing and Fastening:

1.	Place all steel reinforcement accurately and hold firmly in the position indicated on the Drawing during the placing and setting of concrete.  Tie bars at all intersections, except where spacing is less than one foot in each direction, then tie alternate intersections.

2.	Provide the following minimum concrete covering of reinforcement:

a.	Concrete below ground deposited against forms: Two (2) inches

b.	Concrete deposited against earth: Three (3) inches

c.	Concrete elsewhere: As indicated on the Drawings or otherwise approved by the Engineer.

3.	Maintain the minimum distance from the forms by means of stays, blocks, ties, hangers, or other approved supports.  Blocks, for holding reinforcement from contact with the forms, shall be precast mortar blocks of compressive strength not less than 3750 psi of approved shape and dimensions, or approved metal chairs.  Metal chairs which are in contact with the exterior surface of the concrete shall be plastic-coated or stainless steel.  Separate layers of bars by plastic chairs, by precast mortar blocks of compressive strength not less than 3750 psi, or by other equally suitable devices.  The use of pebbles, pieces of broken stone, brick, metal pipe, and wooden blocks will not be permitted.  The minimum spacing between bars shall be one bar diameter or one inch minimum, but not less than 1-1/3 times the maximum size of coarse aggregate.  Place reinforcement; inspect; and obtain approval of the Engineer before placing concrete.  Concrete placed in violation of this provision may be rejected and removal required, to be followed by placing of new reinforcing steel and concrete by the Contractor at no additional cost to the Port.

4.	In the event that conduits, piping, inserts, sleeves, or other items interfere with placing reinforcement as indicated on the Drawings or as otherwise required, immediately consult the Engineer and obtain approval of new procedure before placing concrete.

D.	Splicing:

1.	Refer to Development Length and Lap Splice Length Table, Table 4, Drawing No. 1F-ID-733-181-2.0.

3.03	DEFECTIVE WORK

A.	General:  The following reinforcing steel work will be considered defective and shall be removed and replaced by the Contractor at no additional cost to the Owner:

1.	Bars with kinks or bends not shown on the approved Drawings

2.	Bars damaged due to bending or straightening

3.	Bars heated for bending

3.04	CLEANING REINFORCEMENT

Steel reinforcement, at the time concrete is placed around it, shall be free from loose rust or mill scale, oil, paint, and all other coatings which will destroy or reduce the bond between steel and concrete.

PART 4- MEASUREMENT AND PAYMENT

No separate measurement or payment will be made for Concrete Reinforcement.  The costs for this portion of the work shall be considered incidental to, and included in, the various lump sum and unit prices bid for the project.

# -END OF CONCRETE REINFORCEMENT-

# SECTION 033000

CAST-IN-PLACE CONCRETE

# PART 1 - GENERAL

1.01	RELATED WORK SPECIFIED ELSEWHERE

The provisions and intent of the Contract, including the General Conditions, Supplementary Conditions, and General Requirements, apply to this Work as if specified in this section.  Work related to this section is described in:

A.	Section 013300 - Submittals

B.	Section 032000 – Concrete Reinforcement

1.02	DESCRIPTION OF WORK

The extent and location of the "Cast-In-Place Concrete" Work is indicated on the Drawings.  The Work includes the requirements for providing all cast-in-place concrete and associated work in conformance with these Specifications and to the dimensions indicated on the Drawings.

1.03	QUALITY ASSURANCE

The USFWS will provide inspection service to the satisfaction of the Owner.  The Contractor may obtain the results of tests performed by the USFWS from the office of the Engineer at no cost.

A.	Qualifications of Manufacturer:  Ready-mixed concrete plants shall be approved and certified.  Ready-mixed concrete shall be batched in accordance with the applicable portions of ASTM Designation C94.

B.	Qualifications of Workers:

1.	Provide at least one person who shall be present at all times during execution of this portion of the work and who shall be thoroughly trained and experienced in placing the types of concrete specified and who shall direct all work performed under this section.

2.	Thoroughly trained and experienced journeyman concrete finishers shall be responsible for finishing of exposed surfaces.

C.	Codes and Standards:  All concrete shall meet the requirements of the International Building Code, 2003 Edition.  All concrete is reinforced, unless stated otherwise.  The amount of reinforcing shall not be less than the minimum required by the Code.  Where provisions of pertinent codes and standards conflict with this Specification, the more stringent provisions shall govern.

1.04	SUBMITTALS

A.	Submit to the Engineer the proposed design mix for each class of concrete required for this portion of the Work.  Also submit the manufacturer's name and catalog number of items such as membranes, all admixtures, and the name and address of the proposed concrete supplier.

B.	Curing Methods:  Submit written methods, procedures, and products for curing all concrete.

C.	Repair Methods:  Submit the proposed methods of repair, along with repair material specification, manufacturer’s data on the proposed patching material, and the proposed preparation and application procedure.

D.	Construction Joints:  Submit information for acceptance of proposed location and treatment of construction joints proposed but not indicated on the Construction Documents.

E.	Qualifications of Finishers:  Submit qualifications of the finishing contractor and finishers who will perform the work.

F.	Records:  Retain records of all concrete placed, including exact mix proportions, slumps, test strength, date, time, location of the placement, weather conditions at the time of placement, and the source of concrete.  Submit copy to the Engineer.

1.05	PRODUCT HANDLING

Ready-mixed concrete shall be placed in its final position within 1-1/2 hours after the addition of cement.

A.	Retempering:  Mix concrete only in such quantities as are required for immediate use, and use while fresh before initial set has taken place.  Concrete which has developed initial set shall not be used.  Concrete which has partially hardened shall not be retempered or remixed.  Disposal of such concrete shall be at the sole expense of the Contractor.

B.	Protection:  Use all means necessary to protect cast-in-place concrete materials before, during, and after installation and to protect the installed work and materials of all other trades.

C.	Replacement:  In the event of damage, immediately make all repairs and replacements necessary to the approval of the Engineer and at no additional cost to the USFWS.

PART 2 - PRODUCTS

2.01	CONCRETE

A.	General:

1.	All concrete, unless otherwise specifically permitted by the Engineer, shall be batched and mixed at one of the approved plants.

B.	Quality:

1.	Concrete shall have a minimum 28 day compressive strength (f’c) of 4,000 psi.  Concrete shall be proportioned within the following limits unless approved otherwise after submittal of a mix design.

Minimum psi  Minimum Sacks of   Maximum

@ 28 days    	  Cement/C.Y.**    	     Slump

4000			6.5			3"

For plant-mix concrete, a certificate showing proportions and the 28-day strength of the concrete mix being furnished shall be obtained from the supplier and furnished to the Engineer.

Concrete shall contain an air-entraining admixture resulting in a minimum of 4 ½%  +/- 1% of air.

2.	Concrete may contain an appropriate amount of Fly Ash as a pozzolanic material.  Concrete mix designs, including Fly Ash, shall be prepared by a certified laboratory and have the approval of the Engineer prior to use.  Mix designs submitted without a verifiable break history as described in the IBC will not be accepted.

C.	Cement

1.	All cement shall be Portland cement conforming to ASTM Designation C150, Type I or III, and shall be the product of one manufacturer.

2.	Type III cement shall be used for all concrete unless the use of Type I cement is specifically authorized in writing by the Engineer.  The use of Type I cement will be authorized only if the Contractor can demonstrate, by preparation of and adherence to a construction schedule approved by the Engineer, that the project will be completed within the stipulated contract time using the Type I cement.

D.	Aggregates

1.	All coarse and fine aggregate shall consist of hard, tough, durable, particles free from foreign materials, and shall be stored in such a manner as to prevent segregation, excessive breakage, and the introduction of foreign material.  Aggregate shall conform to ASTM C 33.  The maximum size of coarse aggregate shall not be larger than three fourths of the minimum clear spacing between reinforcing steel bars and/or between bars and side forms and/or between bars and top or bottom surface of the concrete.  Lightweight aggregate or aggregate larger than 1-1/2 inch shall not be used without written permission from the USFWS.

E.	Water

1.	Water for concrete shall be clear and apparently clean.  If the water contains substances that cause discoloration, unusual or objectionable smell or taste, or other suspicious content, the Engineer may require the Contractor to provide test results documenting that the water meets the physical requirements and chemical limits described in ASTM C94 Section 5.1.3, Tables 2 and 3.

F.	Admixtures:  All admixtures shall be supplied by one manufacturer approved by the Engineer.

1.	Air-Entraining Agents shall be Edoco, MB VR, MB AE-10, or approved equal, added as directed by the Engineer to obtain (4-1/2%) entrained air.

2.	Water-Reducing Agents shall be "Pozzolith," or approved equal, conforming to ASTM C494, Type A for water-reducing, Type D for water-reducing and retarding, and Type E for water-reducing and accelerating.

3.	Accelerators shall be approved by the Engineer prior to use.

4.	Retarders shall be approved by the Engineer prior to use.

5.	Nonshrink Additives shall be "Isovol," "Embeco," or an approved mix design.  The mix design shall be tested in accordance with ASTM C827 for volume change, ASTM C187 and C143 for workability, and ASTM C39 for compressive strength.  The use of powdered aluminum will not be permitted without written permission of the Engineer.

2.02	MEMBRANES

A.	Curing Membrane:  All curing membrane shall be sheet plastic as specified for vapor barrier, a combination sheet plastic and paper, or an equal approved in advance by the Engineer.

B.	Jointing Material:  All cement or tape used for sealing membrane joints shall be only as recommended by the manufacturer of the membrane being joined.

2.03	NON-SHRINK GROUT

Premixed and packaged, non-metallic, tested to comply with ASTM C827 for volume change, ASTM C187 and C143 for workability, and ASTM C39 for compressive strength.  The use of powdered aluminum will not be permitted.

2.04	OTHER MATERIALS

All other materials not specifically described but required for a complete and proper installation of cast-in-place concrete shall be as selected by the Contractor subject to the approval of the Engineer.

PART 3 - EXECUTION

3.01	PREPARATORY WORK

A.	Inspection

1.	Prior to all work of this section, carefully inspect the installed work of all other trades and verify that all such work is complete to the point where this installation may properly commence.

2.	Verify that all items to be embedded in concrete are in place, properly oriented, located, and secured.

3.	Verify that concrete may be placed to the lines and elevations indicated on the Drawings with all required clearances for reinforcement.

B.	General

1.	Thoroughly clean all areas in which concrete is to be placed.  Clean and roughen existing concrete or concrete from a previous pour to provide a bondable surface.  Thoroughly wet down concrete forms which have not been treated with oils, waxes, or other bond breakers prior to placing concrete.

2.	Clean all transporting and handling equipment of all hardened concrete.  No cleaning debris will be allowed to remain on USFWS property.

C.	Discrepancies:  In the event of discrepancy, immediately notify the Engineer.  Do not proceed with installation until all discrepancies have been fully resolved.

D.	Notification:  Notify the Engineer and Hatchery Manager at least 48 hours in advance of concrete placement.

3.02	PLACING CONCRETE:

A.	General

1.	Place concrete as soon as possible after mixing.  Concrete shall be plastic and readily workable when placed in the forms.  Concrete that does not reach its final position in the forms within 1-1/2 hours after the addition of cement shall not be used.

2.	The method and manner of placing concrete shall not allow segregation of the aggregates, or displacement of reinforcement.

3.	Conveyor belts, when used, shall be limited to approximately 300 feet in length to prevent segregation and shall be covered to protect the concrete from sun or rain.

4.	Do not use aluminum conduits or tremis for pumping or placing concrete.

5.	Place concrete in continuous horizontal layers and compact so that there will be no line of separation between layers.  Carefully fill each part of the forms by depositing concrete directly at or as near as possible to the final position.

6.	When concrete must be dropped more than five feet into the forms, it shall be deposited through approved conduit.  Approved conduit shall also be used to place concrete in sloping forms or in other locations, as directed, to prevent concrete from sliding around reinforcing or other embedments.

7.	In general, the method of depositing and compacting concrete shall be conducted to form a compact, dense, impervious concrete with the required surface and a minimum of segregation.  Remove defective concrete as directed by the Engineer at no additional cost to the USFWS.  "Plastering" will not be permitted.

8.	Do not place concrete where other work in the area, such as the driving of piling or sheets, or other vibratory action, will adversely affect the initial set or strength of the concrete.

B.	Cold Weather Placement

1.	Do not place concrete on frozen ground or against frosted reinforcing steel or forms.  Do not mix or place concrete while the atmospheric temperature is below 40° F.

2.	During cold weather, perform all cold weather concreting in accordance with ACI 306, "Cold Weather Concreting".

C.	Hot Weather Placement

1.	Temperature of concrete shall not exceed 90 degrees Fahrenheit.

2.	Steel forms, dowels and reinforcing shall be cooled prior to concrete placement when steel temperatures are greater than 120 degrees Fahrenheit.

3.	See ACI 305R for additional information.

D.	Underwater Placement:  In no case place concrete in running water.  Whenever permission is given to place concrete under water, place concrete within the confines of a compartment, such as a cofferdam, tube, or caisson.  Method of placement, forms, confining structure, special concrete mix, and all equipment shall have prior approval of the Engineer.

E.	Vibration of Concrete:  Provide suitable internal vibrating tampers for use in placing and compacting all concrete except that which is placed under water.  The vibrators shall be of the type designed to be placed directly in the concrete, and their frequency of vibration shall be not less than (7,000) impulses per minute when in actual operation.  The type of vibrator and its method of use shall be subject to the approval of the Engineer.

Vibration shall be such that the concrete becomes uniformly plastic.  Insert vibrators to a depth sufficient to vibrate the bottom of each layer effectively, but do not penetrate partially hardened concrete.  Do not apply the vibrators directly to steel which extends into partially hardened concrete.

Do not continue vibration in any one spot until pools of grout are formed.  In vibrating and finishing top surfaces which are exposed to weather or wear, extreme care shall be exercised to avoid drawing water or laitance to the surface.  In relatively high lifts, the top layer shall be comparatively small and the concrete mix shall be as stiff as can be effectively vibrated into place and properly finished.  Do not use vibrators to transport or move concrete inside the form.

Supply a sufficient number of vibrating tampers to effectively vibrate all of the concrete placed.  Hand-tamping shall be required wherever necessary to secure a smooth and dense concrete on the outside surfaces.

3.03	FINISHING CONCRETE SURFACES

Finish concrete surfaces in accordance with the procedure specified for each type of surface.

A.	Unformed Surfaces

The surface shall be rodded across the screeds and smoothed with a "bull float"; the larger aggregate shall be depressed with a "jitter bug" or similar device; and the surface shall be hand- or power-steel-troweled to a finish that has no irregularities greater than 1/32 inch in depth and shall not vary from a true plane by more than 1/8 inch in ten feet.

B.	Formed Surfaces

The surface shall be ground smooth to remove all fins and protrusions, all rock pockets, and tie holes, and shall be repaired by dry-packing.  All depressions shall be filled with a one-to-one sand cement grout and sack- or carpet-rubbed with a one-to-one sand/cement dry mix.  The surface plane dimension shall be within a tolerance of plus or minus 1/4 inch of design dimensions, and the surface shall be free of irregularities greater than 3/16 inch in ten feet in any direction.

3.04	CURING CONCRETE

A.	Keep all concrete surfaces continuously wet with water for not less than three days after the concrete is placed.  This curing may be done by covering the surface with cotton mats, burlap, or white polyethylene sheeting or by wetting the outside surfaces of the forms.  Keep all other concrete continuously wet with water for not less than ten days when Type I cement is used and not less than three days when Type III cement is used.  Retaining walls may be cured by wetting the outside surfaces of the forms or covering the outside surfaces with white polyethylene sheeting.

B.	Use white-pigmented-type curing compound, except that when bonding other materials to the concrete surface is required, the clear-type curing material shall be used.  Thoroughly agitate the white-pigmented-type curing compound immediately before and during application.

C.	Supply a separate work bridge, backup spray equipment, and sufficient workmen to properly apply the curing compound.

D.	Not later than ten-hours following the application of the curing compound, the top surfaces shall be covered with cotton mats, two-inches of clean sand, an approved vapor proof curing paper, or white polyethylene sheeting.  If the covering used is gravel or cotton mats, it shall be kept continuously wet day and night for the period of time specified above, and if curing paper or plastic film is used, it shall be left in place for the same length of time.

E.	Curing paper and white polyethylene sheeting must be kept tightly in place by taping and weighting joints, or other methods as the Contractor may devise, for the prescribed length of time.

F.	Sprinkling, ponding, or covering with material other than clean gravel, cotton mats, curing paper, or white polyethylene sheeting will not be allowed.

G.	Membrane curing compounds which leave a waxy film on the concrete will not be allowed.

H.	After the concrete has cured for the required time, the gravel covering, if used, shall be removed and the slabs shall be swept clean.

3.05	PROTECTION OF INSTALLED WORK

A.	After curing as specified herein, cover slabs with plywood or particle board or plastic sheeting or other material to protect from material and damage due to other construction work.

B.	Repair defective areas and areas damaged by construction.

PART 4- MEASUREMENT AND PAYMENT

#### No separate measurement or payment will be made for Cast-In-Place Concrete.  The costs for this portion of the work shall be considered incidental to, and included in, the various lump sum and unit prices bid for the project.

## -END OF CAST-IN-PLACE CONCRETE-

# SECTION 110000

# PNEUMATIC CREST GATES

## Part 1 -GENERAL

### 1.1	RELATED DOCUMENTS

A. 	The provisions and intent of the Contract, including the General Requirements, apply to this work as if specified in this section.

### 1.2	DESCRIPTION OF WORK

A. 	This Section includes the design and fabrication requirements for procurement and installation of pneumatic crest gates and appurtenances for control of water at the Kooskia National Fish Hatchery Project  near Kooskia, Idaho.  The pneumatic crest gate is intended to function to allow flushing of bed load (sand, gravel, cobbles, and rock) over the crest gate and past the existing water intake and concrete weir structure at the existing hatchery water diversion on Clear Creek during high water flow events.  All components of the supplied system shall be designed to be compatible with the intended use of the system.

B.	Items to be supplied by the pneumatic crest gate supplier include (but are not limited to) the following:

##### Stainless steel gate panel(s).

##### Polyester reinforced air bladder(s) for above gates and associated piping components to attach to Contractor supplied main air piping.

##### Reinforced rubber interpanel seals and stainless steel attachment hardware.

##### Spillway gate clamping hardware and stainless steel anchor bolts, nuts, and washers.

##### Reinforced rubber restraining straps and stainless steel attachment hardware.

##### Knappe breakers and stainless steel attachment hardware.

##### UHMW polyethylene abutment plates with stainless steel anchor bolts, nuts, and washers.

##### Automatic gate control system (with manual override capability) complete and ready for installation.  System shall be provided with pneumatic water level controller to be able to automatically regulate air bladder pressure.

##### Anchor bolt setting template (if required).

##### Installation supervision and training by Manufacturer’s technician as outlined in proposal.

##### Delivery FOB Destination with freight prepaid.

##### Two-year written warranty on pneumatic crest gate system.

C.	Work to be performed by the Contractor:

##### Verify conditions.

##### Any required concrete work or civil modifications.

##### Air supply pipe and installation of same.

##### Installation of anchor bolts.

##### Installation of the pneumatic spillway gate system including air bladders, gate panels, and other related components.

##### Installation of abutment plates including any needed grouting.

##### Provide and install any required electrical conduit and wiring.

##### Provide and install any required control conduit and cable.

##### Installation of all pneumatic spillway gate control equipment.

##### Installation of all mechanical equipment in accordance with Manufacturer’s specification.

##### Start-up, debug, and test spillway gate in conjunction with manufacturer.

##### Provide and install Neversieze or other approved lubricating compound for all stainless steel anchor bolts and fasteners.

##### Provide 100% silicone caulk for all interpanel seals.

##### Provide and install condensate purge valves at near side abutment.

##### Provide and install stilling well complete with bubbler pipe.

D.	Pneumatic crest gate performance criteria.

  - The pneumatic crest gate system, including gate panels, air bladders, air supply components, abutment plates, and controls and associated appurtenances shall be furnished by the gate supplier unless otherwise indicated. The crest gate shall be installed by the Contractor.

  - The crest gates shall consist of a stainless steel gate panel attached to the spillway crest by means of an elastomeric hinge and an air bladder mounted between the hinged gate and the spillway crest.  The hinge shall be anchored using stainless steel anchor bolts.  The elastomeric hinge shall allow the pneumatic crest gate to operate through a range from fully raised to fully lowered.  Rubber wiper type abutment seals shall be provided to allow a water tight seal across the full range of gate motion.  Pneumatic air control lines (supplied by the Contractor) to and from the gates shall be manufactured from stainless steel.

  - The pneumatic crest gates shall be specifically designed for this project.  The gates shall be designed for a height of 48” above the existing sill.  The gates shall be designed for 12” of overtopping in the raised position.

  - The pneumatic crest gate shall operate within the ambient temperature range of plus 120 degrees Fahrenheit to minus 40 degrees Fahrenheit.

  - The crest gate system shall be capable of withstanding impact from floating logs and debris and shall have a minimum gate steel thickness of ½”.  The crest gate system, when in a fully lowered position, shall be capable of passing bed load from the creek including sand, gravel, cobbles, and boulders (less than 12 inches in diameter).

  - The pneumatic crest gate system shall be designed to operate in both a fully raised and a partially raised position for extended periods of overtopping without experiencing significant oscillation, adverse flow conditions, or wear.

  - The pneumatic crest gate system shall be anchored to the concrete spillway crest.  The anchor bolt allowable shear and tension stresses for attachment to the concrete shall not exceed that recommended by the anchor bolt manufacturer.

  - The gap between adjacent gates shall be sealed by a rubber web clamped to each gate panel and made of polyester reinforced rubber.  The pneumatic crest gate system shall be watertight at these seals.

  - The pneumatic crest gate system shall be designed,  manufactured, and installed so as not to cause  binding or damage to component parts of the system.

  - A UHMW polyethylene abutment plate shall be supplied and installed at each concrete abutment.  The abutment plate will provide a flat vertical sealing surface for the pneumatic spillway gate system.

  - A restraining strap shall be incorporated to limit the upstream travel of the gate and to define the maximum gate height.

E.	Pneumatic Crest Gate Control Equipment

  - The control system shall be supplied by the crest gate manufacturer and installed by the contractor.  The control system shall consist of a NEMA 12 rated steel electrical cabinet located per engineer’s specification.

  - The control system shall allow automated and manual operation complete and ready for installation.  System shall be provided with pneumatic water level controller to be able to automatically regulate air bladder pressure.    The system shall include manual inflate valve, manual deflate valve, pressure regulator, and other components required for manual operation of a single zone of Obermeyer gate.

  - An ASME stamped pressure relief valve shall be incorporated into the control system to protect the air bladders from over pressurization.  The pressure relief valve shall be set at a pressure not more than 20% higher than maximum operating pressure.

F.	Quality Assurance

1.         Codes and Standards:  Comply with the provisions of the following except as otherwise indicated:

- AISC “Manual of Steel Construction Allowable Stress Design” latest Edition.

- AWS D1.1 “Structural Welding Code” latest Edition.

- ASTM123-89A Specification for Zinc coating on Iron and Steel Hardware.

- ASTM 153-82 Specification for Zinc Coating on Iron and Steel Hardware.

### 1.3	Submittals

Submit the following in accordance with the requirements of this section, Section 010000, and Section 013300.

#### A.	Shop Drawings and product data for pneumatic crest gate system.

## Products

## 2.1	 PRODUCT STANDARD

#### A	The product standard used for design of the supporting structures, supply piping and control building is the ‘Obermeyer Spillway Gate’ as manufactured by Obermeyer Hydro, Inc., P.O. Box 668, Fort Collins, CO, 80522. Telephone (970) 568-9844.  Email address: hydro@obermeyerhydro.com.

#### B.	Contractor’s proposed alternatives to the defined product standard shall demonstrate equivalency to the product standard to the sole satisfaction of the Engineer.

### 2.2	STEEL

A. 	The stainless steel gate panels, clamp bars, and restraining strap clamps will be manufactured from Grade 3CR12 stainless steel or equal.

- Steel hinge retainers, web retainers, and other non structural components to be manufactured from ASTM A 36 steel or equal.

- All threaded fasteners including anchor bolts shall be from 304 stainless steel or approved equal.

- All welded stainless steel components shall be passivated by stainless steel wire wheel or by acid.

- All steel components to be designed so that the maximum stress level in each component is less then 40% of yield strength and less then 25% of ultimate strength.

- All ferrous components, except stainless steel, shall be sand blasted in accordance with SSPC-SP10 prior to coating.

- Non-stainless peripheral steel parts shall be hot dip galvanized in accordance with ASTM A123 and ASTM A153.

### 2.3	Air Bladders

  - The working pressure for the air bladder and controls shall not exceed 30 pounds per square inch.

  - The material for the air bladder shall be reinforced with not less then two layers of 1000/3/3 polyester bias ply fabric.  The polyester bias ply fabric shall have a minimum tensile strength of 2320 lbs/linear inch.

  - The outer rubber cover shall meet or exceed ASTM D2000 2BA5.515A14B13C12.

  - The air bladder material shall have a minimum thickness of .31" as measured in accordance with ASTM D751.

  - An abrasion test using an H18 stone with a 2.2 pound load for 1000 repetitions as modified from ASTM C501 shall show less then 0.03 cubic inches of abrasion.

  - An ozone test shall show no abnormality in appearance when subjected to an ozone test conducted as 100mPa, 104 degrees Fahrenheit and 50 percent elongation, in accordance with ASTM D 1149.

  - The adhesion between the polyester reinforcement and the rubber shall be a minimum of 50 pounds per inch before aging and a minimum of 36 pounds per inch after aging in 158 degrees Fahrenheit for 96 hours.

### 2.4	Air Piping and Electrical Conduit

- The air supply piping between the control system plumbing

cabinet and the gates to be 304 stainless steel 1 1/2” schedule 10 pipe conforming to ASTM A313 or owner approved substitute.

- Contractor to provide all piping up to and including 1 1/2" x 1/2" hex bushing at the connection to each air bladder.  Gate system manufacturer to provide connection hardware between 1" x 1/2" hex bushing and air bladder.

- Contractor to provide means of removing condensate from air line at low point of air pipe system or at control side abutment as shown on the Drawings.

- Any exposed portions of the piping shall be securely supported on six-foot centers using 14 gauge galvanized steel unistrut.  A minimum of two ½” stainless steel epoxy type anchor bolts per six-foot section shall be used to mount unistrut.

- All air piping shall utilize welded fittings.  All welding to be in accordance with AWS Structural Welding specifications.  All pipe joints shall be leak proof.

- Before installation of gate system, the entire run of pipe and connections shall be inspected and pressure tested to 50 psi gage and each joint checked for leaks in the presence of the owner’s representative.

### 2.5	Air Supply System

A.	The air supply system shall inflate the gates to operating

pressure in less than 30-minutes.

B.	The air compressor system shall include an Ingersoll Rand model 2475N5FP 5-hp air compressor complete with low oil level switch, auto start/stop function, air cooled aftercooler, automatic drain valve, and 80-gallon vertical receiver tank.  Air compressor to provide the gate system with 16.8 ACFM at 175 psig.

C.	A Wilkerson in-line desiccant type air dryer shall be mounted downstream of the air compressor.  The air dryer shall not utilize electricity to operate and shall be shipped complete with two fills of desiccant beads.  The air dryer shall be sized to match air compressor specification outlined in paragraph B of this section.

D.	All equipment shall be installed in accordance with original manufacturer’s instruction.  All components will be installed using sufficient unions and proper fittings to facilitate long term maintenance.

### 2.6 	Control System

- The gate system manufacturer shall supply the control system.  Control system to be factory assembled, tested and ready for connection into contractor supplied piping and wiring.

- The control cabinet shall include the following connection points:

- ¾” MPT high pressure in (from the compressor system)

- ¾” MPT for connection to air supply pipe (to the gate system)

- ¾” MPT for exhaust line (vent to atmosphere)

- The control system shall be factory assembled in a NEMA12 while electrical cabinet.

- The control cabinet shall be complete with pressure regulator, pressure gages, manual inflate/deflate valves, and other required mechanical equipment.  The system shall be designed to provide both manual control and automatic control using a pneumatic water level controller to automatically regulate air bladder pressure.

- The contractor will be responsible for providing and installing all interconnecting piping including piping between the air compressor and the controls, between the controls and the gate, and between the controls and the stilling well.

### 2.7	Electrical

A.	The air compressor system shall utilize 240 volt or 480 three  phase power.  The air compressor motor shall be 5-hp.

B.	The electronic drain valve shall utilize 120 volt single phase power.

### Part 3 - EXECUTION

### 3.1	Installation

##### The installed work shall be in accordance with the crest gate Manufacturer’s approved written instructions to comply with the requirements specified herein and on the drawings.

### 3.2	Field Testing

#### All air supply pipes shall be tested prior to covering with concrete, back filled, or otherwise concealed.

#### The air piping downstream of the plumbing cabinet shall be tested by pressurizing to 50 psi for 24-hours.  Pressure readings and ambient air temperature shall be recorded at six different times during the test.  Any joints or fittings exhibiting leakage during this time shall be repaired or replaced.

#### The air piping upstream of the plumbing cabinet shall be tested by pressurizing to 150 psi for 24-hours.  Pressure readings and ambient air temperature shall be recorded at six different times during the test.  Any joints or fittings exhibiting leakage during this time shall be repaired or replaced.

#### The pneumatic spillway gate supplier shall be present and shall aid in the startup, debugging, and testing of complete system

#### After installation of the gate system the spillway gates shall be fully raised and lowered three times using the control system.  The gate shall operate smoothly with no binding.

#### After installation of the spillway gate system, the air bladders shall be inflated to ½ normal operating pressure.  The gate system shall be isolated form the air supply system and held at pressure for 24 hours.  Pressure and outside ambient temperature shall be recorded at the beginning and end of the test and at four different intervals during the test.  Any bladders exhibiting leakage will be repaired by the manufacturer at no cost to the Owner.  If the Contractor is responsible for the damage, the Contractor shall be responsible for making the necessary repairs that shall be acceptable to the Owner and the Gate Supplier at no cost to the Owner or Supplier.

PART 4- MEASUREMENT AND PAYMENT

#### No separate measurement or payment will be made for Pneumatic Crest Gates.  The costs for this portion of the work shall be considered incidental to, and included in, the various lump sum and unit prices bid for the project.

## -end of pneumatic crest gates-

SECTION 133423

PRE-ENGINEERED FIBERGLASS BUILDINGS

# PART 1 – GENERAL

1.1	SECTION INCULDES

  - Pre- engineered fiberglass building.

  - Electrical wiring and devices for pre-engineered structure.

  - Heating equipment for pre-engineered structures.

  - Ventilation equipment for pre-engineered structures.

  - RELATED SECTIONS

- Section 013300 – Submittals

- Section 033000 – Cast-In-Place Concrete.

- Section 260500-Electrical Requirements.

  - REFERENCES

- ASTM C518 – Standard Test Method for Steady-State Heat Flux Measurements and Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus.

- ASTM D 256 – Standard Test Method for Determining the Pendulum Impact of Notched Specimens of Plastics.

- ASTM D618 – Standard Practice for Conditioning Plastics for Testing.

- ASTM D638 – Standard Test Method for Tensile Properties of Plastics.

- ASTM D732 – Standard Test Method for Shear Strength Plastics by Punch Tool.

- ASTM D790 – Standard Test Methods for Flexural Properties of Unreinforced and Reinforced Plastics and Electrical Insulating Materials.

- ASTM D792 – Standard Test Method for Specific Gravity (Relative Density) and Density of Plastics by Displacement.

- ASTM D1622 – Standard Test Method for Apparent Density of Rigid Cellular Plastics.

- ASTM D2583 – Standard Test Method for Indentation Hardness of Rigid Plastics by Means of a Barcol Impressor.

### submittals

- Submit under provisions of Section 013300.

- Product Data:   Certified independent test results of representation wall laminate.

C. 	Shop Drawings:   Show:

- Critical dimensions, jointing and connections, fasteners and anchors.

- Materials of construction

- Sizes, spacing and location of structural members, connections attachments, openings and fasteners.

- Color(s).

D.	Calculations:  Structural design calculations, sealed by an independent Professional Civil Engineer, licensed in The State of Idaho.

E.	Samples:  8-inch square sample of representative wall construction, upon request.

F.	Manufacturer’s installation instructions.

  - SYSTEM DESCRIPTION

- Size:  provide one piece molded construction FRP building(s) of the following types(s):

1. 	Size: 7’0” W x 10’0” D x 7’6” H.

  - Paneled construction is not acceptable

- Design factory-fabricated, pre-engineered structure(s) to with stand loads as noted below.

      - Wind:  90 MPH. 3 second gust.

      - Snow:  40 PSF roof load.

      - Seismic:  base shear = 0.22W (from IBC equation 16-56: V=1.2SDSW

R

where  R=2.0,  SDS = 0.373 and W= effective seismic weight of structure.)

  - DELIVERY, STORAGE, AND HANDLING

- Store products indoors or in weather protected area until installation.  Protect from construction traffic and damage.

PART 2 – PRODUCTS

  - MANUFACTURER

- The product standard shall be as manufactured by TRACOM,  Inc.; 6575-A Industrial Way, Alpharetta, Georgia 30004; Tel. (877) 435-8637, Fax (770) 664-6565, www.tracomfrp.com or approved equal.

- Warranty:  Buildings shall be warranted to be free of defects in workmanship and materials for a period of two years from dates of shipment.

  - MATERIALS

- One–Piece Molded Composite Construction:

##### General Construction:  The building shall be provided with a smooth interior and exterior satin finish.  The walls and roof shall be integral with smooth radii for all corners.  No roof overhang shall be allowed.  External flanges shall only be allowed in those instances where the building is over sized.

##### Laminate:  Isophthalic polyester resin with high performance, chopped, commercial grade glass strand fiber reinforcement with a suitable coupling agent.

###### Minimum glass content:  30%

###### Exterior surface:  15 mil (minimum) gel coat with U.V. inhibitors and a textured finish, free from exposed glass or other irregularities.

###### Laminate properties:

(1.)	Tensile strength (ASTM D638):	14,000 PSI.

(2.)	Flexural strength (ASTM D790):	27,000 PSI

(3.)	Flexural modulus (ASTM D790):	1,000,000 PSI.

(4.)	Shear strength (ASTM D732):	12,000 PSI.

(5.)	Barcol hardness (ASTM D2583):	40.

(6.)	Density/specific gravity (ASTM D792): 	93.6 PCF/1.5.

##### Core:

###### Rigid closed cell, self-extinguishing (Class 1), polyisocyanurate foam with a density of 2.3 pounds per cubic foot. Foam shall be T250 Elfoam without exception.

###### Core properties:

            - Thermal conductivity

(ASTM C518):	0.145 BTU inch/hr/SF/ oF

            - Density / specific gravity

(ASTM D1622):	2.3 PCF

(3.)	Shear Strength

(ASTM C273):	25 lb/in2

(4.)	Tensile Strength

(ASTM D1623):	45 lb/in2

(5.)	Compressive Strength (7% deflection/yield)

(ASTM D1621):	35

##### Coupons prepared in accordance with ASTM D 618.

#### The manufacturer shall maintain a continuous quality control program and upon request shall furnish to the engineer certified test results of the physical properties.

#### COMPONENTS

#### Door(s)

##### Quantity:  door(s) of the following quantities:

###### (1)  Double door assembly.

##### Construction:

###### One piece molded fiberglass construction 78 inches high, 1-3/4 inches thick, and:

            - 36 inches wide.

            - Mount door with two T-304 stainless steel laminated strap hinges, 5 inches long. Continuous piano hinges or the use of fastening other than bolting shall not be acceptable.

            - Rubber bulb gasket with flexible lock to retain permanent grip.

            - One-Piece, purpose built, 3 inches deep fiberglass drip cap over doors; drip cap to extend 2 inched each side past door. Cut angle shall not be acceptable.

            - Full threshold, heavy duty black vinyl, 4-1/2 inches deep x ½ inch high.

(a)	T-304 stainless steel, 5 inches deep x ½ inch high.

            - Schlage stainless steel single-point key locked classroom style ball knob. To facilitate entry and exit from the building, raised door sills shall not be acceptable.

    - Key locked three-point hardware with drop handle and raised door sill.

            - Heavy duty stainless steel, dual compression spring cushioned overhead door stop, designed for BHMA L52231 and ANSI A156.16.

(a)	Overhead channel style stainless steel door stop / door holder.

            - Provide single-flap neoprene insert style T-304 stainless steel door sweep.

#### Lifting Eyes:  Provide a minimum of two removable, ¾ inch – 10 partially threaded, eye bolts with 6 inch shank lengths.

##### T-304 stainless steel (5140 lbs. work load limit)

##### Internal Mounting Flange: 3 inches wide x ¼ inch thick (minimum) with closed cell neoprene sponge rubber gasket 2 inches wide x 3/8 inch thick to provide a weather tight seal around the building perimeter.

##### Equipment

##### Electrical

##### Circuit Breaker Panel:  120 / 240 VAC, 1 phase, surface mount.

##### a.	125 amp, main breaker, 12 branch, NEMA 1 metallic body.

##### Electrical Wiring: 12 gauge stranded, color-coded THHN schedule 40 PVC conduit.  SO cord or other non-encased wiring shall not be acceptable.

##### Receptacle:  Interior GFCI receptacle 15A 125V, with 5mA +/- 1mA trip threshold.

##### 4. 	Switch:   Weatherproof switch box.

##### a. 	Single toggle, for light.

##### HVAC

##### 1.	Fan:  Shutter-mounted exhaust fan with integral gravity shutter, aluminum fan blades, fiberglass canopy, and OSHA compliant polyester-coated wire guard.  Exhaust fan to be wired to the weatherproof light / fan switch.

##### a.	585 CFM 10 inch diameter fan (standard)

##### Heater:  Line powered wall heater.  No separate electrical outlet shall be required.

##### a.	2,000 watt, 6,124 BtuH, 240 VAC, white powder coat finish with automatic re-set thermal overload protection with indicator light and built-in thermostat.

##### Shutter:  Gravity operated fiberglass intake shutter, with heavy duty fiberglass frame and exterior removable T-316 stainless steel insect screen.

##### a.	10 inches by 10 inches.

##### Thermostat:  NEMA 4X electric line voltage thermostat for remote operation of fan, 0-45 C and 30-110oF.

##### Lighting

##### Interior Light:  Lamp to be wired to the weatherproof fan switch.

##### a.	64 watt, 2 bulb, 48 inch fluorescent vapor-tight fixture with acrylic lens for damp locations.

##### Mounting

##### 1.	 Equipment mounting panel: ¾ inches thick marine grade plywood equipment mounting panel laminated into wall.

##### a. 	42 inches wide x 48 inches high.

###### Equipment mounting strut: (4)  sections of 12 gauge T-304 stainless steel slotted mounted strut, 48 inches long x 1- 5/8 inches deep.

##### FINISHES

##### Exterior Color: #2445 Gray cloud with U.V inhibitors

##### Interior Color: #2445 Gray Cloud

PART 3 – Execution

  - EXAMINATION

- Verify that the concrete slab is level, true to plane, and of the correct dimensions to receive the structure. Correct all deficiencies before proceeding.

  - INSTALLATION

- Install products in accordance with Engineer’s instructions, plans, blueprints, etc, local codes, and in manner consistent with the installation instruction and recommendation of the manufacturer.

- DO NOT REMOVE THE DOOR SPACER(S) until ALL ANCHOR BOLTS have been COMPLETELY SET and door operation has been VERIFIED.

- Move and position the shelter using the lifting eyes provided. The neoprene gasket provided should be positioned between the concrete slab and the building mounting flange. If more than one lifting eye is provided USE A SPREADER BAR.

- After closing the building door(s):

    - Layout the anchor bolt pattern. The anchor bolts should be installed in accordance with the Engineer's instructions.

2.	Drill and set the anchor bolts starting with one on each side of the door(s). The anchor bolts behind and in front of the door(s) should be flat head anchors if the mounting flange is external.

3.	Drill the anchor bolt holes to the depth and diameter required by Engineer as shown on the Drawings.

4.	Verify the operation of the door(s) before installing the remaining anchor bolts.

5.	FAILURE to VERIFY the operation of the door(s) BEFORE the remaining anchor bolts are set MAY RESULT in the BINDING of the door against the door frame.

6.	Install the threshold (if supplied) and re-verify the operation of the door(s).

7.	After all anchor bolts have been completely set, remove the door spacer(s).

- Seal the flange with sealant or grout to ensure water tightness.

- Install (as necessary) and test the building accessories in accordance with the Manufacturer’s instructions.

  - ADJUST  AND CLEAN

- Clean surfaces in accordance with the Manufacturer's instructions.

- Remove trash and debris, and leave the site in a clean condition.

-END OF PRE-ENGINEERED FIBERGLASS BUILDINGS-

# Section 260500

## BASIC ELECTRICAL REQUIREMENTS

## GENERAL

### SECTION INCLUDES

#### Furnish all materials, equipment, labor, supervision, tools and items necessary for the construction, installation, connection, testing and operation of all electrical work for this project, as shown on the drawings and defined in these specifications.

#### Provision of all materials, equipment and apparatus not specifically mentioned herein or noted on the drawings, but which are necessary to make a complete working installation of all electrical systems shown on the drawings or described herein.

#### Equipment and devices furnished and installed under other Divisions of this specification or by the Government shall be connected as described herein.

#### Drawings, the provisions of the contract documents, including bonds and certificates, the General Conditions, and Division 1 specification sections apply to all work of this Section.

#### E.	Drawings, General Provisions of the Contract including General and supplemental Conditions, apply to this work.

### REFERENCES

#### General:  Publications listed below form a part of this Specification to the extent indicated by references thereto:

#### American National Standards Institute (ANSI)

##### ANSI C2 - National Electrical Safety Code

##### All other applicable ANSI Standards

#### National Electrical Manufacturer's Association (NEMA)

#### National Fire Protection Association (NFPA)

##### NFPA 70	National Electrical Code (NEC)

##### NFPA 101	Life Safety Code

#### National Electrical Contractor's Association (NECA)

#### Underwriters Laboratories (UL)

#### International Code Council (ICC)

##### International Building Code (IBC) - (2003)

#### Institute of Electrical and Electronic Engineers (IEEE)

#### ICEA - Insulated Cable Engineers Association Standards

### SUBMITTALS

#### Provide submittals on panel.

#### Provide submittals on triplexed overhead wire.

### QUALITY ASSURANCE

#### Tests:  Demonstrate that all equipment operates as indicated or specified, and in accordance with the manufacturer's recommendations and these specifications.

#### Qualifications:  Use sufficient journeyman and competent supervisors in the execution of the work to ensure proper and adequate installation throughout.  In the acceptance of installed work, no allowance will be made for lack of skill on the part of the workers.

### WORK OF OTHER TRADES

#### The electrical drawings do not show complete details of the existing conditions.  Refer to the related contract drawings for those details, which may affect the execution of this work.  Specific locations of equipment shall be obtained from the contract drawings, field measurements, or the trade providing the material or equipment.  No extra payments will be allowed for failure to obtain this information.

#### Plan and execute work including, but not limited to, conduit and electrical equipment locations in cooperation with all other trades particularly Mechanical.  Make every reasonable effort to provide all concerned with timely notice of work affecting other trades to prevent conflicts or interference as to space requirements, dimensions, openings, block-outs, sleeving or other matters which will cause delays or necessitate work-around methods.  Failure to coordinate work will be considered sufficient cause for work to be altered at Contractor's expense, as directed by the Contracting Officer.

### CODES, PERMITS, INSPECTIONS AND FEES

#### Make arrangements for inspections by the Contracting Officer or other authority as required.  Submit three (3) copies of certificates of compliance to the Contracting Officer.

#### All work and materials shall be in accordance with requirements of all applicable local codes and regulations and ordinances in their latest adopted edition as referenced in sub-section 1.02.

#### The foregoing referenced codes shall be construed as establishing a minimum or base level, of requirements.  Where provisions of the various codes or standards conflict with each other, the more stringent provisions shall govern.

#### Nothing in drawings and specifications shall be construed to permit work not in conformance with these rules and regulations.

#### Where drawings or specifications call for material or construction of a better quality or larger sizes than required by the above-mentioned rules and regulations, the provisions of the drawings or specifications shall take precedence over requirements of the rules and regulations.

#### Contractor shall promptly submit written notice to the Contracting Officer of any observed variance of contract documents from legal requirements.  Appropriate Change Order modifications to the contract documents will be made to incorporate necessary changes.  Contractor shall assume responsibility for work known to be contrary to such requirements when required notice is not given.

### EQUIPMENT APPROVALS

#### All electrical components shall be approved, or listed and labeled by UL or other testing laboratory accredited by the State of Idaho, when available.  Non-listed or non-approved components may be used only if listed or approved components are not available.  Provide a written request to use non-listed or non-approved components and obtain written approval from the Contracting Officer prior to installing such components.

#### All materials used shall be manufacturers’ standard products with minimum five (5) years of documented availability prior to bid date.

### INTENT OF DRAWINGS

#### Drawings are diagrammatic and show only approximate locations of conduit runs, fixtures and equipment.  Take measurements from building or site and verify with architectural, civil, structural, mechanical, or electrical drawings.

#### Report any conflict between drawings to the Contracting Officer prior to proceeding with the work.  Failure to follow this instruction is considered sufficient cause for the Contractor to alter his work at his own expense, as directed by the Contracting Officer.

#### The drawings generally do not show conduit routing or junction and pull box locations.  The Contractor is responsible for determining final conduit routing.  Refer to diagrams or schematics to obtain a more complete description of systems.  The Contractor shall furnish and install all junction boxes, pull boxes, fittings, and supports not specifically shown but necessary to complete the electrical installation.  The Contractor shall not eliminate any junction box, pull box, or conduit body shown on the drawings without approval from the Contracting Offices.

#### Drawings and specifications are complimentary - anything shown on one, is required to be furnished as if shown on both.

#### Notify the Contracting Officer of any discrepancies between the drawings and specifications in accordance with Division 1 of the Contract.

### DETAIL DRAWINGS BY CONTRACTOR

#### Whenever the Contractor's work is of sufficient complexity to warrant additional detailing, he shall prepare additional detail drawings to scale: 1/4 inch = 1 foot; prepared on vellum or Mylar of the same size as contract drawings; and shall, with these layouts, coordinate his work with the work of other trades.  All such detailing work shall be clearly identified on the drawings as to the area to which it applies.

#### Do not submit these drawings to the Contracting Officer for approval.  At completion, however, include a set of such drawings with each set of as-built drawings for Government's record purposes.

### COORDINATION WITH MECHANICAL WORK

#### Provide motor starters and motor circuit protective devices for equipment included in other Divisions of these specifications unless the starters are supplied (manufactured) as an integral part of the equipment or as specified otherwise.

#### Install electrical devices and connect to the equipment.

### AS-BUILT (RECORD) DRAWINGS

#### Furnish one (1) set of as-built (record) drawings to the Contracting Officer in conformance with the requirements of Division 1.

### SITE CONDITIONS AND METHODS

#### Storage of Materials:  Make all necessary provisions to prevent damage or corrosion of materials.

#### Cutting and Patching:  Keep cutting and patching to a minimum.  If required, all patching shall conform to specifications for the new general construction work.  Finish to match existing work.

#### Measurements:  Verify space availability by field measurement prior to submitting shop drawings for approval.

#### Roughing-In Dimensions:  Obtain roughing-in dimensions for equipment from approved Shop Drawings or actual equipment measurements.

#### Manufacturer's Installation Instructions:  Follow manufacturer's written instructions where furnished.  If the details are in conflict with design drawings, notify the Contracting Officer for resolution.

#### Accessibility:  Install all equipment, which requires periodic servicing or repairs so it is readily accessible.  Otherwise, obtain the Contracting Officer's approval of location.

#### Rejected Materials:  Remove damaged or rejected materials from the site.

#### Operation of Equipment and Systems:  Contractor is responsible for the safe operation of equipment and systems during all periods of installations and testing.

### COMPLETION OF WORK

#### When requesting final inspection of the installation, give a minimum 10-day notice to the Contracting Officer.  Submit written certification that the work has been fully completed in strict accordance with drawings and specifications.

### MATERIALS AND WORKMANSHIP GUARANTEE

#### Submit written guarantee that all materials and workmanship that prove defective within one (1) year after date of acceptance will be replaced.

#### Include complete removal, reinstallation, and retesting of the failed component or system.  Cleanup and restoration of the affected area is the Contractor's responsibility.

#### Include correction of deficiencies on a 24-hour, 7-day a week basis when Government deems this necessary, at no cost to the Government during warranty period.

## PRODUCTS

### MATERIALS - GENERAL

#### Quality:  Provide all materials, products and equipment in strict accordance with all governing codes and ordinances and these specifications and by all other Contract Documents.

#### Quantity:  Items of identical function and rating shall be identical.  Provide items within product categories from one common manufacturer.

### RIGID METAL CONDUIT AND FITTINGS

#### Ferrous Metal Conduit

##### Ferrous metal conduit shall be hot-dip galvanized inside and out and shall conform to the National Electrical Code article “Rigid Metal Conduit: Type RMC”.  Factory cut threads shall be galvanized after cutting.

##### Fittings and Conduit Bodies:  Threaded hot dipped/mechanically galvanized steel.  Conduit bodies shall be Form 8 with gasketed covers, moguls, or pulling elbows.

##### Watertight hubs for connection of conduit to sheet steel enclosures shall be Appleton Uni-seal, Crouse-Hinds Type HUB, or approved equal.

### RIGID NONMETALLIC CONDUIT

#### PVC conduit shall be schedule 40 and shall conform to the National Electrical Code article “Rigid Nonmetallic Conduit: Type RNC”.

### LIQUIDTIGHT FLEXIBLE METAL CONDUIT

#### Liquidtight flexible metal conduit shall have a galvanized flexible steel core with non-metallic outer jacket and shall conform to the National Electrical Code article “Liquidtight Flexible Metal Conduit: Type LFMC”.

### EXPANSION FITTINGS

#### None expected.

### Insulated bushings

#### Insulated bushings shall be provided at ends of all conduits in cabinets, pull boxes, junction boxes, and cable support boxes to prevent abrasion of the conductor insulation.

#### Bushings shall be malleable iron body with flameproof and non-combustible composition insulating ring. Insulating material shall be locked in place and non-removable.

#### Acceptable bushing are O-Z/Gedney Electrical Manufacturing Company Type “IBC”, or as approved by the Government.

### POWER and control CONDUCTORS

#### Stranded copper conductor, single insulated wire, except where noted otherwise in drawing.

#### Insulation type XHHW-2, or THWN-2, 600-volt insulation class, 90 degrees Celsius wet or dry rated, except where noted otherwise in drawing.

#### Minimum conductor size shall be #12 for power conductors and #14 for control conductors.

### wiring connectors

#### Furnish manufacturers standard product for Split Body Connectors, Solderless Pressure Connectors and Compression Connectors, all suitable for use with copper and aluminum conductors.

### Tools and equiPment

#### The Contractor shall furnish all tools and equipment required for the installation work. Tools for making compression connections shall be as recommended by the connector manufacturer and shall be of the type which once an indent has been started cannot be opened until the indent has been properly completed.

### Plastic Cable Ties

#### T&B nylon, locking type. Use black ties for outdoor locations.

### electrical panels

#### NEMA 4 heavy-gage galvanized steel with enamel finish and with Copper busing, Provide with breakers shown and minimum 2 spare single pole 20 amp breakers in each.

### PULL AND JUNCTION BOXES

#### As needed:

##### NEMA Type 4, heavy-gage galvanized steel with enamel finish and external mounting feet.  Continuous hinge cover with oil resistant gasket and external screw clamps.

### GROUNDING - WIRE

#### Material:  Stranded copper as sized on the Drawings.

### SUPPORTING DEVICES

#### Materials and Finishes:  Provide hot-dipped galvanized steel, stainless steel or other corrosion resistant hardware and fasteners for mounting panel, boxes and conduit to existing poles

#### Provide materials, sizes, and types of anchors, fasteners and supports to carry the loads of equipment and conduit.  Consider weight and tension of wire when selecting products.

### ELECTRICAL IDENTIFICATION - mATERIALS

#### Wire and cable markers:  Identify conductors for power and control wiring with wire markers that have machine printed black letters on white background, beneath clear heat shrinkable tubing. Identify both ends of all power and control wires, at the point where they are terminated.  Spare conductors shall be so marked and labeled as to the location of their opposite ends. Suitable wire marker material shall be Raychem “Shrink-Mark”, or approved equal.

#### Provide laminated plastic nameplates for each panelboard, equipment enclosure, relay, switch, and device.  Each nameplate inscription shall identify the function and, when applicable, the position.  Nameplates shall be melamine plastic, 0.125-inch thick, white with black center core unless specified otherwise elsewhere.  Surface shall be matte finish.  Corners shall be square.  Accurately align lettering and engrave into the core.  Minimum size of nameplates shall be 
1-inch by 2 1/2-inches.  Lettering shall be a minimum of 1/4-inch high normal block style.  Screw or rivet all nameplates with two (2) screws or rivets.  Adhesive nameplates are not acceptable.

### CIRCUIT BREAKERS

#### Provide thermal magnetic type circuit breakers of single unit construction per UL 489.

#### Ground fault circuit interrupter type circuit breakers shall be installed where required by code, or as indicated by drawings or specifications.

#### Handle locks shall be provided on all circuit breakers.

#### Minimum interrupting ratings shall be 10,000 amperes RMS asymmetrical at 240 volts.

#### Update existing motor control center compartment nameplates or panelboard circuit directory card upon completion of work.  Directory shall be typewritten.

## EXECUTION

### PRODUCT DELIVERY, STORAGE, AND HANDLING

#### Handle all equipment carefully to prevent internal components damage, breakage, and denting and scoring the finish.  Do not install damaged equipment.

#### Store equipment in a clean, dry space.  Protect equipment from dirt, fumes, water, construction debris, and physical damage.

#### Provide auxiliary heaters, or store in a heated space, for any equipment that would be damaged by moisture condensation, such as electric motors, electronic components, contacts, etc.

### SITE INSPECTION

#### Installer must examine the areas and conditions under which electrical equipment is to be installed and notify the Contracting Officer in writing of conditions detrimental to the proper and timely completion of the work.  Do not proceed with the work until unsatisfactory conditions have been corrected in a manner acceptable to the Installer and the Contracting Officer.

### WORK RESPONSIBILITIES

#### Drawings indicate diagrammatically desired locations or arrangement of conduit runs and equipment.  Proper judgment shall be exercised in executing work to secure best possible installation in available space and to overcome local difficulties due to space limitations or interference with structural conditions.  Contractor shall be responsible for correct placing of work and proper location and connection of work in relation to work of other trades.

#### In the event changes in indicated locations or arrangement are necessary, due to developed conditions in construction or rearrangement of equipment, such changes shall be made without extra cost, providing the change is ordered before the conduit runs, and work directly connected to it is installed and no extra materials are required.

#### The scales and/or dimensions of figures are approximate for typical equipment of the class indicated.  Before proceeding with any work, check and verify dimensions and sizes with Drawings to see that equipment will fit into spaces provided without violation of applicable codes.

#### Where equipment is furnished by others, verify dimensions and the correct locations of this equipment before proceeding with the rough-in of connections.

#### Should any changes to work indicated on drawings or described in Specifications be necessary in order to comply with above requirements, notify the Contracting Officer immediately and cease work on parts of Contract which are affected until approval of any required modifications to construction has been obtained from the Contracting Officer.

#### Contractor shall be responsible for any work, which must be altered due to lack of proper supervision or failure to make proper cooperative provisions in time.  Such change shall be made to the satisfaction of the Contracting Officer.

#### Perform work with competent and skilled personnel.

#### Work, including aesthetic as well as electrical and mechanical aspects of work, shall be of quality consistent with best practices of trade.

#### Replace or repair, without additional compensation, any work, which, in the opinion of the Contracting Officer, does not comply with these requirements.

#### Provide maintenance access to all equipment installed.

### INSTALLATION – GENERAl

#### Locations of Openings: Coring, cutting, drilling, or welding of any structural member is prohibited without written approval of the Contracting Officer.

#### Be responsible for cutting and patching which may be required for proper installation of electrical work.

#### Protect work, materials and equipment from damage from any cause whatever, and provide storage facilities during progress of work.  Storage out of doors shall be weather protected and shall include space heaters to prevent condensation.  Provide for safety and good condition of work until final acceptance of work by the Contracting Officer, and replace damaged or defective work, materials, and equipment before requesting final acceptance.

#### Conduit, and all equipment to be installed:  Clean to remove plaster, splattered paint, cement and dirt on both exterior and interior.

### CONDUIT INSTALLATION

#### Unless otherwise shown, size conduit for conductor type installed.  Minimum size 3/4 inch.

#### Provide suitable fittings to accommodate expansion and deflection where required.

#### Install conduit in interior or enclosed spaces to maintain headroom and present a neat appearance in unfinished spaces.

#### Route conduit parallel and perpendicular to building planes.

#### Maintain minimum six (6) inches clearance between conduit and piping.  Maintain twelve (12) inches clearance between conduit and heat sources such as flues, steam pipes, and heating appliances.

#### Brace conduit or conduit supports to prevent distortion of alignment by wire pulling operations.

#### Support all conduits on formed channel (Unistrut, or approved equal) supports with space for 25 percent additional conduit or twelve (12) inches useable space whichever is greater.

#### Do not support conduit with wire or perforated pipe straps.  Remove temporary conduit support used during construction before conductors are pulled.

#### Route raceways to avoid structural obstructions and to minimize crossovers.

#### Seal around raceway with sealing compound where raceways leave heated area and enter unheated area.

#### Route all accessible raceways parallel or perpendicular to building lines.  Form bends in adjacent raceways to match radii and center of bend.

#### Raceways are sized for copper conductors, Type XHHW-2 insulation, unless noted otherwise.  Size all raceways per the National Electrical Code unless larger size conduits are specifically noted on the Plans.

#### Welding, brazing, or heating of conduit shall not be permitted.  Plumbers perforated hanger iron shall not be used for any purpose.

#### Metallic conduit joints shall be made up watertight and rust resistant with conductive, high temperature thread/joint lubricant, which maintains ground continuity, KOPR-SHIELD by Thomas & Betts or approved equal.  Lubricant shall be applied to male threads only.

#### Install no more than 270 degree of bends between boxes.  Avoid bends and offsets where possible, but where necessary make with conduit bending machine.  Use conduit bodies to make sharp changes in direction, as around beams.

#### Conduits and boxes shall be of such sizes and numbers and shall be so installed that the required number of conductors may be drawn in without injury or excessive strain.  The Contractor will be permitted to increase the size of conduits and number of boxes, if he so desires to facilitate a speedier and less complicated installation, however, such changes shall be at his expense.  Where necessary for ease of pulling or to meet code, install conduit bodies or pull boxes even though not shown on the Plans.

#### For conduits of all sizes, either manufactured elbows or bends fabricated in a bending machine shall be used.  Conduit bending radii shall not be less than the minimums set by the National Electrical Code.  A bending radius greater than six times the internal diameter of the conduit shall be maintained.  Conduit bends that are crushed or deformed in any way shall not be installed.

#### Conduit offsets shall be properly made and installed where required.  Where two or more conduit offsets or bends are installed in parallel, they shall be symmetrically formed and arranged.

#### All conduits shall be installed in such a manner as to insure against trouble from collection of trapped condensation, and all runs of conduit shall be arranged to eliminate traps wherever possible.  Install underground conduit with minimum slope of four (4) inches per 100 feet.  Slope duct away from building entrances and toward underground vault or box.  Install water stops and drain fittings at low point of all vertical conduit runs.

#### Wooden plugs inserted in concrete or masonry are not acceptable as a base for conduit fastenings, nor shall conduit or pipe straps be welded to steel structures.

#### Openings in floors, walls or ceilings required for the installation of the conduit shall be patched to match the existing area after the installation is complete.

#### Contractor shall exercise necessary precautions to prevent lodging of dirt, concrete, or trash in conduit, fittings, and boxes during course of installation. Install manufactured threaded end caps on all raceway ends during construction.

#### Raceways shall not penetrate sheet metal ducts unless permission is granted by the Contracting Officer in writing. All sleeves for raceway installation shall be provided under this section.

#### Install UL approved expansion fittings complete with grounding jumpers where raceways cross slab expansion joints, construction joints, or sawn joints.

#### Install conduits such that wiring can be installed/maintained from a ladder on grade or from within structure.

#### Use 1/4” stand-offs, conduit spacers, or hot-dipped galvanized strut for all surface mounted raceways and enclosures.

#### Rigid Metal Conduit (RMC)

##### Use RMC for all above grade and for stub-ups in underground conduit runs.

##### The ends of all conduits shall be well reamed to remove burrs and rough edges.  Field cuts shall be made square and true.  Slip joints or running threads will not be permitted for coupling metallic conduit.  When a standard coupling cannot be used, an approved threaded union coupling shall be used.  The threads on all metallic conduits shall be rust-free, clean and well painted with good quality colloidal copper suspended in petroleum vehicle before couplings are made up (KOPR-SHIELD, or equal).  All couplings shall be tightened so that a good electrical connection will be made throughout the entire length of the conduit run.  If the conduit has been moved after assembly, it shall be given a final tightening from the ends prior to wiring installation.  Where coating on galvanized conduit has been injured in handling or installing, such injured places shall be thoroughly painted with galvanizing repair paint, Formula A-9-73, Zinc Dust Primer (Federal Spec X-6442/MIL-P-21035).

##### All conduit ends shall be threaded and capped with standard threaded conduit couplings with sealing insert or threaded conduit caps until conduit installation is started.  When couplings or conduit caps are removed, the threaded ends shall be provided with approved conduit bushings.  The use of any plugs, even though temporary, in lieu of the conduit couplings and conduit caps is expressly prohibited.

##### Metallic conduit bends shall have a radius consistent with the requirements of the National Electrical Code.  Where approved by the Contracting Officer, conduit may be bent using a conduit bending tool employing correctly sized dies, without crimping or flattening, using the longest radius practical.

#### Liquidtight Flexible Metal Conduit (LFMC)

##### Liquidtight flexible metal conduit with watertight connectors shall be installed for final connections to dry type transformers, motors without flexible cords, and other equipment with rotating or moving parts.  Conduit shall be installed without sharp bends and in minimum lengths required for the application but not longer than 6(-0(, unless approved by the Contracting Officer.

#### Conduit Hubs

##### Provide galvanized conduit hubs for rigid metal conduits entering metallic enclosures or junction boxes. Coat the hub threads with KOPR-SHIELD, or equal.

#### Grounding End Bushings

##### The ends of all conduits at NEMA rated enclosures, motor control centers and panelboards shall include grounding type insulated throat locking end bushings, which are to be interconnected and bonded to the box, or cabinet at which they terminate by a (#8 minimum) copper ground wire.

#### Sealing Unused Conduit Openings

##### Seal all unused openings in enclosures with stainless steel double gasket hole seals.

#### Sealing Of Penetrations

##### Exterior wall surfaces above grade:  Seal around all penetrations with duct seal or suitable caulking unless otherwise indicated on the drawings.  Methods of sealing shall be approved by the Engineer.  For concrete construction above ground level, cast raceway in wall or core drill wall and hard pack with a mixture of equal parts of sand and cement.

##### Fire rated floors, walls, ceilings/roofs: Seal around raceway penetration through concrete or masonry with 3M Fire Barrier or Dow Corning 30-548 silicone RTV foam or approved equal.  For plaster or gypsum wallboard penetration, seal around raceway with plaster and fire tape per local Fire Marshal’s requirements.

#### Expansion Joints

##### Conduits crossing concrete or structural expansion joints shall be provided with expansion and deflection fittings to compensate for expansion and contraction.

### WIRE AND CABLE INSTALLATION

#### Install products in accordance with manufacturers’ instructions.

#### Completely and thoroughly clean interior of installed raceway before installing wire using a mandrel or large swab.

#### All wiring shall be installed in a raceway system unless otherwise specified.  Pull all conductors into raceway at same time.

#### Neatly train and lace wiring inside boxes, equipment and panelboards.

#### All cables into the control cabinets, motor control centers and panelboards shall be cut to extra length such that the cable will reach along the two longest adjacent sides.

#### When cable enters through the top of the control cabinet or panelboard, it shall be long enough to loop to the bottom of the cabinet before being connected.  Where cable enters through the bottom, the reverse should be used.  Cables shall be carefully handled when unreeling to avoid damage due to kinking or bending to smaller than allowable radius.  Cable shall not be laid on rough ground or dragged over sharp objects.

#### Cables and wires shall be visually inspected by the Contractor for possible damage when received and before installation.  Damaged cables and wires shall not be installed.

#### Care shall be used in order to protect the cables and wires against damage in handling, storage or during installation and after the cables are installed.  Minimum bending radius of cables and wires shall be in accordance with the manufacturer's recommendations.  The Contractor shall replace any wire or cable damaged during installation.

#### Splice and terminate conductors only in accessible locations.  Clean conductor surfaces before installing lugs and connectors.  Make splices, taps, and terminations to carry full ampacity of conductors with no damage from temperature rise.

#### Except where equipment is furnished with bolted or screw type lug, make connections using compression set pressure connectors with insulating covers for wire terminations.

#### Equipment Grounding Conductor:  Provide separate, insulated conductor within each feeder, branch circuit and control circuit raceway.  Terminate each end on suitable lug, bus, or grounding bushing.

#### Provide wire markers on each conductor in panelboard, pull boxes, outlet and junction boxes, and at load connection.  Identify with branch circuit or feeder number for power and lighting circuits, and with control wire number as indicated on schematic and interconnection diagrams or equipment manufacturer's Shop Drawings for control wiring.

### BOX INSTALLATION

#### The Contractor shall size boxes not shown, but required to complete the electrical installation.  Unless dimensioned on the Drawings, the Contractor shall size boxes per the National Electrical Code.

#### Support boxes independently of conduit.

#### Install junction and pull boxes where required to limit the total number of 90-degree bends in any conduit run to a maximum of three.

#### Install boxes plumb.

#### Nameplates:  Provide engraved plastic laminate nameplates on all panel enclosures and above each device installed on the panels.  Text shall include control panel or the equipment controlled name and designation.

### Visual and Mechnical Inspections

#### The Contracting Officer shall be notified prior to visual and mechanical inspections.

#### Perform the following inspections:

##### Cables - Low Voltage (600 volts and less):

###### Inspect cables for physical damage and proper identification.

###### Torque test cable connection.  Tighten connections in accordance with manufacturer’s recommendation or if unavailable to industry standards.

##### Electrical Panels

###### Inspection will be made for physical, electrical, and mechanical condition.

###### Check for proper grounding to panelboard grounding bus.

###### All conductor connections will be checked for tightness.

###### Check rating of overcurrent protective devices to conductor sizes for compliance with the National Electrical Code.

###### Panelboard will be cleaned.

###### Panelboard directory will be updated as necessary for connected loads with spare breakers identified.

### Electrical Tests

#### Perform the following electrical tests:

##### Circuit Breakers:

###### Test installed circuit breakers and installed wiring for short circuits and ground faults before energizing.

#### Measure ampere readings on each phase and the neutral, where present, under fully loaded conditions. Note on plans for as built drawings.

## -end of basic electrical requirements-

SECTION 312316

EXCAVATING AND BACKFILLING

PART 1 - GENERAL

1.1	Summary

A.	This Section specifies the requirements for excavation, backfilling, and compaction.

1.2	Related Sections

A.	Section 013300 - Submittals

B.	Section 024119 – Demolition

1.3	References

A.	General:  Publications listed below form a part of this Specification to the extent indicated by references thereto.

B.	American Society for Testing and Materials (ASTM):

1.	ASTM C33	Standard Specification for Concrete Aggregates

2.	ASTM C136	Standard Test Method for Sieve Analysis of Fine and Coarse Aggregates

3.	ASTM D422	Standard Test Method for Particle-Size Analysis of Soils

4.	ASTM D1556	Standard Test Method for Density and Unit Weight of Soil and Unit Weight in Place by the Sand-Cone Method

5.	ASTM D1557	Standard Test Method for Laboratory Compaction Characteristics of Soil Using Modified Effort (56,000 ft-lbf/ft3 (2,700 kN-m/m3))

6.	ASTM D2974	Test Method for Moisture, Ash, and Organic Matter of Peat and Other Materials

7.	ASTM D3017	Water Content of Soil and Rock in Place by Nuclear Methods (Shallow Depth)

8.	ASTM D4318	Test Method for Liquid Limit, Plastic Limit, and Plasticity Index of Soils

C.	Occupational Safety and Health Administrator (OSHA):  Standards

1.4	Quality Assurance

Submit test reports for the following:

A.	Services of an Independent Testing Laboratory – It shall be the Contractor’s responsibility to obtain and pay for the services of an approved independent testing laboratory (Testing Laboratory) to take all samples and perform all tests necessary for initial approval of materials and adequacy of placement and compaction.  The Contractor shall furnish three certified copies of the results of all tests to the Engineer.  No materials shall be placed without prior acceptance of underlying conditions by the Engineer.  No separate measurement or payment will be made for sampling and testing, including the cost of the services of an independent testing laboratory.  The costs for this portion of the work shall be considered incidental to, and included in, the price bid for placement and compaction of materials.

B.	Tests:

1.	The Testing Laboratory will take samples and perform moisture content, gradation, compaction, and density tests during placement of backfill materials to check compliance with these Specifications.

2.	Remove surface material at locations designated by the Testing Laboratory or Engineer and provide such assistance as necessary for sampling and testing.

3.	Construct inspection trenches in compacted or consolidated backfill where required to determine compliance with these Specifications.

4.	Testing by the Testing Laboratory does not relieve the Contractor of its responsibility to determine to its own satisfaction when and if its work meets the Specification.

5.	Test procedures by the Testing Laboratory shall meet:

1.	Moisture content	ASTM D3017

2.	Gradation	ASTM C136, D422

3.	Density in-place	ASTM D1556, D2922

4.	Moisture-density relationships	ASTM D1557

5.	Organic content	ASTM D2974

6.	Liquid limit	ASTM D4318

6.	Compaction tests at a frequency of one test per 100LF of backfill during placement of each lift of backfill material.

1.5	Job Conditions

A.	Existing Utilities:  The Contractor shall locate existing utilities in the area of the work.  These utilities shall be adequately protected from damage during construction of this project as approved by the Engineer.

B.	Weather:

1.	Do not backfill or construct fills or embankments during freezing weather.

2.	Do not use frozen materials, snow, or ice in any backfill area.

3.	Do not backfill on any frozen surface.

1.6	Protection

A.	The Contractor shall protect structures and other facilities immediately adjacent to excavations from damage caused by settlement, lateral movement, undermining, washouts, and other hazards.  In the event of damage, immediately make all repairs and requirements necessary to the approval of the Engineer and at no additional cost to the District.

B.	All excavation shall be in accordance with applicable OSHA Construction Standards.

C.	The Contractor shall be responsible for dewatering work areas, and no extra payment will be made for water encountered in any excavation or other work area.

1.7	Submittals

A.	Certifications:  Submit sieve analysis and suppliers certification of compliance for each imported material.  Submit sieve analysis for on-site materials to be incorporated into the work.

PART 2 - PRODUCTS

2.1	Structural Fill and Backfill

A.	Structural fill and backfill shall be clean, well graded, 3-inch-minus sand or gravel, natural on-site sand or gravel, or on-site gravelly sand fill, free of refuse, vegetable material, debris, and with less than 5 percent material passing the No. 200 sieve.

B.	Material shall be obtained from required excavations or other Contractor furnished sources and shall be approved by the Engineer prior to placement.

2.2	Compacted Fill

A.	Compacted fill shall be imported pit run, processed sand and gravel, or surplus excavated materials, free from refuse, debris, organic material, and rocks over six (6) inches in diameter and shall meet the following requirements:

Sieve Size	Percent Passing (by weight)

4-inch square	100

3-inch square	75-100

2-inch square	75-100

No. 40	50 max.

No. 200	10 max.

Sand Equivalent	30 min.

The Organic Content shall be less than 3 percent as determined by Testing Laboratory.

B.	Material shall be obtained from required excavations or other Contractor furnished sources and shall be approved by the Engineer prior to placement.

## PART 3 - EXECUTION

3.1	Structural Excavation

A.	Structural excavations include excavations required for footings, retaining walls, grade beams, slabs, concrete floors, and tanks.

B.	The bottom of excavations shall be within + 0.10 feet of the depths shown on the drawings.  The bottom of all structural excavations shall be cleaned to remove all rocks over three (3) inches in diameter and loosened soil.

1.	All excavations shall be carried to the depth indicated on the Drawings and/or approved by the Contracting Officer.  Should the Contractor, through their own negligence or other fault, excavate below the designated depths, they shall replace such over excavation with approved materials and methods at their own expense.

2.	The Engineer shall be notified as soon as excavations for footings or foundations are made, in order that inspections can be made prior to building forms and pouring concrete.

3.	Excess cuts under footings shall be filled with concrete.  Excess cuts under slabs and floors on grade shall be filled with approved compacted fill.

4.	All excavations must be clean, dry and free from loose earth or other materials at time of placing concrete.  Remove excess excavated materials from site.

3.2	Unclassified Excavation

A.	Unclassified excavations include excavations required for roadway cuts, paving and grading, site contouring, and other excavation not classified as Structural Excavation above.

B.	The Contractor shall remove all material to sufficient elevation to allow proper placement and compaction of any necessary fill and surfacing to meet the elevations shown on the drawings or as required for removal of unsuitable material as directed by the Engineer.  Excavated material meeting the requirements of 2.0 of this Section may be used as fill material.  All other material shall be disposed of by the Contractor.

3.3	Waste Material Disposal

A.	See Section 024119.

B.	Concrete, large rock, organic material, and other excavated material not suitable for or included in fills and backfills shall be disposed of by the Contractor in an off-site disposal location.

3.4	Structural Fill and Backfill

A.	All fill and backfill under all sidewalks and concrete slabs on grade (interior and exterior) and all fill and backfill within a horizontal distance of 5 feet from concrete structures such as walls, footings, catch basins, manholes, etc. is defined as structural fill.

B.	Structural fill material shall conform to Paragraph 2.1 above, and shall be placed and compacted in 8-inch maximum thickness layers, loose measure, to at least 95 percent of maximum dry density.

C.	Where backfill is to be placed against both sides of concrete walls, the backfill shall be brought up evenly on both sides of the wall.

D.	Backfill shall not be placed against just one side of concrete walls (including grade beams) until the concrete has developed sufficient strength to resist the loading imposed by the backfill.  Any abutting concrete walls or beams shall also have attained sufficient strength.  In any case, the backfill placement shall not begin prior to 72 hours after concrete placing and shall not exceed the following schedule:

Age of Concrete	Backfill Depth

72 hours	1/2 wall height

7 days	2/3 wall height

28 days	full wall height

3.5	Compacted Fill

A.	All fill not otherwise classified shall be compacted fill.  Material for fill shall conform with the requirements of Paragraph 22 - Compacted Fill, shall be uniformly moisture-conditioned to between zero (0) percent and five (5) percent above the optimum moisture content and shall be placed in 8-inch maximum layers loose depth, and shall be compacted to at least 90 percent of maximum dry density.  The top two (2) feet shall be placed in 6-inch maximum layers loose depth and shall be compacted to at least 95 percent of maximum dry density as determined by the Testing Laboratory.

B.	Compacted fill shall be placed to the shapes and elevations shown on the drawings, sloped to drain, and without noticeable irregularities.

C.	Fill material placed on existing slopes, which are steeper than 4:1 (horizontal to vertical), including existing fill embankments, shall be properly keyed into the slope surface.  This shall be accomplished by constructing the fill on a series of 4-foot to 8-foot wide horizontal benches cut into the slope.

3.6	Compaction

A.	Compaction to the density as required by Paragraphs 3.1, 3.6, 3.7, or 3.8 above, shall be by means of an appropriately sized static, vibratory or impact type compactor suited to the soil and physical restrictions of the area to be compacted.  Although the Contractor is responsible for the selection of the method of compaction, selection of an inappropriate method shall not relieve the Contractor of the responsibility to achieve the specified result.

B.	Jetting, sluicing, or water settling will not be permitted.

#### -END OF EXCAVATING AND BACKFILLING-

SECTION 312319

DEWATERING

PART 1 - GENERAL

1.1	RELATED WORK SPECIFIED ELSEWHERE

The provisions and intent of the Contract, including the General Conditions, Supplementary Conditions and General Requirements, apply to this work as if specified in this section.  Work related to this section is described in:

A.	Section 013300 - Submittals

1.2	DESCRIPTION OF WORK

The Contractor may expect to encounter groundwater.  All Work areas shall be dewatered as required to keep them dry during construction.  This Section describes the Contractor requirements to keep excavations and Work areas free from water.

1.3	QUALITY ASSURANCE

No subsurface investigations have been performed at the site in connection with this project.  The Contractor shall ascertain, to their own satisfaction, the extent to which water may occur, the nature of the material in which it will appear and the extent to which such occurrence of water shall affect their bid.

1.4	SUBMITTALS

The Contractor shall submit a dewatering plan which addresses the methods proposed in handling the dewatering discharge.  Contractor shall submit Dewatering Plan in accordance with Section 013300.  No work shall be done until the Engineer concurs in writing with the proposed methods and materials for water exclusion and water handling and treatment.  Failure to accept all or any part of any such plan shall not make the Owner liable to the Contractor for any work delays.

The Contractor shall be required to obtain all necessary permits for disposing of the dewatering discharge.  Permits required shall be addressed in the Contractor’s dewatering plan.

PART 2 - PRODUCTS

2.1	GENERAL

Products that are required to accomplish, or to be incorporated into, the work of this Section, shall be as selected by the Contractor, subject to review by the Engineer.

PART 3 - EXECUTION

3.1	 GENERAL

A.	Site work for excavation shall be kept free from water to facilitate fine grading and construction of structures.  Adequate pumping equipment shall be provided to handle and dispose of the water without damage to adjacent property.  No pumped water shall be discharged directly back to the stream.

B.	The Contractor shall provide and maintain at all times during construction, ample means and devices with which to promptly remove and properly dispose of all water entering trenches and excavations and other parts of the work, whether the water be surface water or underground water.  No embankment material shall be placed in standing water.  The Contractor shall be responsible for obtaining all water discharge permits that are required.  No water shall be drained into work built or under construction.

C.		Water shall be disposed of in such a manner as to not be a nuisance or menace to the public health or fish health.  Dewatering water shall be allowed to infiltrate onsite.

D.		Dewatering of excavations must be controlled to prevent damage from settlement due to possible lowering of the adjacent groundwater table.

PART 4 - MEASUREMENT AND PAYMENT

A.	No separate or extra payment of any kind will be made for pumping or otherwise dewatering any excavation.  All cost of such work shall be considered incidental to the work and shall be included in the applicable lump sum bid price.

-END OF DEWATERING-

SECTION 354337

STREAMBED PROTECTION

PART 1 – GENERAL

1.1	RELATED WORK SPECIFIED ELSEWHERE

The provisions and intent of the Contract, including the General Conditions, Supplementary Conditions and General Requirements, apply to this work as if specified in this section.  Work related to this section is described in:

A.	Section 013300 - Submittals

1.2	DESCRIPTION OF WORK

- The work includes furnishing of all material, labor and equipment necessary for providing the rock riprap in the river bed as described on the drawings and in this specification.

1.3	QUALITY ASSURANCE

- The Contractor is to provide the results of physical and chemical testing of imported materials to ensure that the quality of materials meets the specifications herein and that materials are placed as shown on the Drawings and described in these specifications.

- The Engineer maintains the right to reject any materials that have been determined to be substandard for any reason.  In the event of rejection, it shall be the responsibility of the contractor to remove all stockpiles of rejected material from the site.

1.4	SUBMITTALS

The Contractor shall submit a gradation report for the riprap.  Contractor shall submit gradation report in accordance with Section 013300.

.

PART 2 – PRODUCTS

2.1	RIPRAP

- Riprap shall be of a dense, hard and durable character, not subject to deterioration in water.  Riprap shall consist of broken stone, broken concrete rubble, or concrete in sacks.  Riprap consisting of broken stone and concrete rubble shall be free from segregation, seams, cracks, and other defects tending to destroy its resistance to weather and shall conform to the following requirements for quality.

Degradation Factor		15 minimum

Los Angles Wear, 500 Rev.	50% maximum

Specific Gravity 		2.55 minimum

- The size and grading of the rock shall be in accordance with the table below and may be varied by the Engineer if, in his judgment, it is necessary to achieve the intended results.

| Percent Smaller | Rock Size (ft) | Rock Size (lb) |
| --- | --- | --- |
| D100 | 1.8 | 500 |
| D50 | 1.3 | 200 |
| D10 | 0.4 | 5 |

PART 3 – EXECUTION

3.1	PLACING RIPRAP

- The intent of this work is to provide a compact blanket of rock riprap over indicated areas.

- Place rock riprap with the largest rock against the river bed with the remainder of the rocks placed in progressively smaller sizes such that the smaller rock will key into the larger rock to form a tight blanket as protection against movement and erosion.  Dress riprap to a uniform thickness as indicated on the drawings.

PART 4 – MEASUREMENT AND  PAYMENT

- No separate measurement or payment shall be made for slope protection work.  The costs for this portion of the work shall be considered incidental to, and included in, the various lump sum and unit prices bid for the project.

-END OF Streambed PROTECTION-