## Beam
CHAPTER 17. ESTIMATING FIRE RESISTANCE TIME OF STEEL BEAMS PROTECTED
BY FIRE PROTECTION INSULATION (QUASI-STEADY-STATE APPROACH)
Version 1805.0
The following calculations estimate the fire resistance time for structural steel beams protected by board type fire protection
insulating material.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Beam and Insulation Selected.
All subsequent output values are calculated by the spreadsheet, and based on values specified in the input
parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cell(s).
The chapter in the NUREG should be read before an analysis is made.
INPUT PARAMETERS
| Ratio of Weight of Steel Section per Linear Foot and Heated Perimeter (W/D) | [6 empty] | 16.7374 | lb/ft2
| Thickness of Applied Protection on Steel Beam (h) |  |  |  |  | h ≥ 1/16 in |  | 1.5 | in |  | 0.125 | ft
| Density of Applied Material (ri) | [6 empty] | 50 | lb/ft3
| Thermal Conductivity of Applied Material (ki) | [6 empty] | 0.1156 | Btu/ft-hr-°F |  | 3.2111e-05 | Btu/ft-sec-°F
| Specific Heat of Applied Material (ci) | [6 empty] | 0.4063 | Btu/lb-°F
| Ambient Air Temperature (Ta) | [6 empty] | 77 | °F
| Specific Heat of Steel (cs) | [6 empty] | 0.132 | Btu/lb-°F
Calculate
SECTIONAL FACTORS FOR STEEL BEAMS
| Structural Shape | W/D Ratio | [10 empty] | 33x221 | 23.3194
| W Shapes | (lb/ft2) | [10 empty] | 33x201 | 21.314
[13 empty] | 33x152 | 18.1664
| 36x300 | 29.6162 | [10 empty] | 33x141 | 16.9208
| 36x280 | 27.756 | [10 empty] | 33x130 | 15.6705
| 36x260 | 25.8943 | [10 empty] | 33x118 | 14.2944
| 36x245 | 24.4816 | [10 empty] | 30x211 | 23.9671
| 36x230 | 23.0596 | [10 empty] | 30x191 | 21.8161
| 36x210 | 23.2773 | [10 empty] | 30x173 | 19.8613
| 36x194 | 21.5965 | [10 empty] | 30x132 | 17.4018
| 36x182 | 20.3286 | [10 empty] | 30x124 | 16.403
| 36x170 | 19.053 | [10 empty] | 30x116 | 15.4025
| 36x160 | 17.991 | [10 empty] | 30x108 | 14.4008
| 36x150 | 16.9213 | [10 empty] | 30x99 | 13.2574
| 36x135 | 15.3191 | [10 empty] | 27x178 | 22.1519
| 33x241 | 25.3063 | [10 empty] | 27x161 | 20.1418
| 33x221 | 23.3194 | [10 empty] | 27x146 | 18.3561
| 33x201 | 21.314 | [10 empty] | 27x114 | 16.3539
| 33x152 | 18.1664 | [10 empty] | 27x102 | 14.7124
| 33x141 | 16.9208 | [10 empty] | 27x94 | 13.6183
| 33x130 | 15.6705 | [10 empty] | 27x84 | 12.236
| 33x118 | 14.2944 | [10 empty] | 24x162 | 22.2286
| 30x211 | 23.9671 | [10 empty] | 24x146 | 20.1657
| 30x191 | 21.8161 | [10 empty] | 24x131 | 18.2124
| 30x173 | 19.8613 | [10 empty] | 24x117 | 16.3598
| 30x132 | 17.4018 | [10 empty] | 24x104 | 14.6187
| 30x124 | 16.403 | [10 empty] | 24x94 | 15.0832
| 30x116 | 15.4025 | [10 empty] | 24x84 | 13.563
| 30x108 | 14.4008 | [10 empty] | 24x76 | 12.336
| 30x99 | 13.2574 | [10 empty] | 24x68 | 11.0983
| 27x178 | 22.1519 | [10 empty] | 24x62 | 10.9832
| 27x161 | 20.1418 | [10 empty] | 24x55 | 9.7974
| 27x146 | 18.3561 | [10 empty] | 21x147 | 21.9923
| 27x114 | 16.3539 | [10 empty] | 21x132 | 19.8795
| 27x102 | 14.7124 | [10 empty] | 21x122 | 18.4546
| 27x94 | 13.6183 | [10 empty] | 21x111 | 16.8736
| 27x84 | 12.236 | [10 empty] | 21x101 | 15.4218
| 24x162 | 22.2286 | [10 empty] | 21x93 | 16.5726
| 24x146 | 20.1657 | [10 empty] | 21x83 | 14.889
| 24x131 | 18.2124 | [10 empty] | 21x73 | 13.1819
| 24x117 | 16.3598 | [10 empty] | 21x68 | 12.3244
| 24x104 | 14.6187 | [10 empty] | 21x62 | 11.2898
| 24x94 | 15.0832 | [10 empty] | 21x57 | 11.2205
| 24x84 | 13.563 | [10 empty] | 21x50 | 9.919
| 24x76 | 12.336 | [10 empty] | 21x44 | 8.7824
| 24x68 | 11.0983 | [10 empty] | 18x119 | 20.2769
| 24x62 | 10.9832 | [10 empty] | 18x106 | 18.2026
| 24x55 | 9.7974 | [10 empty] | 18x97 | 16.7374
| 21x147 | 21.9923 | [10 empty] | 18x86 | 14.937
| 21x132 | 19.8795 | [10 empty] | 18x76 | 13.2799
| 21x122 | 18.4546 | [10 empty] | 18x71 | 14.4763
| 21x111 | 16.8736 | [10 empty] | 18x65 | 13.3174
| 21x101 | 15.4218 | [10 empty] | 18x60 | 12.3499
| 21x93 | 16.5726 | [10 empty] | 18x55 | 11.3734
| 21x83 | 14.889 | [10 empty] | 18x50 | 10.3887
| 21x73 | 13.1819 | [10 empty] | 18x46 | 10.3024
| 21x68 | 12.3244 | [10 empty] | 18x40 | 9.02
| 21x62 | 11.2898 | [10 empty] | 18x35 | 7.9545
| 21x57 | 11.2205 | [10 empty] | 16x100 | 18.7368
| 21x50 | 9.919 | [10 empty] | 16x89 | 16.807
| 21x44 | 8.7824 | [10 empty] | 16x77 | 14.6632
| 18x119 | 20.2769 | [10 empty] | 16x67 | 12.8486
| 18x106 | 18.2026 | [10 empty] | 16x57 | 12.8186
| 18x97 | 16.7374 | [10 empty] | 16x50 | 11.3272
| 18x86 | 14.937 | [10 empty] | 16x45 | 10.2515
| 18x76 | 13.2799 | [10 empty] | 16x40 | 9.1612
| 18x71 | 14.4763 | [10 empty] | 16x36 | 8.2941
| 18x65 | 13.3174 | [10 empty] | 16x31 | 7.7849
| 18x60 | 12.3499 | [10 empty] | 16x26 | 6.5851
| 18x55 | 11.3734 | [10 empty] | 14x730 | 94.836
| 18x50 | 10.3887 | [10 empty] | 14x665 | 88.1086
| 18x46 | 10.3024 | [10 empty] | 14x605 | 81.6694
| 18x40 | 9.02 | [10 empty] | 14x550 | 75.5841
| 18x35 | 7.9545 | [10 empty] | 14x500 | 69.8893
| 16x100 | 18.7368 | [10 empty] | 14x455 | 64.6039
| 16x89 | 16.807 | [10 empty] | 14x426 | 61.0935
| 16x77 | 14.6632 | [10 empty] | 14x398 | 57.6742
| 16x67 | 12.8486 | [10 empty] | 14x370 | 54.1761
| 16x57 | 12.8186 | [10 empty] | 14x342 | 50.7293
| 16x50 | 11.3272 | [10 empty] | 14x311 | 46.5859
| 16x45 | 10.2515 | [10 empty] | 14x283 | 42.8626
| 16x40 | 9.1612 | [10 empty] | 14x257 | 39.3392
| 16x36 | 8.2941 | [10 empty] | 14x233 | 36.0263
| 16x31 | 7.7849 | [10 empty] | 14x211 | 32.9344
| 16x26 | 6.5851 | [10 empty] | 14x193 | 30.3499
| 14x730 | 94.836 | [10 empty] | 14x176 | 27.8886
| 14x665 | 88.1086 | [10 empty] | 14x159 | 25.2923
| 14x605 | 81.6694 | [10 empty] | 14x145 | 23.2932
| 14x550 | 75.5841 | [10 empty] | 14x132 | 21.9375
| 14x500 | 69.8893 | [10 empty] | 14x120 | 20.0585
| 14x455 | 64.6039 | [10 empty] | 14x109 | 18.318
| 14x426 | 61.0935 | [10 empty] | 14x99 | 16.7218
| 14x398 | 57.6742 | [10 empty] | 14x90 | 15.2715
| 14x370 | 54.1761 | [10 empty] | 14x82 | 16.9684
| 14x342 | 50.7293 | [10 empty] | 14x74 | 15.4033
| 14x311 | 46.5859 | [10 empty] | 14x68 | 14.2272
| 14x283 | 42.8626 | [10 empty] | 14x61 | 12.8387
| 14x257 | 39.3392 | [10 empty] | 14x53 | 12.4025
| 14x233 | 36.0263 | [10 empty] | 14x48 | 11.2963
| 14x211 | 32.9344 | [10 empty] | 14x43 | 10.1785
| 14x193 | 30.3499 | [10 empty] | 14x38 | 9.5218
| 14x176 | 27.8886 | [10 empty] | 14x34 | 8.5669
| 14x159 | 25.2923 | [10 empty] | 14x30 | 7.6062
| 14x145 | 23.2932 | [10 empty] | 14x26 | 7.3611
| 14x132 | 21.9375 | [10 empty] | 14x22 | 6.2827
| 14x120 | 20.0585 | [10 empty] | 12x336 | 57.3991
| 14x109 | 18.318 | [10 empty] | 12x305 | 52.9705
| 14x99 | 16.7218 | [10 empty] | 12x279 | 49.1919
| 14x90 | 15.2715 | [10 empty] | 12x252 | 45.104
| 14x82 | 16.9684 | [10 empty] | 12x230 | 41.6824
| 14x74 | 15.4033 | [10 empty] | 12x210 | 38.5144
| 14x68 | 14.2272 | [10 empty] | 12x190 | 35.2668
| 14x61 | 12.8387 | [10 empty] | 12x170 | 31.9499
| 14x53 | 12.4025 | [10 empty] | 12x152 | 28.8973
| 14x48 | 11.2963 | [10 empty] | 12x136 | 26.1371
| 14x43 | 10.1785 | [10 empty] | 12x120 | 23.3085
| 14x38 | 9.5218 | [10 empty] | 12x106 | 20.7775
| 14x34 | 8.5669 | [10 empty] | 12x96 | 18.9474
| 14x30 | 7.6062 | [10 empty] | 12x87 | 17.2833
| 14x26 | 7.3611 | [10 empty] | 12x79 | 15.7842
| 14x22 | 6.2827 | [10 empty] | 12x72 | 14.4578
| 12x336 | 57.3991 | [10 empty] | 12x65 | 13.1181
| 12x305 | 52.9705 | [10 empty] | 12x58 | 12.9633
| 12x279 | 49.1919 | [10 empty] | 12x53 | 11.9068
| 12x252 | 45.104 | [10 empty] | 12x50 | 12.5313
| 12x230 | 41.6824 | [10 empty] | 12x45 | 11.3481
| 12x210 | 38.5144 | [10 empty] | 12x40 | 10.1469
| 12x190 | 35.2668 | [10 empty] | 12x35 | 9.5281
| 12x170 | 31.9499 | [10 empty] | 12x30 | 8.2342
| 12x152 | 28.8973 | [10 empty] | 12x26 | 7.1807
| 12x136 | 26.1371 | [10 empty] | 12x22 | 7.2948
| 12x120 | 23.3085 | [10 empty] | 12x19 | 6.3572
| 12x106 | 20.7775 | [10 empty] | 12x16 | 5.4069
| 12x96 | 18.9474 | [10 empty] | 12x14 | 4.7552
| 12x87 | 17.2833 | [10 empty] | 10x112 | 25.622
| 12x79 | 15.7842 | [10 empty] | 10x100 | 23.1392
| 12x72 | 14.4578 | [10 empty] | 10x88 | 20.5988
| 12x65 | 13.1181 | [10 empty] | 10x77 | 18.2213
| 12x58 | 12.9633 | [10 empty] | 10x68 | 16.2388
| 12x53 | 11.9068 | [10 empty] | 10x60 | 14.4462
| 12x50 | 12.5313 | [10 empty] | 10x54 | 13.083
| 12x45 | 11.3481 | [10 empty] | 10x49 | 11.9318
| 12x40 | 10.1469 | [10 empty] | 10x45 | 12.3967
| 12x35 | 9.5281 | [10 empty] | 10x39 | 10.8421
| 12x30 | 8.2342 | [10 empty] | 10x33 | 9.261
| 12x26 | 7.1807 | [10 empty] | 10x30 | 9.5314
| 12x22 | 7.2948 | [10 empty] | 10x26 | 8.3311
| 12x19 | 6.3572 | [10 empty] | 10x22 | 7.114
| 12x16 | 5.4069 | [10 empty] | 10x19 | 7.1161
| 12x14 | 4.7552 | [10 empty] | 10x17 | 6.4212
| 10x112 | 25.622 | [10 empty] | 10x15 | 5.7107
| 10x100 | 23.1392 | [10 empty] | 10x12 | 4.6095
| 10x88 | 20.5988 | [10 empty] | 8x67 | 19.2806
| 10x77 | 18.2213 | [10 empty] | 8x58 | 16.9178
| 10x68 | 16.2388 | [10 empty] | 8x48 | 14.2117
| 10x60 | 14.4462 | [10 empty] | 8x40 | 12.003
| 10x54 | 13.083 | [10 empty] | 8x35 | 10.5823
| 10x49 | 11.9318 | [10 empty] | 8x31 | 9.438
| 10x45 | 12.3967 | [10 empty] | 8x28 | 9.5577
| 10x39 | 10.8421 | [10 empty] | 8x24 | 8.2628
| 10x33 | 9.261 | [10 empty] | 8x21 | 7.9071
| 10x30 | 9.5314 | [10 empty] | 8x18 | 6.8419
| 10x26 | 8.3311 | [10 empty] | 8x15 | 6.4806
| 10x22 | 7.114 | [10 empty] | 8x13 | 5.6686
| 10x19 | 7.1161 | [10 empty] | 8x10 | 4.4021
| 10x17 | 6.4212 | [10 empty] | 6x25 | 9.8814
| 10x15 | 5.7107 | [10 empty] | 6x20 | 8.016
| 10x12 | 4.6095 | [10 empty] | 6x15 | 6.1038
| 8x67 | 19.2806 | [10 empty] | 6x16 | 7.9569
| 8x58 | 16.9178 | [10 empty] | 6x12 | 6.1017
| 8x48 | 14.2117 | [10 empty] | 6x9 | 4.6392
| 8x40 | 12.003 | [10 empty] | 5x19 | 9.1751
| 8x35 | 10.5823 | [10 empty] | 5x16 | 7.824
| 8x31 | 9.438 | [10 empty] | 4x13 | 7.8235
| 8x28 | 9.5577
| 8x24 | 8.2628
| 8x21 | 7.9071
| 8x18 | 6.8419
| 8x15 | 6.4806
| 8x13 | 5.6686
| 8x10 | 4.4021
| 6x25 | 9.8814
| 6x20 | 8.016
| 6x15 | 6.1038
| 6x16 | 7.9569
| 6x12 | 6.1017
| 6x9 | 4.6392
| 5x19 | 9.1751
| 5x16 | 7.824
| 4x13 | 7.82
| User Specified Value | Enter Value
Select Beam
Scroll to desired beam size then Click on selection,
THERMAL PROPERTIES OF BOARD TYPE INSULATION MATERIALS
Select Insulation Type
Insulation Material |  | Density | Thermal | Specific Heat
Board |  | ρi | Conductivity ki | ci |  | Scroll to desired material then Click on selection
|  | (lb/ft3) | (Btu/ft-hr-°F) | (Btu/lb-°F)
Fiber-silicate, fiber-calcium silicate |  | 38 | 0.0867 | 0.2868
Gypsum plaster |  | 50 | 0.1156 | 0.4063
Mineral wool, fiber silicate |  | 10 | 0.1156 | 0.2868
Concrete |  | 150 | 0.9248 | 0.1793
User Specified Value |  | Enter Value | Enter Value | Enter Value
Reference: Buchanan, A. H., Structural Design for Fire Safety, 2001, Page 182.
ESTIMATING FIRE RESISTANCE TIME USING QUASI-STEADY-STATE APPROACH
Reference: "Analytical Methods for Determining Fire Resistance of Steel Members,"
"SFPE Handbook of FireProtection Engineering, 3rd Edition, 2002, Page 4-209.
Temperature Rise in Steel Beam
DTs = (ki /(cs h W/D + 1/2 ci ri h2)) (Tf - Ts) Dt
| Where | DTs = temperature rise in steel (°F)
ki = thermal conductivity of insulation material (Btu/ft-sec-°F)
ri = density of insulation material (lb/ft3)
ci = specific heat of insulation material (Btu/lb-°F)
cs = specific heat of steel (Btu/lb-°F)
h = thickness of protection on steel beam (in)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
Tf = fire exposure temperature (°F)
Ts = steel temperature (°F)
Dt = time step (sec)
The Maximum Allowable Time Step
Dt = 15.9 W/D
| Dt = | 266.1241 | sec
| Dt = | 4.4354 | minutes
For ASTM-E-119 exposure, Tf at any time, t, is given by the following expression
Tf = C1 LOG (0.133 t + 1) + Ta
| Where | Tf = fire exposure temperature (°F) |  |  | Caution! This equation is only valid up to 1000 °F (538 °C) where
|  | C1 = constant = 620 |  |  | carbon steel structural members begin to fail. Predicted
|  | t = time step (sec) |  |  | temperatures above 1000 °F (538 °C) are not accurate or valid.
Ta = ambient air temperature (°F)
DTs1 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t1 + 1)+Ta) - Ts0) Dt
| Where | t1 = Dt/2
Ts0 = initial steel temperature (°F)
DTs2 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t2 + 1)+Ta) - Ts) Dt
| Where | t2 = t1 + Dt/2
Ts = Ts0 + DTs from previous row
Time | Time | DTs | Ts
(min) | (sec) | (°F) | (°F) |  |  | Time | Time | DTs | Ts
4.4354 | 266.1241 | 24.3666 | 101.3666 |  |  | (min) | (sec) | (°F) | (°F)
8.8708 | 532.2482 | 32.4529 | 133.8195 |  |  | 235.0763 | 14104.5769 | 60.7656 | 2879.3201 | failure of beam | Failure of Beam
13.3062 | 798.3723 | 36.3918 | 170.2112 |  |  | 239.5117 | 14370.701 | 60.9177 | 2940.2378 | failure of beam | Failure of Beam
17.7416 | 1064.4964 | 39.0432 | 209.2544 |  |  | 243.9471 | 14636.8251 | 61.067 | 3001.3049 | failure of beam | Failure of Beam
22.177 | 1330.6205 | 41.0376 | 250.2919 |  |  | 248.3825 | 14902.9492 | 61.2136 | 3062.5185 | failure of beam | Failure of Beam
26.6124 | 1596.7446 | 42.6362 | 292.9282 |  |  | 252.8179 | 15169.0733 | 61.3576 | 3123.8762 | failure of beam | Failure of Beam
31.0478 | 1862.8686 | 43.9703 | 336.8985 |  |  | 257.2533 | 15435.1974 | 61.4991 | 3185.3753 | failure of beam | Failure of Beam
35.4832 | 2128.9927 | 45.115 | 382.0135 |  |  | 261.6887 | 15701.3214 | 61.6381 | 3247.0134 | failure of beam | Failure of Beam
39.9186 | 2395.1168 | 46.1174 | 428.1309 |  |  | 266.1241 | 15967.4455 | 61.7748 | 3308.7882 | failure of beam | Failure of Beam
44.354 | 2661.2409 | 47.009 | 475.1399 |  |  | 270.5595 | 16233.5696 | 61.9092 | 3370.6973 | failure of beam | Failure of Beam
48.7894 | 2927.365 | 47.8119 | 522.9519 |  |  | 274.9949 | 16499.6937 | 62.0414 | 3432.7387 | failure of beam | Failure of Beam
53.2248 | 3193.4891 | 48.5421 | 571.494 |  |  | 279.4303 | 16765.8178 | 62.1714 | 3494.9102 | failure of beam | Failure of Beam
57.6602 | 3459.6132 | 49.2117 | 620.7057 |  |  | 283.8657 | 17031.9419 | 62.2994 | 3557.2096 | failure of beam | Failure of Beam
62.0956 | 3725.7373 | 49.83 | 670.5357 |  |  | 288.3011 | 17298.066 | 62.4254 | 3619.6351 | failure of beam | Failure of Beam
66.531 | 3991.8614 | 50.4043 | 720.9401 |  |  | 292.7365 | 17564.1901 | 62.5495 | 3682.1846 | failure of beam | Failure of Beam
70.9664 | 4257.9855 | 50.9405 | 771.8805 |  |  | 297.1719 | 17830.3142 | 62.6717 | 3744.8563 | failure of beam | Failure of Beam
75.4018 | 4524.1096 | 51.4432 | 823.3237 |  |  | 301.6073 | 18096.4383 | 62.7921 | 3807.6483 | failure of beam | Failure of Beam
79.8372 | 4790.2337 | 51.9165 | 875.2402 |  |  | 306.0427 | 18362.5624 | 62.9107 | 3870.559 | failure of beam | Failure of Beam
84.2726 | 5056.3578 | 52.3635 | 927.6037 |  |  | 310.4781 | 18628.6865 | 63.0275 | 3933.5865 | failure of beam | Failure of Beam
88.708 | 5322.4818 | 52.7871 | 980.3907 |  |  | 314.9135 | 18894.8106 | 63.1428 | 3996.7293 | failure of beam | Failure of Beam
93.1434 | 5588.6059 | 53.1895 | 1033.5802 | Failure of Beam |  | 319.3489 | 19160.9347 | 63.2563 | 4059.9856 | failure of beam | Failure of Beam
97.5788 | 5854.73 | 53.5729 | 1087.1531 | Failure of Beam |  | 323.7843 | 19427.0587 | 63.3684 | 4123.354 | failure of beam | Failure of Beam
102.0142 | 6120.8541 | 53.9388 | 1141.0919 | Failure of Beam |  | 328.2197 | 19693.1828 | 63.4788 | 4186.8328 | failure of beam | Failure of Beam
106.4496 | 6386.9782 | 54.2889 | 1195.3808 | Failure of Beam |  | 332.6551 | 19959.3069 | 63.5878 | 4250.4207 | failure of beam | Failure of Beam
110.885 | 6653.1023 | 54.6244 | 1250.0052 | Failure of Beam |  | 337.0905 | 20225.431 | 63.6954 | 4314.116 | failure of beam | Failure of Beam
115.3204 | 6919.2264 | 54.9466 | 1304.9518 | Failure of Beam |  | 341.5259 | 20491.5551 | 63.8015 | 4377.9175 | failure of beam | Failure of Beam
119.7558 | 7185.3505 | 55.2563 | 1360.2081 | Failure of Beam |  | 345.9613 | 20757.6792 | 63.9062 | 4441.8237 | failure of beam | Failure of Beam
124.1912 | 7451.4746 | 55.5546 | 1415.7627 | Failure of Beam |  | 350.3967 | 21023.8033 | 64.0096 | 4505.8334 | failure of beam | Failure of Beam
128.6266 | 7717.5987 | 55.8423 | 1471.605 | Failure of Beam |  | 354.8321 | 21289.9274 | 64.1117 | 4569.9451 | failure of beam | Failure of Beam
133.062 | 7983.7228 | 56.1201 | 1527.7252 | Failure of Beam |  | 359.2675 | 21556.0515 | 64.2126 | 4634.1577 | failure of beam | Failure of Beam
137.4974 | 8249.8469 | 56.3887 | 1584.1138 | Failure of Beam |  | 363.7029 | 21822.1756 | 64.3121 | 4698.4698 | failure of beam | Failure of Beam
141.9328 | 8515.971 | 56.6485 | 1640.7624 | Failure of Beam |  | 368.1383 | 22088.2997 | 64.4105 | 4762.8803 | failure of beam | Failure of Beam
146.3683 | 8782.095 | 56.9003 | 1697.6627 | Failure of Beam |  | 372.5737 | 22354.4238 | 64.5077 | 4827.388 | failure of beam | Failure of Beam
150.8037 | 9048.2191 | 57.1445 | 1754.8072 | Failure of Beam |  | 377.0091 | 22620.5479 | 64.6037 | 4891.9916 | failure of beam | Failure of Beam
155.2391 | 9314.3432 | 57.3815 | 1812.1887 | Failure of Beam |  | 381.4445 | 22886.6719 | 64.6986 | 4956.6902 | failure of beam | Failure of Beam
159.6745 | 9580.4673 | 57.6117 | 1869.8005 | Failure of Beam |  | 385.8799 | 23152.796 | 64.7924 | 5021.4826 | failure of beam | Failure of Beam
164.1099 | 9846.5914 | 57.8356 | 1927.6361 | Failure of Beam |  | 390.3153 | 23418.9201 | 64.8851 | 5086.3677 | failure of beam | Failure of Beam
168.5453 | 10112.7155 | 58.0534 | 1985.6895 | Failure of Beam |  | 394.7507 | 23685.0442 | 64.9768 | 5151.3444 | failure of beam | Failure of Beam
172.9807 | 10378.8396 | 58.2655 | 2043.955 | Failure of Beam |  | 399.1861 | 23951.1683 | 65.0674 | 5216.4118 | failure of beam | Failure of Beam
177.4161 | 10644.9637 | 58.4722 | 2102.4271 | Failure of Beam |  | 403.6215 | 24217.2924 | 65.157 | 5281.5688 | failure of beam | Failure of Beam
181.8515 | 10911.0878 | 58.6737 | 2161.1008 | Failure of Beam |  | 408.0569 | 24483.4165 | 65.2456 | 5346.8145 | failure of beam | Failure of Beam
186.2869 | 11177.2119 | 58.8702 | 2219.971 | Failure of Beam |  | 412.4923 | 24749.5406 | 65.3333 | 5412.1478 | failure of beam | Failure of Beam
190.7223 | 11443.336 | 59.0622 | 2279.0332 | Failure of Beam |  | 416.9277 | 25015.6647 | 65.4201 | 5477.5679 | failure of beam | Failure of Beam
195.1577 | 11709.4601 | 59.2496 | 2338.2828 | Failure of Beam |  | 421.3631 | 25281.7888 | 65.5059 | 5543.0738 | failure of beam | Failure of Beam
199.5931 | 11975.5842 | 59.4328 | 2397.7156 | Failure of Beam |  | 425.7985 | 25547.9129 | 65.5908 | 5608.6645 | failure of beam | Failure of Beam
204.0285 | 12241.7082 | 59.612 | 2457.3276 | Failure of Beam |  | 430.2339 | 25814.037 | 65.6748 | 5674.3394 | failure of beam | Failure of Beam
208.4639 | 12507.8323 | 59.7872 | 2517.1148 | Failure of Beam |  | 434.6694 | 26080.1611 | 65.758 | 5740.0973 | failure of beam | Failure of Beam
212.8993 | 12773.9564 | 59.9587 | 2577.0736 | Failure of Beam |  | 439.1048 | 26346.2851 | 65.8403 | 5805.9376 | failure of beam | Failure of Beam
217.3347 | 13040.0805 | 60.1267 | 2637.2003 | Failure of Beam |  | 443.5402 | 26612.4092 | 65.9218 | 5871.8594 | failure of beam | Failure of Beam
221.7701 | 13306.2046 | 60.2912 | 2697.4915 | Failure of Beam |  | 447.9756 | 26878.5333 | 66.0024 | 5937.8618 | failure of beam | Failure of Beam
226.2055 | 13572.3287 | 60.4525 | 2757.944 | Failure of Beam |  | 452.411 | 27144.6574 | 66.0823 | 6003.9441 | failure of beam | Failure of Beam
230.6409 | 13838.4528 | 60.6106 | 2818.5545 | Failure of Beam |  | 456.8464 | 27410.7815 | 66.1614 | 6070.1055 | failure of beam | Failure of Beam
[6 empty] | 461.2818 | 27676.9056 | 66.2397 | 6136.3452 | failure of beam | Failure of Beam
The Failure Temperature for Steel Beams is Assumed at 1000 °F (538 °C)
The above calculations are based on principles developed in the Society of Fire Protection
Engineers (SFPE) Handbook of Fire Protection Engineering, 3rd Edition 2002.
Calculations are based on certain assumptions and have inherent limitations. The results
of such calculations may or may not have reasonable predictive capabilities for a given
situation, and should only be interpreted by an informed user.
Although each calculation in the spreadsheet has been verified with the results of hand calculation,
there is no absolute guarantee of the accuracy of these calculations.
Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheet,
please send an email to nxi@nrc.gov or mxs3@nrc.gov.
Prepared by: |  | Date |  | Organization
Checked by: |  | Date |  | Organization
Additional Information
Revision Log | Description of Revision |  |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  |  | January 2005
Note on I19: This default value (0.132) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Column
CHAPTER 17. ESTIMATING FIRE RESISTANCE TIME OF STEEL COLUMNS PROTECTED
BY FIRE PROTECTION INSULATION (QUASI-STEADY-STATE APPROACH)
Version 1805.0
The following calculations estimate the fire resistance time for structural steel columns protected by board type fire protection
insulating material.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Column and Insulation Selected.
All subsequent output values are calculated by the spreadsheet, and based on values specified in the input
parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cell(s).
The chapter in the NUREG should be read before an analysis is made.
INPUT PARAMETERS
| Ratio of Weight of Steel Section per Linear Foot and Heated Perimeter (W/D) | [5 empty] | 15.7895 | lb/ft2
| Thickness of Applied Protection on Steel Column (h) |  |  |  | h ≥ 1/16 in |  | 1 | in |  | 0.083333 | ft
| Density of Applied Material (ri) | [5 empty] | 150 | lb/ft3
| Thermal Conductivity of Applied Material (ki) | [5 empty] | 0.9248 | Btu/ft-hr-°F |  | 0.00025689 | Btu/ft-sec-°F
| Specific Heat of Applied Material (ci) | [5 empty] | 0.1793 | Btu/lb-°F
| Ambient Air Temperature (Ta) | [5 empty] | 77 | °F
| Specific Heat of Steel (cs) | [5 empty] | 0.132 | Btu/lb-°F
Calculate
SECTIONAL FACTORS FOR STEEL COLUMNS
| Structural Shape | W/D Ratio
| W Shapes | (lb/ft2)
| 36x300 | 26.0473
| 36x280 | 24.4097
| 36x260 | 22.7671
| 36x245 | 21.5227
| 36x230 | 20.2703
| 36x210 | 20.9233
| 36x194 | 19.4146
| 36x182 | 18.2746
| 36x170 | 17.1285
| 36x160 | 16.1725
| 36x150 | 15.2091
| 36x135 | 13.7638
| 33x241 | 22.2222
| 33x221 | 20.474
| 33x201 | 18.7107
| 33x152 | 16.2901
| 33x141 | 15.1708
| 33x130 | 14.0465
| 33x118 | 12.8098
| 30x211 | 20.9689
| 30x191 | 19.0841
| 30x173 | 17.3709
| 30x132 | 15.5952
| 30x124 | 14.6992
| 30x116 | 13.7999
| 30x108 | 12.8994
| 30x99 | 11.8729
| 27x178 | 19.3286
| 27x161 | 17.5732
| 27x146 | 16.0132
| 27x114 | 14.5967
| 27x102 | 13.1316
| 27x94 | 12.1526
| 27x84 | 10.9162
| 24x162 | 19.3606
| 24x146 | 17.5586
| 24x131 | 15.8516
| 24x117 | 14.2365
| 24x104 | 12.7191
| 24x94 | 13.4526
| 24x84 | 12.095
| 24x76 | 10.9986
| 24x68 | 9.8921
| 24x62 | 9.9492
| 24x55 | 8.8745
| 21x147 | 19.025
| 21x132 | 17.195
| 21x122 | 15.9616
| 21x111 | 14.5925
| 21x101 | 13.3363
| 21x93 | 14.7307
| 21x83 | 13.2359
| 21x73 | 11.7191
| 21x68 | 10.956
| 21x62 | 10.0351
| 21x57 | 10.1318
| 21x50 | 8.9526
| 21x44 | 7.9255
| 18x119 | 17.4807
| 18x106 | 15.6882
| 18x97 | 14.4256
| 18x86 | 12.871
| 18x76 | 11.4415
| 18x71 | 12.814
| 18x65 | 11.7896
| 18x60 | 10.9339
| 18x55 | 10.0671
| 18x50 | 9.1954
| 18x46 | 9.2555
| 18x40 | 8.104
| 18x35 | 7.1429
| 16x100 | 16.1139
| 16x89 | 14.45
| 16x77 | 12.604
| 16x67 | 11.0424
| 16x57 | 11.3095
| 16x50 | 9.9933
| 16x45 | 9.0437
| 16x40 | 8.0822
| 16x36 | 7.3134
| 16x31 | 6.9781
| 16x26 | 5.9002
| 14x730 | 79.4486
| 14x665 | 73.7387
| 14x605 | 68.2908
| 14x550 | 63.1458
| 14x500 | 58.3317
| 14x455 | 53.8727
| 14x426 | 50.9316
| 14x398 | 48.0483
| 14x370 | 45.1082
| 14x342 | 42.1962
| 14x311 | 38.7378
| 14x283 | 35.6199
| 14x257 | 32.673
| 14x233 | 29.9037
| 14x211 | 27.3198
| 14x193 | 25.1684
| 14x176 | 23.1123
| 14x159 | 20.9454
| 14x145 | 19.2905
| 14x132 | 18.2216
| 14x120 | 16.6551
| 14x109 | 15.2075
| 14x99 | 13.8769
| 14x90 | 12.6701
| 14x82 | 14.4451
| 14x74 | 13.1128
| 14x68 | 12.1086
| 14x61 | 10.9237
| 14x53 | 10.7179
| 14x48 | 9.7594
| 14x43 | 8.792
| 14x38 | 8.3425
| 14x34 | 7.5041
| 14x30 | 6.6593
| 14x26 | 6.5809
| 14x22 | 5.6146
| 12x336 | 48.2124
| 12x305 | 44.4552
| 12x279 | 41.2315
| 12x252 | 37.7764
| 12x230 | 34.8881
| 12x210 | 32.2168
| 12x190 | 29.4878
| 12x170 | 26.6946
| 12x152 | 24.127
| 12x136 | 21.8065
| 12x120 | 19.4332
| 12x106 | 17.3203
| 12x96 | 15.7895
| 12x87 | 14.394
| 12x79 | 13.1411
| 12x72 | 12.0334
| 12x65 | 10.9152
| 12x58 | 10.9262
| 12x53 | 10.03
| 12x50 | 10.7219
| 12x45 | 9.707
| 12x40 | 8.6784
| 12x35 | 8.2938
| 12x30 | 7.1656
| 12x26 | 6.2475
| 12x22 | 6.5639
| 12x19 | 5.7186
| 12x16 | 4.8608
| 12x14 | 4.2748
| 10x112 | 21.3774
| 10x100 | 19.2926
| 10x88 | 17.1624
| 10x77 | 15.1724
| 10x68 | 13.5144
| 10x60 | 12.016
| 10x54 | 10.8798
| 10x49 | 9.919
| 10x45 | 10.4692
| 10x39 | 9.1496
| 10x33 | 7.8076
| 10x30 | 8.2607
| 10x26 | 7.2189
| 10x22 | 6.1596
| 10x19 | 6.3228
| 10x17 | 5.7015
| 10x15 | 5.0676
| 10x12 | 4.0909
| 8x67 | 16.0864
| 8x58 | 14.1005
| 8x48 | 11.8421
| 8x40 | 9.9875
| 8x35 | 8.8028
| 8x31 | 7.8464
| 8x28 | 8.0595
| 8x24 | 6.9649
| 8x21 | 6.7851
| 8x18 | 5.8664
| 8x15 | 5.6622
| 8x13 | 4.9492
| 8x10 | 3.8462
| 6x25 | 8.2327
| 6x20 | 6.6741
| 6x15 | 5.0733
| 6x16 | 6.8182
| 6x12 | 5.2174
| 6x9 | 3.9677
| 5x19 | 7.6305
| 5x16 | 6.4997
| 4x13 | 6.5
| User Specified Value | Enter Value
Select Column
Scroll to desired column size then Click on selection,
THERMAL PROPERTIES OF BOARD TYPE INSULATION MATERIALS
Select Insulation Type
Insulation Material |  | Density | Thermal | Specific Heat
Board |  | ρi | Conductivity ki | ci | Scroll to desired material then Click on selection
|  | (lb/ft3) | (Btu/ft-hr-°F) | (Btu/lb-°F)
Fiber-silicate, fiber-calcium silicate |  | 38 | 0.0867 | 0.2868
Gypsum plaster |  | 50 | 0.1156 | 0.4063
Mineral wool, fiber silicate |  | 10 | 0.1156 | 0.2868
Concrete |  | 150 | 0.9248 | 0.1793
User Specified Value |  | Enter Value | Enter Value | Enter Value
Reference: Buchanan, A. H., Structural Design for Fire Safety, 2001, Page 182.
ESTIMATING FIRE RESISTANCE TIME USING QUASI-STEADY-STATE APPROACH
Reference: "Analytical Methods for Determining Fire Resistance of Steel Members,"
"SFPE Handbook of FireProtection Engineering, 3rd Edition, 2002, Page 4-209.
Temperature Rise in Steel Beam
DTs = (ki /(cs h W/D+1/2cirih2)) (Tf - Ts) Dt
| Where | DTs = temperature rise in steel (°F)
ki = thermal conductivity of insulation material (Btu/ft-sec-°F)
ri = density of insulation material (lb/ft3)
ci = specific heat of insulation material (Btu/lb-°F)
cs = specific heat of steel (Btu/lb-°F)
h = thickness of protection on steel beam (in)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
Tf = fire exposure temperature (°F)
Ts = steel temperature (°F)
Dt = time step (sec)
The Maximum Allowable Time Step
Dt = 15.9 W/D
| Dt = | 251.0526 | sec
| Dt = | 4.1842 | minutes
For ASTM-E-119 exposure, Tf at any time, t, is given by the following expression
| Tf = C1 LOG (0.133 t + 1) + Ta |  |  |  | Caution! This equation is only valid up to 1000 °F (538 °C) where
| Where | Tf = fire exposure temperature (°F) |  |  | carbon steel structural members begin to fail. Predicted
|  | C1 = constant = 620 |  |  | temperatures above 1000 °F (538 °C) are not accurate or valid.
t = time step (sec)
Ta = ambient air temperature (°F)
DTs1 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t1 + 1)+Ta) - Ts0) Dt
| Where | t1 = Dt/2
Ts0 = initial steel temperature (°F)
DTs2 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t2 + 1)+Ta) - Ts) Dt
| Where | t2 = t1 + Dt/2
Ts = Ts0 + DTs from previous row
Time | Time | DTs | Ts |  | Time | Time | DTs | Ts
(min) | (sec) | (°F) | (°F) |  | (min) | (sec) | (°F) | (°F)
4.1842 | 251.0526 | 286.3299 | 363.3299 |  | 255.2368 | 15314.2105 | 553.9337 | 29632.4862 | failure of beam | Failure of Column
8.3684 | 502.1053 | 286.0134 | 649.3433 |  | 259.4211 | 15565.2632 | 555.1202 | 30187.6063 | failure of beam | Failure of Column
12.5526 | 753.1579 | 336.2522 | 985.5955 |  | 263.6053 | 15816.3158 | 556.2876 | 30743.8939 | failure of beam | Failure of Column
16.7368 | 1004.2105 | 350.8518 | 1336.4474 | Failure of Column | 267.7895 | 16067.3684 | 557.4366 | 31301.3305 | failure of beam | Failure of Column
20.9211 | 1255.2632 | 370.3047 | 1706.752 | Failure of Column | 271.9737 | 16318.4211 | 558.5677 | 31859.8983 | failure of beam | Failure of Column
25.1053 | 1506.3158 | 382.9828 | 2089.7348 | Failure of Column | 276.1579 | 16569.4737 | 559.6816 | 32419.5798 | failure of beam | Failure of Column
29.2895 | 1757.3684 | 394.855 | 2484.5898 | Failure of Column | 280.3421 | 16820.5263 | 560.7786 | 32980.3584 | failure of beam | Failure of Column
33.4737 | 2008.4211 | 404.6605 | 2889.2503 | Failure of Column | 284.5263 | 17071.5789 | 561.8593 | 33542.2177 | failure of beam | Failure of Column
37.6579 | 2259.4737 | 413.4577 | 3302.7081 | Failure of Column | 288.7105 | 17322.6316 | 562.9242 | 34105.1419 | failure of beam | Failure of Column
41.8421 | 2510.5263 | 421.249 | 3723.9571 | Failure of Column | 292.8947 | 17573.6842 | 563.9737 | 34669.1156 | failure of beam | Failure of Column
46.0263 | 2761.5789 | 428.3093 | 4152.2664 | Failure of Column | 297.0789 | 17824.7368 | 565.0083 | 35234.1239 | failure of beam | Failure of Column
50.2105 | 3012.6316 | 434.7372 | 4587.0036 | Failure of Column | 301.2632 | 18075.7895 | 566.0284 | 35800.1523 | failure of beam | Failure of Column
54.3947 | 3263.6842 | 440.6468 | 5027.6504 | Failure of Column | 305.4474 | 18326.8421 | 567.0344 | 36367.1867 | failure of beam | Failure of Column
58.5789 | 3514.7368 | 446.1114 | 5473.7618 | Failure of Column | 309.6316 | 18577.8947 | 568.0266 | 36935.2133 | failure of beam | Failure of Column
62.7632 | 3765.7895 | 451.1948 | 5924.9566 | Failure of Column | 313.8158 | 18828.9474 | 569.0055 | 37504.2188 | failure of beam | Failure of Column
66.9474 | 4016.8421 | 455.9462 | 6380.9028 | Failure of Column | 318 | 19080 | 569.9714 | 38074.1903 | failure of beam | Failure of Column
71.1316 | 4267.8947 | 460.4064 | 6841.3092 | Failure of Column | 322.1842 | 19331.0526 | 570.9247 | 38645.115 | failure of beam | Failure of Column
75.3158 | 4518.9474 | 464.609 | 7305.9182 | Failure of Column | 326.3684 | 19582.1053 | 571.8656 | 39216.9806 | failure of beam | Failure of Column
79.5 | 4770 | 468.5821 | 7774.5003 | Failure of Column | 330.5526 | 19833.1579 | 572.7945 | 39789.7751 | failure of beam | Failure of Column
83.6842 | 5021.0526 | 472.3495 | 8246.8498 | Failure of Column | 334.7368 | 20084.2105 | 573.7117 | 40363.4867 | failure of beam | Failure of Column
87.8684 | 5272.1053 | 475.9314 | 8722.7812 | Failure of Column | 338.9211 | 20335.2632 | 574.6174 | 40938.1042 | failure of beam | Failure of Column
92.0526 | 5523.1579 | 479.3453 | 9202.1265 | Failure of Column | 343.1053 | 20586.3158 | 575.5121 | 41513.6162 | failure of beam | Failure of Column
96.2368 | 5774.2105 | 482.6061 | 9684.7326 | Failure of Column | 347.2895 | 20837.3684 | 576.3958 | 42090.0121 | failure of beam | Failure of Column
100.4211 | 6025.2632 | 485.7271 | 10170.4597 | Failure of Column | 351.4737 | 21088.4211 | 577.269 | 42667.281 | failure of beam | Failure of Column
104.6053 | 6276.3158 | 488.7196 | 10659.1793 | Failure of Column | 355.6579 | 21339.4737 | 578.1317 | 43245.4128 | failure of beam | Failure of Column
108.7895 | 6527.3684 | 491.594 | 11150.7733 | Failure of Column | 359.8421 | 21590.5263 | 578.9844 | 43824.3972 | failure of beam | Failure of Column
112.9737 | 6778.4211 | 494.359 | 11645.1323 | Failure of Column | 364.0263 | 21841.5789 | 579.8272 | 44404.2244 | failure of beam | Failure of Column
117.1579 | 7029.4737 | 497.0229 | 12142.1552 | Failure of Column | 368.2105 | 22092.6316 | 580.6603 | 44984.8847 | failure of beam | Failure of Column
121.3421 | 7280.5263 | 499.5926 | 12641.7477 | Failure of Column | 372.3947 | 22343.6842 | 581.484 | 45566.3688 | failure of beam | Failure of Column
125.5263 | 7531.5789 | 502.0746 | 13143.8224 | Failure of Column | 376.5789 | 22594.7368 | 582.2985 | 46148.6673 | failure of beam | Failure of Column
129.7105 | 7782.6316 | 504.4748 | 13648.2972 | Failure of Column | 380.7632 | 22845.7895 | 583.104 | 46731.7713 | failure of beam | Failure of Column
133.8947 | 8033.6842 | 506.7983 | 14155.0955 | Failure of Column | 384.9474 | 23096.8421 | 583.9006 | 47315.6719 | failure of beam | Failure of Column
138.0789 | 8284.7368 | 509.0499 | 14664.1453 | Failure of Column | 389.1316 | 23347.8947 | 584.6886 | 47900.3606 | failure of beam | Failure of Column
142.2632 | 8535.7895 | 511.2338 | 15175.3791 | Failure of Column | 393.3158 | 23598.9474 | 585.4682 | 48485.8288 | failure of beam | Failure of Column
146.4474 | 8786.8421 | 513.3541 | 15688.7333 | Failure of Column | 397.5 | 23850 | 586.2395 | 49072.0682 | failure of beam | Failure of Column
150.6316 | 9037.8947 | 515.4144 | 16204.1477 | Failure of Column | 401.6842 | 24101.0526 | 587.0027 | 49659.0709 | failure of beam | Failure of Column
154.8158 | 9288.9474 | 517.4179 | 16721.5656 | Failure of Column | 405.8684 | 24352.1053 | 587.758 | 50246.8289 | failure of beam | Failure of Column
159 | 9540 | 519.3677 | 17240.9333 | Failure of Column | 410.0526 | 24603.1579 | 588.5055 | 50835.3344 | failure of beam | Failure of Column
163.1842 | 9791.0526 | 521.2666 | 17762.2 | Failure of Column | 414.2368 | 24854.2105 | 589.2454 | 51424.5798 | failure of beam | Failure of Column
167.3684 | 10042.1053 | 523.1172 | 18285.3172 | Failure of Column | 418.4211 | 25105.2632 | 589.9779 | 52014.5576 | failure of beam | Failure of Column
171.5526 | 10293.1579 | 524.9219 | 18810.2391 | Failure of Column | 422.6053 | 25356.3158 | 590.703 | 52605.2606 | failure of beam | Failure of Column
175.7368 | 10544.2105 | 526.6829 | 19336.922 | Failure of Column | 426.7895 | 25607.3684 | 591.421 | 53196.6816 | failure of beam | Failure of Column
179.9211 | 10795.2632 | 528.4023 | 19865.3243 | Failure of Column | 430.9737 | 25858.4211 | 592.132 | 53788.8136 | failure of beam | Failure of Column
184.1053 | 11046.3158 | 530.0819 | 20395.4062 | Failure of Column | 435.1579 | 26109.4737 | 592.8361 | 54381.6497 | failure of beam | Failure of Column
188.2895 | 11297.3684 | 531.7237 | 20927.1299 | Failure of Column | 439.3421 | 26360.5263 | 593.5334 | 54975.1831 | failure of beam | Failure of Column
192.4737 | 11548.4211 | 533.3292 | 21460.4591 | Failure of Column | 443.5263 | 26611.5789 | 594.2242 | 55569.4073 | failure of beam | Failure of Column
196.6579 | 11799.4737 | 534.9001 | 21995.3592 | Failure of Column | 447.7105 | 26862.6316 | 594.9084 | 56164.3157 | failure of beam | Failure of Column
200.8421 | 12050.5263 | 536.4377 | 22531.7968 | Failure of Column | 451.8947 | 27113.6842 | 595.5862 | 56759.9019 | failure of beam | Failure of Column
205.0263 | 12301.5789 | 537.9435 | 23069.7403 | Failure of Column | 456.0789 | 27364.7368 | 596.2578 | 57356.1597 | failure of beam | Failure of Column
209.2105 | 12552.6316 | 539.4188 | 23609.1591 | Failure of Column | 460.2632 | 27615.7895 | 596.9233 | 57953.083 | failure of beam | Failure of Column
213.3947 | 12803.6842 | 540.8647 | 24150.0238 | Failure of Column | 464.4474 | 27866.8421 | 597.5827 | 58550.6657 | failure of beam | Failure of Column
217.5789 | 13054.7368 | 542.2824 | 24692.3062 | Failure of Column | 468.6316 | 28117.8947 | 598.2362 | 59148.9019 | failure of beam | Failure of Column
221.7632 | 13305.7895 | 543.6731 | 25235.9793 | Failure of Column | 472.8158 | 28368.9474 | 598.8838 | 59747.7857 |  | Failure of Column
225.9474 | 13556.8421 | 545.0377 | 25781.017 | Failure of Column | 477 | 28620 | 599.5258 | 60347.3115 |  | Failure of Column
230.1316 | 13807.8947 | 546.3771 | 26327.3941 | Failure of Column | 481.1842 | 28871.0526 | 600.1621 | 60947.4736 |  | Failure of Column
234.3158 | 14058.9474 | 547.6923 | 26875.0864 | Failure of Column | 485.3684 | 29122.1053 | 600.793 | 61548.2666 |  | Failure of Column
238.5 | 14310 | 548.9842 | 27424.0705 | Failure of Column | 489.5526 | 29373.1579 | 601.4183 | 62149.6849 |  | Failure of Column
242.6842 | 14561.0526 | 550.2535 | 27974.324 | Failure of Column | 493.7368 | 29624.2105 | 602.0384 | 62751.7233 |  | Failure of Column
246.8684 | 14812.1053 | 551.501 | 28525.825 | Failure of Column | 497.9211 | 29875.2632 | 602.6532 | 63354.3766 |  | Failure of Column
251.0526 | 15063.1579 | 552.7275 | 29078.5525 | Failure of Column | 502.1053 | 30126.3158 | 603.2629 | 63957.6395 |  | Failure of Column
The Failure Temperature for Steel Beams is Assumed at 1000 °F (538 °C)
The above calculations are based on principles developed in the Society of Fire Protection
Engineers (SFPE) Handbook of Fire Protection Engineering, 3rd Edition 2002.
Calculations are based on certain assumptions and have inherent limitations. The results
of such calculations may or may not have reasonable predictive capabilities for a given
situation, and should only be interpreted by an informed user.
Although each calculation in the spreadsheet has been verified with the results of hand calculation,
there is no absolute guarantee of the accuracy of these calculations.
Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheet,
please send an email to nxi@nrc.gov or mxs3@nrc.gov.
Prepared by: |  | Date |  | Organization
Checked by: |  | Date |  | Organization
Additional Information
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | January 2005
Note on I19: This default value (0.132) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Data
SECTIONAL FACTORS FOR STEEL MEMBERS
| BEAMS |  | COLUMNS
| Structural Shape | W/D Ratio | Structural Shape | W/D Ratio
| W Shapes | (lb/ft2) | W Shapes | (lb/ft2)
| 36x300 | 29.6162 | 36x300 | 26.0473
| 36x280 | 27.756 | 36x280 | 24.4097
| 36x260 | 25.8943 | 36x260 | 22.7671
| 36x245 | 24.4816 | 36x245 | 21.5227
| 36x230 | 23.0596 | 36x230 | 20.2703
| 36x210 | 23.2773 | 36x210 | 20.9233
| 36x194 | 21.5965 | 36x194 | 19.4146
| 36x182 | 20.3286 | 36x182 | 18.2746
| 36x170 | 19.053 | 36x170 | 17.1285
| 36x160 | 17.991 | 36x160 | 16.1725
| 36x150 | 16.9213 | 36x150 | 15.2091
| 36x135 | 15.3191 | 36x135 | 13.7638
| 33x241 | 25.3063 | 33x241 | 22.2222
| 33x221 | 23.3194 | 33x221 | 20.474
| 33x201 | 21.314 | 33x201 | 18.7107
| 33x152 | 18.1664 | 33x152 | 16.2901
| 33x141 | 16.9208 | 33x141 | 15.1708
| 33x130 | 15.6705 | 33x130 | 14.0465
| 33x118 | 14.2944 | 33x118 | 12.8098
| 30x211 | 23.9671 | 30x211 | 20.9689
| 30x191 | 21.8161 | 30x191 | 19.0841
| 30x173 | 19.8613 | 30x173 | 17.3709
| 30x132 | 17.4018 | 30x132 | 15.5952
| 30x124 | 16.403 | 30x124 | 14.6992
| 30x116 | 15.4025 | 30x116 | 13.7999
| 30x108 | 14.4008 | 30x108 | 12.8994
| 30x99 | 13.2574 | 30x99 | 11.8729
| 27x178 | 22.1519 | 27x178 | 19.3286
| 27x161 | 20.1418 | 27x161 | 17.5732
| 27x146 | 18.3561 | 27x146 | 16.0132
| 27x114 | 16.3539 | 27x114 | 14.5967
| 27x102 | 14.7124 | 27x102 | 13.1316
| 27x94 | 13.6183 | 27x94 | 12.1526
| 27x84 | 12.236 | 27x84 | 10.9162
| 24x162 | 22.2286 | 24x162 | 19.3606
| 24x146 | 20.1657 | 24x146 | 17.5586
| 24x131 | 18.2124 | 24x131 | 15.8516
| 24x117 | 16.3598 | 24x117 | 14.2365
| 24x104 | 14.6187 | 24x104 | 12.7191
| 24x94 | 15.0832 | 24x94 | 13.4526
| 24x84 | 13.563 | 24x84 | 12.095
| 24x76 | 12.336 | 24x76 | 10.9986
| 24x68 | 11.0983 | 24x68 | 9.8921
| 24x62 | 10.9832 | 24x62 | 9.9492
| 24x55 | 9.7974 | 24x55 | 8.8745
| 21x147 | 21.9923 | 21x147 | 19.025
| 21x132 | 19.8795 | 21x132 | 17.195
| 21x122 | 18.4546 | 21x122 | 15.9616
| 21x111 | 16.8736 | 21x111 | 14.5925
| 21x101 | 15.4218 | 21x101 | 13.3363
| 21x93 | 16.5726 | 21x93 | 14.7307
| 21x83 | 14.889 | 21x83 | 13.2359
| 21x73 | 13.1819 | 21x73 | 11.7191
| 21x68 | 12.3244 | 21x68 | 10.956
| 21x62 | 11.2898 | 21x62 | 10.0351
| 21x57 | 11.2205 | 21x57 | 10.1318
| 21x50 | 9.919 | 21x50 | 8.9526
| 21x44 | 8.7824 | 21x44 | 7.9255
| 18x119 | 20.2769 | 18x119 | 17.4807
| 18x106 | 18.2026 | 18x106 | 15.6882
| 18x97 | 16.7374 | 18x97 | 14.4256
| 18x86 | 14.937 | 18x86 | 12.871
| 18x76 | 13.2799 | 18x76 | 11.4415
| 18x71 | 14.4763 | 18x71 | 12.814
| 18x65 | 13.3174 | 18x65 | 11.7896
| 18x60 | 12.3499 | 18x60 | 10.9339
| 18x55 | 11.3734 | 18x55 | 10.0671
| 18x50 | 10.3887 | 18x50 | 9.1954
| 18x46 | 10.3024 | 18x46 | 9.2555
| 18x40 | 9.02 | 18x40 | 8.104
| 18x35 | 7.9545 | 18x35 | 7.1429
| 16x100 | 18.7368 | 16x100 | 16.1139
| 16x89 | 16.807 | 16x89 | 14.45
| 16x77 | 14.6632 | 16x77 | 12.604
| 16x67 | 12.8486 | 16x67 | 11.0424
| 16x57 | 12.8186 | 16x57 | 11.3095
| 16x50 | 11.3272 | 16x50 | 9.9933
| 16x45 | 10.2515 | 16x45 | 9.0437
| 16x40 | 9.1612 | 16x40 | 8.0822
| 16x36 | 8.2941 | 16x36 | 7.3134
| 16x31 | 7.7849 | 16x31 | 6.9781
| 16x26 | 6.5851 | 16x26 | 5.9002
| 14x730 | 94.836 | 14x730 | 79.4486
| 14x665 | 88.1086 | 14x665 | 73.7387
| 14x605 | 81.6694 | 14x605 | 68.2908
| 14x550 | 75.5841 | 14x550 | 63.1458
| 14x500 | 69.8893 | 14x500 | 58.3317
| 14x455 | 64.6039 | 14x455 | 53.8727
| 14x426 | 61.0935 | 14x426 | 50.9316
| 14x398 | 57.6742 | 14x398 | 48.0483
| 14x370 | 54.1761 | 14x370 | 45.1082
| 14x342 | 50.7293 | 14x342 | 42.1962
| 14x311 | 46.5859 | 14x311 | 38.7378
| 14x283 | 42.8626 | 14x283 | 35.6199
| 14x257 | 39.3392 | 14x257 | 32.673
| 14x233 | 36.0263 | 14x233 | 29.9037
| 14x211 | 32.9344 | 14x211 | 27.3198
| 14x193 | 30.3499 | 14x193 | 25.1684
| 14x176 | 27.8886 | 14x176 | 23.1123
| 14x159 | 25.2923 | 14x159 | 20.9454
| 14x145 | 23.2932 | 14x145 | 19.2905
| 14x132 | 21.9375 | 14x132 | 18.2216
| 14x120 | 20.0585 | 14x120 | 16.6551
| 14x109 | 18.318 | 14x109 | 15.2075
| 14x99 | 16.7218 | 14x99 | 13.8769
| 14x90 | 15.2715 | 14x90 | 12.6701
| 14x82 | 16.9684 | 14x82 | 14.4451
| 14x74 | 15.4033 | 14x74 | 13.1128
| 14x68 | 14.2272 | 14x68 | 12.1086
| 14x61 | 12.8387 | 14x61 | 10.9237
| 14x53 | 12.4025 | 14x53 | 10.7179
| 14x48 | 11.2963 | 14x48 | 9.7594
| 14x43 | 10.1785 | 14x43 | 8.792
| 14x38 | 9.5218 | 14x38 | 8.3425
| 14x34 | 8.5669 | 14x34 | 7.5041
| 14x30 | 7.6062 | 14x30 | 6.6593
| 14x26 | 7.3611 | 14x26 | 6.5809
| 14x22 | 6.2827 | 14x22 | 5.6146
| 12x336 | 57.3991 | 12x336 | 48.2124
| 12x305 | 52.9705 | 12x305 | 44.4552
| 12x279 | 49.1919 | 12x279 | 41.2315
| 12x252 | 45.104 | 12x252 | 37.7764
| 12x230 | 41.6824 | 12x230 | 34.8881
| 12x210 | 38.5144 | 12x210 | 32.2168
| 12x190 | 35.2668 | 12x190 | 29.4878
| 12x170 | 31.9499 | 12x170 | 26.6946
| 12x152 | 28.8973 | 12x152 | 24.127
| 12x136 | 26.1371 | 12x136 | 21.8065
| 12x120 | 23.3085 | 12x120 | 19.4332
| 12x106 | 20.7775 | 12x106 | 17.3203
| 12x96 | 18.9474 | 12x96 | 15.7895
| 12x87 | 17.2833 | 12x87 | 14.394
| 12x79 | 15.7842 | 12x79 | 13.1411
| 12x72 | 14.4578 | 12x72 | 12.0334
| 12x65 | 13.1181 | 12x65 | 10.9152
| 12x58 | 12.9633 | 12x58 | 10.9262
| 12x53 | 11.9068 | 12x53 | 10.03
| 12x50 | 12.5313 | 12x50 | 10.7219
| 12x45 | 11.3481 | 12x45 | 9.707
| 12x40 | 10.1469 | 12x40 | 8.6784
| 12x35 | 9.5281 | 12x35 | 8.2938
| 12x30 | 8.2342 | 12x30 | 7.1656
| 12x26 | 7.1807 | 12x26 | 6.2475
| 12x22 | 7.2948 | 12x22 | 6.5639
| 12x19 | 6.3572 | 12x19 | 5.7186
| 12x16 | 5.4069 | 12x16 | 4.8608
| 12x14 | 4.7552 | 12x14 | 4.2748
| 10x112 | 25.622 | 10x112 | 21.3774
| 10x100 | 23.1392 | 10x100 | 19.2926
| 10x88 | 20.5988 | 10x88 | 17.1624
| 10x77 | 18.2213 | 10x77 | 15.1724
| 10x68 | 16.2388 | 10x68 | 13.5144
| 10x60 | 14.4462 | 10x60 | 12.016
| 10x54 | 13.083 | 10x54 | 10.8798
| 10x49 | 11.9318 | 10x49 | 9.919
| 10x45 | 12.3967 | 10x45 | 10.4692
| 10x39 | 10.8421 | 10x39 | 9.1496
| 10x33 | 9.261 | 10x33 | 7.8076
| 10x30 | 9.5314 | 10x30 | 8.2607
| 10x26 | 8.3311 | 10x26 | 7.2189
| 10x22 | 7.114 | 10x22 | 6.1596
| 10x19 | 7.1161 | 10x19 | 6.3228
| 10x17 | 6.4212 | 10x17 | 5.7015
| 10x15 | 5.7107 | 10x15 | 5.0676
| 10x12 | 4.6095 | 10x12 | 4.0909
| 8x67 | 19.2806 | 8x67 | 16.0864
| 8x58 | 16.9178 | 8x58 | 14.1005
| 8x48 | 14.2117 | 8x48 | 11.8421
| 8x40 | 12.003 | 8x40 | 9.9875
| 8x35 | 10.5823 | 8x35 | 8.8028
| 8x31 | 9.438 | 8x31 | 7.8464
| 8x28 | 9.5577 | 8x28 | 8.0595
| 8x24 | 8.2628 | 8x24 | 6.9649
| 8x21 | 7.9071 | 8x21 | 6.7851
| 8x18 | 6.8419 | 8x18 | 5.8664
| 8x15 | 6.4806 | 8x15 | 5.6622
| 8x13 | 5.6686 | 8x13 | 4.9492
| 8x10 | 4.4021 | 8x10 | 3.8462
| 6x25 | 9.8814 | 6x25 | 8.2327
| 6x20 | 8.016 | 6x20 | 6.6741
| 6x15 | 6.1038 | 6x15 | 5.0733
| 6x16 | 7.9569 | 6x16 | 6.8182
| 6x12 | 6.1017 | 6x12 | 5.2174
| 6x9 | 4.6392 | 6x9 | 3.9677
| 5x19 | 9.1751 | 5x19 | 7.6305
| 5x16 | 7.824 | 5x16 | 6.4997
| 4x13 | 7.82 | 4x13 | 6.5
| User Specified Value | Enter Value | User Specified Value | Enter Value