|  | Department of the Interior Bureau of Land Management. |  |
| --- | --- | --- |

COMMUNICATIONS SITE PLAN

QUEALY PEAK

KEMMERER FIELD OFFICE

Prepared by the

Kemmerer Field Office

State of Wyoming

Approved: Signed by Mary Jo Rugwell                                               June 29, 2004

Field Manager						Date

QUEALY PEAK COMMUNICATIONS

SITE PLAN

I.	INTRODUCTION	3

A.	Terms and Definitions	3

B.	Purpose	4

C.	Site Description	4

D.	Area Served	5

E.	Access	5

F.	Site History and Development	5

G.	Goals and Objectives of Site Management Plan	6

II.	AUTHORITY AND DIRECTION	6

A.	Authority	6

B.	Relationship to Communications Site Lease	6

III.	GENERAL RESPONSIBILITIES	7

A.	The Bureau of Land Management	7

B.	Facility Owners and Facility Managers 	7

C.	FCC and NTIA/IRAC	8

IV.	AUTHORIZED USES AND USERS WITHIN A FACILITY	8

A.	Exclusive Use of a Facility By a Single User	8

B.	Use by Multiple Users	9

V.	FEES	9

VI.	General Operation and Maintenance Direction	9

A.	Unique Resource Considerations at this Communication Site	9

B.	Wiring and Grounding	10

C.	Equipment	10

D.	Cables and Transmission Line (Wave Guides)	13

E.	Radiation	13

F.	Utilities-Availability of and Requirements for:	13

G.	Sanitary Facilities	14

H.	Security And Law Enforcement	14

I.	Site Maintenance	15

J.	Inspections	16

K.	Fire Prevention and Hazard Reduction Requirements	16

L.	Access Maintenance and Restrictions	17

VII.	CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION	17

A.	Responsibilities	17

B.	Construction Methods and Resource Protection	18

C.	Construction Inspection	19

D.	New or Remodeled/Expanded Buildings	20

E.	New or Remodeled/Expanded Towers	21

VIII.	SITE ASSOCIATION/ADVISORY GROUP	21

IX.	APPENDICES	22

A.	Site Map	22

B.	Authorized Facilities	22

C.	Site Photographs	22

D.	Inspection Checklist	22

INTRODUCTION

## Terms and Definitions

The terms used in this communication site plan conform to the definitions listed in the October 27, 1995, Federal Register notice “Fee Schedule for Communications Uses on Public Lands” and clarifications provided in Bureau of Land Management Handbook 2860-1.  In the event of a conflict, between the plan and these sources, the Federal Register notice and the Bureau of Land Management Handbook will govern.

The words “lease” and “lessee” as used in this plan refer to the relationship between the Bureau of Land Management and the communications use leaseholder, the lessee.  The words “customer” and “tenant” refer to the relationship between the lessee and the occupants in the lessee’s facilities.

LEASE – An authorization issued to a communication facility owner or facility manager, allowing for the use of Public Lands to construct and or operate a communications facility and unless specifically prohibited, to sublease to occupants in that facility.

LEASEHOLDER OR LESSEE – Facility Owner/Facility Manager

CUSTOMER – Entities that pay a facility owner, facility manager or tenant for communications services and are not re-selling or broadcasting communications services to others

TENANT – A communications user who rents space in a communications facility and operates communication equipment for the purpose of re-selling, or broadcasting communications services to others for profit.

COMMUNICATIONS SITE – An area of Bureau of Land Management administered public land designated through the land and resource management planning process.  A communications site may be limited to a single communications facility, but most often encompasses more than one.  Each site is identified by name; usually a local prominent landmark, such as Quealy Peak Communications Site.

FACILITY MANAGER – The holder of a Bureau of Land Management communications use authorization who leases space for other communication users.  A facility manager does not directly provide communications services to third parties.

FACILITY OWNER – Individual, commercial activities, organizations, or agencies that owns a communication facility on Federal land; own and operate their own communications equipment; and hold a communication use authorization.

NON-BROADCAST – This category includes Commercial Mobile Radio Service (CMRS), Facility Managers, Cellular Telephone, Private Mobile Radio Service (PMRS), Microwave, Local Exchange Network, and Passive Reflector.

BROADCAST – This category includes Television Broadcast, AM and FM Radio Broadcast, Cable Television, Broadcast Translator, Low Power Television, and Low Power FM Radio.

## Purpose

This plan is intended to be used by Bureau of Land Management officials administering communication uses at Quealy Peak, existing lessees, and applicants desiring a lease or a lease amendment.  The plan will be kept updated by amending pages or sections of the plan rather than issuing a revised edition of the plan.  When a revision is necessary, the plan will be amended by letter from the Kemmerer Field Office Manager enclosing a copy of revised pages or sections.  The amendments will be consecutively numbered.

General management direction for all land use is outlined in the Kemmerer Resource Area RMP adopted in 1986, the U.S. Code of Federal Regulations (CFRs) and the BLM Handbook and applicable Instruction Memoranda.  Specific direction for site management planning on designated communications site is contained in BLM Handbook 2860-1.  Primary regulations and policy pertaining to issuance of rights-of-way and leases by the Bureau of Land Management are found in Title 43, Code of Federal Regulations (CFR), Sections 2801- 2803 and BLM Handbook 2860-1.

The 1986 Kemmerer Resources Management Plan, RMP, does not specifically name Quealy Peak but states that all existing communication rights-of-way shall for subleasing, thus encouraging collocation. Quealy Peak was not included in any defined visual resource area in the 1986 RMP.  This RMP will be revised over the next 12-24 months.  Any applicable changes to this communications site plan as a result of the revised RMP will be made to keep this activity plan consistent with the RMP.

Quealy Peak will continue to be managed for both low power radio, microwave, cellular, cable TV, and broadcast uses.   The senior uses at this site are the microwave relay and associated low-power UHF and VHF radio uses.

No communications site plan has ever been prepared for this site.  This plan has technical standards for better management of the Quealy Peak communications site.  This plan governs development and management of Quealy Peak and will be modified in the future as needs and conditions warrant.  Any future such uses must be designed, installed, operated, and maintained to be compatible and not interfere with the primary uses.

This site-specific plan is administrative in nature and is Categorically Excluded from further review under the National Environmental Policy Act (NEPA) (516.DM2, Appendix 1,17).  Any additional development of the site will be addressed in a site-specific NEPA document.

## Site Description

The site is located on lands which are administered by the Kemmerer Field Office, and located north east of Kemmerer, Wyoming in portions of Section 31, Township 212 North, Range 115 East in the 6th Principle Meridian, Wyoming at approximately 41º 50’ 18” North Latitude and 110º 30’ 13” West Longitude.  A USGS benchmark is located on Quealy Peak at the north end of the site and established the elevation as 8017 feet above mean sea level (msl).  A site map is provided as Appendix A.

## Area Served

This site does not serve an RMA, Ranally Metro Area.  The largest community served is Kemmerer, Wyoming.  The population of Quealy Peak according to the 2000 Census is less than 25,000. Fee determination is based in part on the population zone which may be adjusted annually based upon changes in population and growth or designation of an RMA.

## Access

Access to the site is from US Highway 189 north of Kemmerer to Aspen Springs Road, a County road to just west of the summit.  A dirt road then follows the ridgeline through portions of private land to public lands and the communications site.  No rights-of-way across the private land appear to be of record.  Access across private lands and maintenance is the individual and collective responsibility of the users.

## Site History and Development

Quealy Peak communication site was first developed in 1962 under a grant issued to Mountain States Telephone for a microwave relay site with UHF/VHF two-radio.  This facility has changed ownership over time and is currently owned by Qwest Corp.  In 1980 the Lincoln County Sheriff was authorized to construct facilities and operate two-way radio equipment for public safety.  PacificCorp was authorized to add microwave and UHF/VHF facilities in 1982.  Exxon also was authorized to construct a microwave and UHF/VHF facility in 1983.

Western Wyoming Communications, now Uinta Communications, was authorized to construct a commercial communications facility at the site in 1984.  Two-way radio, paging, and other users were authorized as tenants or customers. This original grant was cancelled due to default and the building, now facility # 4 became the property of the Bureau of Land Management in 1970.  Individual grants have been issued to various broadcasting entities and others since that time.

In 1986, Northwest Pipeline added a microwave and two-way radio facility.  Also in 1986, Western Wyoming Cable was authorized to construct and operate a cable TV and LPTV translator facility at this site.  The facility has changed ownership numerous times as is currently cable TV only under ownership of Mallard Cablevision.

The final authorized facility was issued to Chaparral Broadcasting for an FM radio station facility.  This authorization was issued in 2000 as is still under an FCC construction permit until it demonstrates that it can operate at this site at its full power level of 100,000 watts without material interference with the other senior uses.

One additional cellular facility has been authorized adjacent to the Uinta Communications facility, but has yet to be constructed.

Current building space and tower space appears to be adequate for the foreseeable demand.  If in the future, this existing space becomes utilized to its optimum capacity, ample land area is available for future site development.  Site specific NEPA analysis will be required prior to any future facility modification or new facility construction.

Indications are that the site might already be close to its noise floor limitation for the senior two-way radio uses.  Additional studies, equipment upgrades, frequency isolation, and separation may be necessary in conjunction with the increase in power from the Chaparral FM station from 16,000 watts to the construction licensed level of 100,000 watts.

## Goals and Objectives of Site Management Plan

1.	Quealy Peak Site will be managed as a both low power two-way radio, microwave, and cellular and broadcast FM, TV and Cable TV.

2.	Future authorizations and additional uses must be designed to prevent degredation of the senior uses at this site.

3.	The overall appearance of the site and the integrity of the natural environment will be improved through stringent maintenance requirements and selection of authorized paint colors.

- The site will be systematically developed to maximize the number of compatible uses while ensuring safety and protection of resources.

- New facilities will be developed only after appropriate site-specific NEPA analysis and coordination with current lease holders and users.

AUTHORITY AND DIRECTION

## Authority

Bureau of Land Management authority to authorize communications uses on Resource Area (BLM) land is granted by the Federal Land Policy and Management Act of 1976, 90 Stat. 2776 (43 U.S. C. 1761-1771) and is reflected in Title 43, Code of Federal Regulations (CFR), Sections 2801- 2803

and WO IB 98-23.

Bureau of Land Management authority for communications site management planning is contained in Bureau of Land Management Handbook 2801-1, Plan of Development.  Direction on and policy for communication use authorizations is contained in Bureau of Land Management Manual (BLM Manual) section 2860.

Authority for the issuance of authorizations and/or licenses for the transmission and reception of electronic radiation for communication purposes is granted by Congress and administered by the Federal Communications Commission (FCC) and/or the National Telecommunication and Information Administration – Interagency Radio Advisory Committee (NTIA/IRAC).

## Relationship to Communications Site Lease

This site plan will be incorporated into all leases now and in the future issued for this communications site and must be used in conjunction with the lease. PROVISIONS OF THE SITE PLAN ARE ENFORCED THROUGH THE LEASE. Each lessee is expected to include the requirements of the lease and the site plan into any documents, which describe the business relationship between the lessee and the lessee's tenants and customers. The lessee is responsible for enforcing those provisions.

GENERAL RESPONSIBILITIES

## The Bureau of Land Management retains the responsibility for:

Issuing and amending leases and existing rights-of-way to facility owners and facility managers, only for the areas actually occupied by the authorized improvements.  Granting occupancy and use of Public Lands rest exclusively with the Bureau of Land Management Title 43, CFR, Sections 2801-2803

- .  The issuance of a FCC license (authorization), or frequency assignment, does not authorize occupancy of Public Lands.

1.   Approving any new/modified facility(ies) at the site.

- Approving amendments to leases to qualified buyers of facilities on the site.

## Facility Owners and Facility Managers (or their designated representatives) are responsible for:

- Complying with their authorization and all sections of this Site Management Plan.

- Ensuring that all new facilities, expansions, or improvements are consistent with the Resource Management Plans, RMP; any environmental document(s)/decisions for the site; and, this Site Plan.

- Ensuring facilities/equipment not complying with Federal/State/local laws/regulations/ ordinances will be removed or modified within one year of the approval of this plan.  Any modification needs pre-approval by the Bureau of Land Management.

- Keeping all facilities within the established limits of their authorized area.

- Providing the Bureau of Land Management, with the name, address and phone number for a local contact person.  The Facility Owner and Facility Manager and the contact person may be the same individual.  The contact person will be available for emergencies and will have the authority to make decisions about construction issues, facility maintenance and all equipment within the facility.

- Adhering to the terms of the Facility Owner/Manager Lease or Right-of-Way:

  - Facility Owners and Facility Managers are authorized to rent building/tower space to tenants and/or customers without prior written approval from the Bureau of Land Management.

  - Tenants and/or customers may not construct there own equipment shelter (building, shelter or cabinet) or antenna support structure (tower or mast).  The facility owner/manager must own all communication shelters and towers under their lease. [If that is not possible, a separate SF-299 application, cost-recovery deposit, analysis, and authorization are required.  This will also result in the use being a tenant/customer of the original lease holder in additional to being a separate facility for billing purposes.]

  - Tenants and/or customers using a facility covered by a Facility Lease/right-of-way will not have separate Bureau of Land Management permits to authorize the use.

  - Facility Owners and Facility Managers are responsible for complying with the terms and conditions of the Facility Lease or their valid right-of-way.  Facility Owner/Managers are also responsible for ensuring that their tenants and customers are in compliance with the terms and conditions of the Lease or right-of-way, and applicable FCC or NTIA/IRAC license terms and conditions.

  - The Facility Owner and Facility Manager may not place any unreasonable restrictions nor any restriction restraining competition or trade practices on tenants and/or customers, or potential tenants and/or customers.

- Ensuring that all communications equipment is properly installed, operated, and maintained.

- Ensuring that all communication equipment meets ANSI, FCC and Bureau of Land Management regulations, guidelines and standards concerning radiation limitations.

  - Monitoring radiation levels at their facility and;

  - Immediately correcting any radiation levels that are, or could be a hazard to human health. (FCC 47CFR sections 1.1307(b), 1.1310 and 2.1093) and FCC OET Bulletin 54, August 1999.

- Providing a certified copy of their use and the category of use along with the current phone numbers and addresses of all tenants and customers as of September 30 each year.  This report is due by October 15th.

- Keeping the premises around their buildings free of trash and debris.

- Placing the BLM serial number in six inch lettering on the face of the building visible from the access road.  This numbering system ties to the site map, Appendix A, and will be provide upon request to the County 911 emergency response system as a physical address in the case of emergencies.

## FCC and NTIA/IRAC are responsible for:

The responsibilities of the FCC and NTIA/IRAC are frequency management.  Correcting interference problems is the responsibility of the affected licensees.  The FCC and NTIA/IRAC are not normally responsible for the resolution of conflicts when the licensees or agencies are operating within the limits of the authorizations.

AUTHORIZED USES AND USERS WITHIN A FACILITY

## Exclusive Use of a Facility By a Single User

All facilities are currently designed to accommodate multiple users.

## Use by Multiple Users

The capacity of the current facilities is adequate on both the towers and within the existing buildings for future tenants/customers.  Any future proposals must be designed to include multiple users.  This includes multiple use of buildings, towers, back-up generators, grounding systems, fuel containers, access ways and parking areas.

Facility Owners and Facility Managers are not required to lease facility space to others if they can prove to the authorized Bureau of Land Management officer that:

- Space is not available;

- The use is incompatible with the existing facilities;

- Additional space is needed by the facility owner/manager;

- Additional users would violate system security needs; or,

- Potential interference is not resolvable.

FEES

The Bureau of Land Management will charge Facility Owners and Facility Managers annual fees based on the Fee Schedule for Communications Uses on Public Lands as adjusted annually.  These fees will be fair market value for the use of Public Lands.  Since this site is not within an established RMA, Ranally Metro Area, the population zone is less than 25,000, Zone 9 will be used for these calculations unless specifically agreed to by the authorizing officer and until populations or RMP designations change.

Fees that Facility Owners and Facility Managers may charge their tenants and “customers” are to be: reasonable (consistent with, and not in excess of, other fees for similar facilities) and commensurate with the uses and occupancy of the facilities and services provided to tenants and “customers” and

General Operation and Maintenance Direction

## Unique Resource Considerations at this Communication Site

- There are no currently identified special resource coordination considerations with on-site or adjacent resource values.  Should special conditions arise through the revision process of the RMP, this plan will be amended accordingly.  The area has been identified as being within suitable sage grouse nesting habitat, but long term use of the site for communications purposes has probably reduced the usefulness of sage grouse nesting in this area.

## Wiring and Grounding

1.	All equipment is to be installed within existing buildings and on equipment racks that are grounded and shielded.  Grounding is to be installed in accordance with accepted standards.

2.	All electrical wiring and grounding must meet the ‘National Electrical Code” and applicable estate codes.  All permanent wiring shall be installed in metallic conduit.  Surge protection shall be installed on all power distribution panels.

3.	Lightening protection “down” conductors installed upon communications towers shall be treated as “Transmission lines”.  Therefore, they shall have an insulating jacket.  Periodic bonding of the down conductor to the tower (Galvanized) steel shall be made with proper bonding connectors that are tin plated or made of brass.

4.	Each building is to have its own separate grounding system for all users in that structure.  Wherever practical, interconnection of individual grids and/or the simultaneous placement of a large sized copper ground wire with any new grounding systems that are buried on the site will be required.

5.	Site or facility grounding must be constructed of copper, with #2 AWG or larger wire or 2” or larger solid copper strap, connected to an adequate site/facility ground electrode system.  The site/facility ground electrode system shall be bonded to the power service entrance grounding electrode conductor.  Guy wires should also be grounded using manufacturers approved methods to preclude bi-metallic junction and corrosion.  All equipment on the site (buildings, towers, power units, transmitters, receivers, antennas, combiners, telephone systems, power cabinets, HVAC units, etc) must be connected to the site/facility ground by direct connection.  Electrical system ground wiring is required for electrical ground fault protection and circuit breaker coordination.  The grounding systems shall comply with applicable laws, codes and in accordance with standard engineering practice.  Below ground connections must use either an exothermic welding process (i.e. Cadweld, Thermoweld, etc.), copper wedge pressure devices (i.e. Ampact, Wrench-lock, etc.), or brazed copper connections in conjunction with a mechanical UL listed connector (to be used as a physical strength enhancement component).  Brazing by itself is not an acceptable method of bonding below earth grade (buried). Communications Equipment

## Equipment

Equipment Ownership

All equipment shall be labeled with:

- The owner’s name;

- Transmitter frequency(ies);

- A valid FCC, or IRAF, authorization;

- Transmitting power output(s); and

- A current 24-hour phone contact number.

Transmitting Equipment

All transmitters will have protective devices (shields, filters, isolation components), designed into or externally installed, to prevent interference with other users.  All transmitters will meet FCC licensing requirements.

The re-radiation of intercepted signals from any unprotected transmitter and its associated antenna system will be prevented by the use of appropriate filters (wide band and narrow band broadcast transmitters).

The direct radiation of out-of-band emissions (i.e. noise or spurious harmonics) will be reduced to a level such that they may not be identified as a source of interference as defined in the FCC Rules and Regulations (e.g. Part 90.209(e)).  If electromagnetic noise becomes an issue at this site, prior to any additional uses, noise threshold limits must be established, and amended into the Site Plan.

All transmitters not in immediate use and not specifically designated as standby equipment shall be removed.  Loads connected to circulators are to be capable of dissipating the total power output of the transmitter.

Receiving Equipment

A bandpass device (cavity, crystal filter, etc.) is recommended at the input of all receiving devices.  Cavity filters, or other protective device, may be used at receiver inputs to reduce interference.

Where duplexing is used, use of the notch type device should be avoided.  In situations where a notch type device is used, a bandpass filter must be used with the transmitter.

Tower

- Generally only one tower is authorized for each facility owner.  Facility Owners and Facility Managers may obtain permission to construct the second tower only after submitting evidence that demonstrates that their existing tower(s) is/are completely filled and full use has been made of combining systems.  When a single equipment building is required, multiple antenna support structures may need to be designed and authorized to accommodate all uses without interference.

- All new towers must be self supporting lattice or monopole or reduce visual impact, land occupied and reduce potential for interference.

- All towers will be left unpainted, if they are dull, galvanized steel.  Paint is required, only if they have a shiny (i.e. reflective) surface.  Only non-reflective, Bureau of Land Management approved dark gray to light tan (Carlsbad Canyon) colors will be approved unless FCC requires red/white striping.  All towers will be treated for low to non-reflectance.

- Only lights, beacons or strobes specifically required by the FCC will be allowed on towers (including antennas).

- The maximum tower height for this site is 199 feet including the antenna.

Antennas

            - As stated, the maximum antenna height will be 199 feet.

            - Microwave (dish) antennas (other than ground mounted satellite dishes) will be limited to a maximum of ten (10) feet in diameter.  Smallest diameter dishes are preferred if technically feasible.

            - All antennas must meet all OSHA safety standards.  If an antenna exceeds FCC public or occupation standards (see FSS OET Bulletin 57), it will be remedied within 24 hours after measures are taken or isolated (e.g., fencing, signing, relocation, lowering power levels are all possible remedies).  Ground measurements of Radio Frequency Radiation, RFR, levels will be taken before mitigation measures are implemented.

            - Color(s) for dish antennas, or covers, must be pre-approved by the Bureau of Land Management.  White dish antennas and/or covers will not be approved.  Existing white dishes and covers must be repainted or replaced with grey as repairs or replacement become necessary.

            - Antennas will be treated for low to non-reflectance.

Interference

The responsibility for correcting interference problems is a matter for resolution between the permit/lease holder of the facility(ies), the user causing the interference, and the affected party(ies).  Generally, the first users on a site have seniority with respect to the resolution of interference complaints.  Senior holders have an obligation to maintain their equipment to industry standards, to operate their systems in accordance with the terms of both the FCC license and NTIA/IRAC frequency authorization, and to comply with the Bureau of Land Management authorization.  New users on a site must correct, at their expense, interference problems that they create.  They must cease operation of the suspect equipment until the problem is corrected.  If interference problems cannot be resolved or corrected within a reasonable time, the new use that is causing the interference may be terminated and the equipment removed.

The Bureau of Land Management does not have authority for correcting interference problems, but can act as a mediator to help all affected parties.  Interference problems must be coordinated with the FCC or NTIA/IRAC, whichever is appropriate.

Interference with law enforcement and/or emergency communications must be corrected immediately.  The operation of equipment covered by this Site Plan shall not interfere with United States Government radio or electronic operations already in existence on public land within two (2) miles of the site to which this authorization refers.  The user causing this interference, shall, at its own expense, take all action necessary to prevent or eliminate such interferences.  If it does not eliminate such interference within ten (10) days after receipt of notice from the Bureau of Land Management to do so, this use will be terminated.

If electromagnetic noise becomes an issue, noise thresholds will be established and appended to this Plan.

## Cables and Transmission Line (Wave Guides)

All new cabling will be jacketed and shielded and shall either be flexible or semi-rigid type.  Existing substandard cables will be upgraded as repairs or replacement become necessary.

Cables will be properly installed and will be strapped and fastened down.

All transmission lines (wave guides) are to be supported in accordance with manufacturer’s specifications.

Unjacketed transmission line of any type is prohibited. No transmission lines shall be left unterminated.

Double shielded braided, or solid shielded cable will be used.  No RG-8 type cable is permitted.  No connector-type adapters will be used on transmission lines.  Only correct connectors that will mate to connected devices are to be used.

## Radiation

All communications uses must meet ANSI, FCC and Bureau of Land Management regulations guidelines and standards concerning radiation limitations.

Monitoring radiation levels at the site is the responsibility of all site users and will occur at intervals to comply with FCC regulations and guidelines.  A copy of the monitoring report will be provided to the Bureau of Land Management within 30 days of its completion.

Onsite RFR measurements will be taken using appropriate equipment that can adequately measure both on-tower and on the ground levels before mitigation measures related to RFR are implemented.

Security fences with RFR notice signs are required around areas that exceed public use levels.  All fencing location and design will be pre-approved by the Bureau of Land Management.

Warning signs will comply with ANSI C95.2 color, symbol, and content conventions.  Contact information including name and telephone number will also be included on warning signs.

Lowering power levels for on-tower access during maintenance will be coordinated between affected users.

Any identified RFR radiation problems that are, or could be, a human health hazard must be corrected within 24 hours after measurement tests have been completed or be removed from the site by the site user(s).  If the proposed corrective action involves any new ground disturbance, it must be pre-approved by the BLM.

## Utilities-Availability of and Requirements for:

Commercial Electrical Power

Commercial power is provided to the site under permit to Pacific Power Corp.  The distribution line and portions of the service drops are aerial.  Future service drops or modifications will be buried.

Telephone Service

Qwest provides commercial telephone service both copper and fiber optics to this site.

Fuel Tanks

All facility owners are responsible for providing fuel storage (propane or diesel) and emergency power for their tenants.  No tenants will be authorized their own fuel tank and/or generator.  Fuel storage will preferably be consolidated into a tank large enough in size to accommodate all tenants by each facility owner.  At a minimum, tanks will be grouped together in a consolidated area adjacent to their facilities.  All fuel, storage tanks (e.g. LPG, propane) must meet current fire department, Federal, State and Borough safety and hazardous materials requirements.

- All tanks will be:

a.	Signed in red letters, “SMOKING OR OPEN FLAME PROHIBITED WITHIN 20 FEET”;

b.	In conformance with National Fire Protection Association (NFPA) requirements; and,

c.	Painted an approved color, or screened by an enclosure to blend in with the natural environment.  (If an enclosure is used, it must be pre-approved and painted an approved color).

2.	Diesel tanks will also be:

a.	Enclosed in Bureau of Land Management and fire department approved secondary containment vaults that are painted a Bureau of Land Management approved color.

b.	Constructed with underground fuel lines.  Fuel line must be constructed of black, treated pipe and fittings, and must be posted.

## Sanitary Facilities

1.	Plans for any new sanitary facilities must be pre-approved by the Bureau of Land Management.  If it is determined by the Bureau of Land Management that the user needs such facilities, they will be provided by the applicant/holder in a manner and location satisfactory to the Bureau of Land Management and within the requirements of the Borough Health Department.

## Security And Law Enforcement

The Lincoln County Sheriff’s Department is the key law enforcement agency for the area.  They are responsible for most civil and criminal matters.  The Bureau of Land Management will be responsible for enforcing matters related to uses of BLM lands (e.g. resource protection issues).

Patrol and policing for security purposes is the holder’s responsibility.  If holders desire to have the protection of fencing, Bureau of Land Management approval must be obtained first.  To reduce visual clutter and efficiently utilize existing space, fencing groups of buildings will be encouraged.

Any access gates must be adequate for Bureau of Land Management and County Fire Department access needs.

Fencing

Several facilities are currently fenced.  Current fencing and any future modification must meet the following criteria:

1.	All fences must meet health and safety requirements.

2.	All fence locations and design require Bureau of Land Management pre-approval.  The standard fencing type will be chain-link (i.e. cyclone).

3.	The standard fence height will be eight (8) feet.

4.	Fencing will be designed, maintained, and of a type to minimize interference issues.

5.	Fences will be signed with RFR notices if RFR is above public levels.

## Site Maintenance

The objective of maintenance activities is to present a clean, neat, and orderly appearance at the site and have all of the authorized improvements safe for workers and the public.  All users will keep up the overall appearance of the site.

Miscellaneous debris remaining after any construction and/or equipment installation, removal or modification, is not only a hazard, but can cause interference or intermodulation problems.  In particular, all loose wire or metal objects are to be removed from the site.

The users of the Site will remove all graffiti within 10 working days of finding it.  If graffiti is on natural features (e.g. rocks), the graffiti will be removed in a method approved by the Bureau of Land Management Authorized Officer.

Holders will not be permitted to leave or dispose of trash, garbage or cut brush on public lands.  No outside trash or litter containers will be provided.  Site users (i.e. holders) will remove litter from the site as it is produced.

Policing of litter in common areas (i.e. areas between buildings and developed sites) is the shared responsibility of those holders bordering these areas.

During construction and/or maintenance, paintbrushes will not be cleaned off on the rocks around the site and excess materials (e.g. cement) will be removed from public lands.

Peeling paint on buildings and/or towers will be re-painted within ten (10) days of notification of the holder by the BLM.

Users are collectively and individually responsibly for the abatement and control of noxious weeds according to the Kemmerer Field Office Weed Abatement programs.

## Inspections

Unless waived in writing by the Bureau of Land Management, the holder is to provide, annually, a certified inspection of the facilities and equipment covered by the authorization.  The inspection will include technical review that assures that authorized equipment is operating within the specifics of this Site Plan, the FCC authorization, ANSI Standards, and the manufacturer’s specifications.  In addition, the inspection must assure that the authorized equipment is secure, free of rust, properly grounded, and otherwise properly operated and maintained.  This inspection should also review general good "housekeeping". A copy of the inspection report, certified by a telecommunication specialist, is to be provided to the Bureau of Land Management within 30 days of completion.  Appendix D provides an example of the inspection checklist.

The Bureau of Land Management may also conduct un-announced periodic reviews to monitor for authorization compliance.

## Fire Prevention and Hazard Reduction Requirements

Facility owners and managers will be required to maintain to mineral soil, a minimum of thirty (30) feet clearance around their buildings and a minimum of ten (10) feet clearance around any propane tanks.  Identified threatened, endangered, or sensitive plant species must remain within the minimum clearance areas.

Smoking is prohibited while walking in flammable vegetation.

The roof structure shall be kept reasonably clear of leaves, twigs, and other debris at all times.

No explosive will be stored at this site.  Flammable materials shall be stored in conformance with the requirements of local fire regulations.  Flammables will be placed in closed containers and stored away from sources of ignition and combustible materials.  If flammables are stored within a building, the building will be locked, properly signed and well ventilated.

Approved spark arresters will be required and maintained on all internal combustion engines.

At least one (1) U.L. rated 4 B:C dye chemical fire extinguisher is required inside each building.  Prior to each June, fire extinguisher(s) shall be inspected and refilled by holders, if necessary.

Any fire will be immediately reported to “911”, the nearest Bureau of Land Management office or the County Sheriff.

Periodic fire prevention inspections are made by Bureau of Land Management Officers.  They will call to your attention any lack of compliance with the above regulations, plus any other existing hazards.  Compliance with these inspections is required within the time limits specified.

All fire protection standards must be accomplished by the beginning of fire season unless otherwise agreed to, and then maintained throughout the fire season.

For new construction, the Bureau of Land Management will provide the Holder with a separate Construction Fire Plan which will be prepared at that time as applicable.

## Access Maintenance and Restrictions

Roads

From Highway 189, the current access is on County, private and finally on roads administered by the BLM.

Holders who damage or disturb the access road, or any associated structures, such as ditches, culverts, roadside vegetation, signs and/or underground utilities or facilities, will be required to repair the road or associated structures to conditions equal to or superior to those prior to any damage or disturbance.  These actions may require a new NEPA analysis.

Interior Site Driveways/ Parking Areas

Roads within the communications site will be maintained by the site users.  Interior roads will be planned and approved during establishment of new facilities.  Interior roads will be maintained in a manner to allow only one entrance to the site.  The intent is to discourage off-road vehicle use in and around the site.

Road Closures

Native surface roads are subject to periodic closures to entry during periods of extreme fire danger, inclement weather, or wet conditions.  Authorized site users may use the site during these periods, but should use judgment and may need to seek advance approval from the Bureau of Land Management.

CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION

## Responsibilities

In addition to the responsibilities listed in Section III, New Facility Owners and Facility Managers are responsible for:

1.	Submitting a complete application to the Kemmerer Field Office prior to any new construction, or modifications to existing improvements (ATTN: “Realty Specialist”).  The application must include:

a.	Submitting the appropriate Cost Recovery fees in connection with the application.

b.	A copy of the approved Site Plan Base Map showing all of the proposed (new) facilities including structures, towers, and auxiliary equipment;

c.	Completed drawings/plans prepared by a registered engineer and approved by the Bureau of Land Management;

d.	Identification of any microwave beam paths, a plot of their azimuth(s), and their proposed elevation(s) on the tower;

e.	All proposals must include documentation that shows that proposed facilities will not be obstructing, or interfering with, any existing fixed point to point antennas, omni directional broadcast antennas, or microwave beam paths in the directions of primary population targets.  Proposed beam path needs must be shown on Site Plan Base Map; and,

f.	Any needed recommendations, changes or modifications to their original proposal, based on any required resource surveys and/or reports.

2.	Demonstrating that their proposals will not cause undue interference with any existing uses before new facilities can be approved by the Bureau of Land Management, the applicant has the responsibility to demonstrate that they will not cause undue interference with any existing uses.  In addition, it is the applicant’s responsibility to show that any new facilities will make the most efficient use of the limited amount of space at the site.

3.	Showing that their proposals will provide for future users without additional construction are encouraged.

4.	Providing engineering and geotechnical investigations for development of specific foundation designs and grading plans.

5.	Providing an Erosion Control Plan prior to construction activities.  At a minimum, the Erosion Control Plan must include: sediment control, stipulations that cut/fill slopes will be graded and contoured to prevent erosion and/or excessive runoff, and recommendations for temporary erosion control measures, (e.g. netting, silt fences, swales, and/or sediment collection areas).

6.	Coordinating with other Federal (e.g., FCC and FAA), State and Borough agencies and obtainment of all required approvals and/or permits.

7.	Providing 30-day notice to all facility owners/managers at the site, as well as the Bureau of Land Management, of all new frequencies proposed for the site.  A completed BLM technical data sheet or equivalent must be sent with the 30-day notice to allow for comment of potential interference.  This would be for new frequencies for themselves and their tenants.

8.	Insuring that all written approvals have been obtained from the Bureau of Land Management prior to construction.  In addition:

New and/or modified facilities will not obstruct existing fixed point-to-point antennas or omni-directional broadcast antennas in directions of primary population targets.

## Construction Methods and Resource Protection

Plans submitted by an applicant for any new construction or modifications shall specify provisions for soil rehabilitation measures including, but not limited to, soil replacement and stabilization and for proper handling of runoff from buildings, parking area, access roads, and undeveloped common areas.

The following methods and resource protection measures will be required to minimize impacts during construction:

1.	Avoid and protect sensitive resource areas, as identified by the Bureau of Land Management.

2.	Compliance with the Erosion Control Plan.

3.	During construction and/or maintenance, paintbrushes will not be cleaned off on rocks around site and no marks of any kind (including survey marks) will be permitted on rocks.

4.	Minimize ground disturbance and vegetation removal as much as possible during construction activities.  All ground-disturbing activities require Bureau of Land Management pre-approval.

5.	Any extensive cut and fill slopes will be re-vegetated with vegetation species approved by BLM as soon as possible after construction.  All re-vegetation requires Bureau of Land Management pre-approval. If necessary, reseeding will be required until vegetation is successfully established as determined by the Bureau of Land Management.

6.	No grading material will be cast off during construction/reconstruction activities. Excess soil can be used for fill material on road and/or building/tower pads.

7.	Temporary, on-site storage of construction materials will require pre-approval by the Bureau of Land Management.

8.	Construction materials and supplies, except for hazardous materials (see number 10. below) may be left unattended at the construction site at the end of each workday, but at the owner’s risk.

9.	Hazardous materials, including, but not limited to all fuels, oils, and lubricants are not to be left unattended at the site at any time.  During construction, these materials are to be removed from the site at the end of each workday, or temporarily stored inside a locked and signed building until the following workday.

10.	All surplus construction materials and/or waste debris must be removed from the site no later than thirty (30) days after construction has been completed.

11.	Any earth moving or heavy equipment (e.g. dozers, graders, cranes, backhoes, etc.) leaving the designated roadway and/or approved parking area(s) to perform authorized activities at the site, will be washed off prior to being brought onto public land to prevent the introduction and spread of noxious weeds into the area.

## Construction Inspection

1.	All new construction, reconstruction, or major modification shall conform to the established technical standards and accepted engineering practices (i.e., the Uniform Building Code).

2.	Any construction inspections required by other applicable agencies are the responsibility of the holder.  Copies of completed inspections are to be provided to the Field Manager, either as they occur or as part of the final as-built plan.  Inspection information shall become a permanent part of the proponent’s special-use file.

3.	The Holder agrees that corrective work detailed in Bureau of Land Management, or other agency required compliance inspections, would be completed by the scheduled completion date.  If the Holder disagrees or has questions about specific items, the Holder must contact the Bureau of Land Management in order that the disagreement or item may be resolved.

4.	A final set of as-built plans will be submitted to the Field Manager within 90 days of acceptance of structure (if contracted) or of completion date.

## New or Remodeled/Expanded Buildings

- Any new buildings must be designed to accommodate multiple users along with fitting into the physical environment as defined in a site-specific environmental analysis developed at the time of the proposal.

- Buildings are required to be one-story, flat roofed.  The roof must be metal or covered with metal to be fire resistant.  Roofs can be equipped with antenna support structures, such as poles and railings that can extend up to 25-feet above ground level.

- Facility Owners and Facility Managers are encouraged to construct the interior of their buildings in a modular fashion, so that they can:

a.	Sublease sections to others;

b.	Provide tenants and customers with internal separation and security;

c.	Reduce physical interference; and

d.	Increase management effectiveness.

- The following materials are approved for construction of new facilities (i.e. buildings)

#### a.	Floors – Concrete slab with drainage.

b.	Walls – Concrete block, pre-fabricated concrete, or other pre-approved fire resistant materials.

c.	Roof – Metal, or concrete, if painted to eliminate shiny surfaces, or other fireproof material as approved by the Bureau of Land Management.  Proposals for wooden roofs will not be approved.

d.	Partitions – If it is felt partitions are necessary in buildings, ensure they are constructed with fire resistant material (e.g., concrete block, reinforced concrete, or properly grounded expanded metal.

e.	Color – Proposed color for use on all exterior building surfaces must be pre-approved by the Bureau of Land Management. The goal of the color selection for the facilities is to make the building as inconspicuous as possible and make buildings located on the skyline look inconspicuous when viewed from a distance.  The intent is to reduce or eliminate glare from reflective and/or illuminated surfaces such as windowpanes, sheeting and reflective paints.  Non-reflective, Bureau of Land Management approved dark gray to green colors will be used on equipment buildings.

f.	Pre-fabricated equipment shelters which meet the above requirements may be approved.

- Building entry lights must:

a.	Only light the immediate area in the vicinity of the door;

b.	Be motion activated and have a limited time duration (e.g., 3-5 minutes); and

c.	Have a shielded beam that is pointed at the building door.

Requests for all-night (i.e. “dusk-to-dawn”) lighting, or entry lighting that would be visible from outside of the site will not be approved.

## New or Remodeled/Expanded Towers

- All new construction, reconstruction, and modifications to towers will be pre-approved by the Bureau of Land Management prior to implementation.

- It is the applicant/holder’s responsibility to assure that a new, or modified, structure will not unduly interfere electronically or physically with any existing equipment at the site.  Towers must be spaced, so as to prevent ground level radiation and/or interference problems.  This must be clearly demonstrated in writing to the Bureau of Land Management prior to issuance of a lease, permit, or amendment.

- All new towers will comply with current structural and safety specifications and design standards, including safety-climbing devices.  Towers should be as narrow and “open” as safety and structural integrity allow.  New towers will be designed using maximum wind, snow, and/or tower loading anticipated for the site.

SITE ASSOCIATION/ADVISORY GROUP

A Site Association is desirable for the Quealy Peak Communication Site as issues arise in the future requiring more user coordination.  If formed in the future, the Site Association would be responsible for obtaining access, maintenance and upkeep of internal roads and parking areas.  The Site Association would also be responsible for ensuring cooperation between users for on-tower access.  A Site Safety officer would be identified within the Site Association. The Site Association would be expected to develop a Radiofrequency Radiation Plan/Agreement and recommend measures to reduce interference issues (e.g., through use of filters).

The goal of the Site Association would also be to maximize the effective use of the site.  The objective of a sanctioned association will be to represent all site users as a group when dealing with the Kemmerer Field Office on matters relating to the Site administration.  The association would be able to work in cooperation with the Bureau of Land Management (BLM), and Lincoln County to identify problems or opportunities and make recommendations to these entities for any changes in management strategies at the site.  The association could also provide input to these entities regarding the future addition of equipment and facilities at the site. While the advice and recommendations of the association would not be binding on these entities, they could use the input for administration of the site.  The BLM and County or their representatives would be a member of such a group and would help jointly develop the charter (i.e., the ground rules).

In the absence of a formal Site Association, the BLM may utilize a Site Advisory Group that can make suggestions and/or recommendations to specific problems associated with the administration of the site.

APPENDICES

## Site Map

## Authorized Facilities

## Site Photographs

## Inspection Checklist

APPENDIX A

QUEALY PEAK

SITE MAP

APPENDIX B

LEASEE FACILITY TABLE

(See associated User’s Table on this Website)

|  | Auth # | Use | Building | Tower | Access/Parking | Other |
| --- | --- | --- | --- | --- | --- | --- |
| Facility 1 Union Telephone Co. | WYW 102142 | CEL | 10’x 14’ aggregate 10’x 18’ fiberglass | 40’ lattice | Access and parking | 250 gal propane 8’x 8’ metal generator shelter |
| Facility 2 Exxon | WYW 82543 | MIC | 12’x 24’ aggregate | 60’ lattice | Access and parking | 500 gal propane 15Kw generator in 7’x 10’ agg shelter |
| Facility 3 Lincoln County | WYW 60706 | PMRS | 14’x 20’ metal | 20’ & 50’ lattice | Access and parking | 500 gal propane 5Kw generator in 6’x 8’ wood shelter |
| Facility 4 Mallard Cablevision | WYW 94321 | CT | 21’x 25’ metal | 2- 25’ & 30’ lattice, rec’v dish, Ch 10 rec’v antenna and 3 wood pole support (to remove) | Access and parking | 500 gal propane outside generator |
| Facility 5 Northwest Pipeline | WYW 94356 | MIC | 11’x 22’ metal | 45’ & 60’ lattice | Access and parking | 1000 gal propane, generator in 9’x 11’ fiberglass shelter |
| Facility 6 Chaparral Broadcasting | WYW 149815 | FM | 20’x 30’ wood | 160’ guyed | Access and parking |  |
| Facility 7 Pacificorp | WYW 78439 | MIC | 15’x 23’ block | 45’ lattice | Access and parking | 500 gal propane, 7.5 Kw generator 45’x 70’ fence |
| Facility 8 Qwest | WYW 0170345 | MIC | 24’x 28’ concrete | 60’ lattice | Access and parking | Diesel tank and generator 158’x 133’ x 116’ 95’ fence |
| Facility 9 Uinta Comm. | WYW 87816 | CMRS | 12’x 24’ wood w/ alum siding | 40’ lattice 90’ guyed | Access and parking |  |

APPENDIX C

SITE PHOTOGRAPHS

(See associated Facility Photos on this Website

APPENDIX D

INSPECTION CHECKLIST

COMMUNICATIONS SITE INSPECTION CHECKLIST

EXAMPLE

Site Name  Big Mountain                	Date  5/26/92

Inspector(s) Name   James Holder

I.  Site Inspection.  Each communications site should be inspected at least once each year.  Inspections should include a careful examination of:

1.  Power Systems

a. Power lines - (10ft. clearance from average snow level)

b. Solar Array

c. Generators-Fuel Storage

d. Batteries

- Safety venting

- eye wash

- goggles

e. Wiring

f. Protection (fuses)

2.  Grounding

a. Building

b. Antenna system

c. Equipment

d. Lightning Protection

e. Standby Power

3.  Conformance to

a. Equipment Manufacturers Specifications.

- Installation

- Maintenance

b. Conditions of Permit

c. Safety Standards

d. Specification of Site Plan

e. Specification of Site Design

f. Conditions of License or Authorization

4.  Structures

a. Towers

b. Buildings

c. Cable Trays

5.  Electromagnetic Environment

a. Site Noise Level

- Ambient (noise floor) (General Electric ECP-877A)

- Transmitter produced

b. Effective Receiver Sensitivity

c. Electromagnetic Radiation Safety

- Levels (ANSI C95.1 - 1982)

- Signing

- Fencing

6.  Housekeeping

a. Internal

b. External

COMMUNICATIONS TOWER INSPECTION CHECKLIST

Tower Owner        James Holder                                 Date of Inspection  5/26/92

Name of Inspector(s)  Joe Technician & James Holder

| TOWER | YES | NO |
| --- | --- | --- |
| Bent or fractured cross members? Loose or missing bolts? Broken or cracked welds? Signs of unusual stress? Twisted or distorted tower? Signs of rust, pitting, rot, etc.? Does the tower need paint or repair? | X X | X X X X X |

Condition of galvanizing:   GOOD

Condition of paint (faded, peeling, etc.):  PAINT IS PEELING

Condition of cat walk:    GOOD

Condition of climbing pegs or steps:   GOOD

Condition of fall safety system:    GOOD

NOTES:  James Holder has contacted Service R Us to plan to paint tower.

Painting to start on 6/10/92___________________________________________

| GUY WIRES | YES | NO |
| --- | --- | --- |
| Broken guy wire strands? Any rust or deterioration noted? |  | X X |

Guy wire connections; preforms         clamps         both    X

Conditions of thimbles and shackles:   GOOD

Condition of preforms and/or cable clamps:   GOOD

NOTES:   General maintenance completed last year._____________________________

______________________________________________________________________________

______________________________________________________________________________

| GROUNDING SYSTEM | YES | NO |
| --- | --- | --- |
| Grounding clamps, straps or wires, broken or torn? Connections clean and secure? Lighting rod at the top of the tower? Signs of arcing? Gradual curves in grounding wires? Transmission line lightning-loop secure at the bottom of the tower? | X X X | X X X |

Condition of antenna grounding:   GOOD

Condition of transmission line grounding kits at the top and bottom:    GOOD

NOTES:   MAINTENANCE COMPLETED LAST YEAR._________________________

_____________________________________________________________________________

_____________________________________________________________________________

| ANTENNA AND TRANSMISSION LINES | YES | NO |
| --- | --- | --- |
| Antennas stable? Bolts and connectors secure? Connections to transmission weather sealed transmission line brackets/wire ties secure? Signs of transmission line slippage? Waterproof jacket unbroken transmission line secured at 3 ft. intervals? Hoist Grip secure? Gradual Curves in transmission line? | X X X X X X X |  |

Condition of antenna mounting hardware:   VERY GOOD

Physical damage to antenna and line (dents, cracks):  NONE

NOTES:   ____________________________________________________________

_____________________________________________________________________

_____________________________________________________________________

ACTION ITEMS:  PAINTING TOWER - TO BE COMPLETED 6/2________

______________________________________________________________________