## 25F nomo
Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 014
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6612.5153
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -1395.83 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | -190.8 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | -752.7 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 21.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | -190.8 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 330.59 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | -1120.66 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 926.29 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | -540.03 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1485.12 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 21.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | -752.7 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | -822.45 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | -540.03 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | -203.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | -203.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 330.59 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 409.46 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | -194.58 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 890.7 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 409.46 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -1395.83 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 926.29 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -1120.66 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 337.24 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | -822.45 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 890.7 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | -194.58 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1485.12 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 337.24 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 014
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6283.7067
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -862.74 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 274.92 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | -283.94 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 506.33 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 274.92 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 842.26 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | -636.79 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1404.38 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | -32.96 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1951.16 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 506.33 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | -283.94 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | -282.26 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | -32.96 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 297.73 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 297.73 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 842.26 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 863.7 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 318.13 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1368.04 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 863.7 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -862.74 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1404.38 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -636.79 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 829.57 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | -282.26 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1368.04 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 318.13 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1951.16 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 829.57 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 014
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6005.974
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -362.35 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 745.82 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 208.49 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 964.11 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 745.82 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1310.82 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | -121.73 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1874.09 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 436.29 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2365.41 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 964.11 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 208.49 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 217.41 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 436.29 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 754.75 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 754.75 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1310.82 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1325.23 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 783.27 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1844.83 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1325.23 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -362.35 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1874.09 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -121.73 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1286.41 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 217.41 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1844.83 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 783.27 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2365.41 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1286.41 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 014
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4962.9553
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1546.91 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2582.35 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2104.73 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2918.4 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2582.35 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2864.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 1772.22 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3306.31 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 460 | 2314.56 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1796.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2918.4 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2104.73 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2033.9 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2314.56 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2617.13 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2617.13 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2864.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3138.92 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2600.79 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1946.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3138.92 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1546.91 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3306.31 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1772.22 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2046.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2033.9 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1946.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2600.79 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1796.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2046.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 014
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4630.6393
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2004.48 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2440.39 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2433.74 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2565.44 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2440.39 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2782.68 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2218.46 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3075.84 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2545.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1596.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2565.44 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2433.74 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2535.69 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2545.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2741.73 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2741.73 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2782.68 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3058.02 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3035.43 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1702.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3058.02 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2004.48 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3075.84 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2218.46 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1811.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2535.69 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1702.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3035.43 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1596.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1811.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
G0 | -1395.83 | -862.74 | -362.35 | 1546.91 | 2004.48
G1 | -752.7 | -283.94 | 208.49 | 2104.73 | 2433.74 | Season/Year: | WINTER 2009
G2 | -190.8 | 274.92 | 745.82 | 2582.35 | 2440.39 | Direction: | South-to-North (SN)
G3 | -1120.66 | -636.79 | -121.73 | 1772.22 | 2218.46 | Case Loads: | Heavy Loads
G4 | -540.03 | -32.96 | 436.29 | 2314.56 | 2545.71 | Outage: | 014
G5 | 21.67 | 506.33 | 964.11 | 2918.4 | 2565.44 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | -822.45 | -282.26 | 217.41 | 2033.9 | 2535.69 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | -203.67 | 297.73 | 754.75 | 2617.13 | 2741.73 | Study Person: | FRP9899
G8 | 330.59 | 842.26 | 1310.82 | 2864.33 | 2782.68 | Source: | 014WINTER09v1SNH
G9 | -194.58 | 318.13 | 783.27 | 2600.79 | 3035.43
G10 | 409.46 | 863.7 | 1325.23 | 3138.92 | 3058.02
G11 | 926.29 | 1404.38 | 1874.09 | 3306.31 | 3075.84
G12 | 337.24 | 829.57 | 1286.41 | 2046.15 | 1811.19
G13 | 890.7 | 1368.04 | 1844.83 | 1946.58 | 1702.76
G14 | 1485.12 | 1951.16 | 2365.41 | 1796.6 | 1596.89
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 014 | Christopher Tap-O’Brien (PSE) sect. of Tacoma-Covington #2 230kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6612.5153 | -1395.83 | -752.7 | -190.8 | -1120.66 | -540.03 | 21.67 | -822.45 | -203.67 | 330.59 | -194.58 | 409.46 | 926.29 | 337.24 | 890.7 | 1485.12
35F | 6283.7067 | -862.74 | -283.94 | 274.92 | -636.79 | -32.96 | 506.33 | -282.26 | 297.73 | 842.26 | 318.13 | 863.7 | 1404.38 | 829.57 | 1368.04 | 1951.16
45F | 6005.974 | -362.35 | 208.49 | 745.82 | -121.73 | 436.29 | 964.11 | 217.41 | 754.75 | 1310.82 | 783.27 | 1325.23 | 1874.09 | 1286.41 | 1844.83 | 2365.41
60F | 4962.9553 | 1546.91 | 2104.73 | 2582.35 | 1772.22 | 2314.56 | 2918.4 | 2033.9 | 2617.13 | 2864.33 | 2600.79 | 3138.92 | 3306.31 | 2046.15 | 1946.58 | 1796.6
70F | 4630.6393 | 2004.48 | 2433.74 | 2440.39 | 2218.46 | 2545.71 | 2565.44 | 2535.69 | 2741.73 | 2782.68 | 3035.43 | 3058.02 | 3075.84 | 1811.19 | 1702.76 | 1596.89

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -1395.69 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 522.09 | 522.06 | 6653.03 | -1395.83 | 592.65 | FULL
G1 | -752.95 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 522.78 | 522.81 | 6585.62 | -752.7 | 259.92 | FULL
G2 | -192.27 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 522.62 | 522.66 | 6598.06 | -190.8 | -24.94 | FULL
G3 | -1122.01 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 522.79 | 522.85 | 6650.89 | -1120.66 | 501.61 | FULL
G4 | -540.64 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 523.21 | 523.25 | 6583.67 | -540.03 | 208 | FULL
G5 | 20.45 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 522.55 | 522.59 | 6594.07 | 21.67 | -72.56 | FULL
G6 | -820.72 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 523.09 | 523.08 | 6650.33 | -822.45 | 456.38 | FULL
G7 | -204.68 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 523.58 | 523.61 | 6580.98 | -203.67 | 140.2 | FULL
G8 | 330.34 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 522.81 | 522.86 | 6594.84 | 330.59 | -129.8 | FULL
G9 | -195.46 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 523.67 | 523.68 | 6652.59 | -194.58 | 310.67 | FULL
G10 | 407.73 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 524.1 | 524.03 | 6584.13 | 409.46 | 1.76 | FULL
G11 | 926.14 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 522.91 | 522.94 | 6602.42 | 926.29 | -270.86 | FULL
G12 | 336.66 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 524.05 | 524.07 | 6655.58 | 337.24 | 166.32 | FULL
G13 | 889.12 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 523.54 | 523.57 | 6590.54 | 890.7 | -119 | FULL
G14 | 1485.28 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 522.36 | 522.39 | 6610.98 | 1485.12 | -431.24 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -862.56 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 507.48 | 507.52 | 6320.21 | -862.74 | 336.04 | FULL
G1 | -285.46 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 507.71 | 507.74 | 6254.39 | -283.94 | 38.53 | FULL
G2 | 273.36 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 507.17 | 507.16 | 6268.49 | 274.92 | -247.86 | FULL
G3 | -637.69 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 507.9 | 508.01 | 6318.79 | -636.79 | 271.96 | FULL
G4 | -34.19 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 508.4 | 508.38 | 6249.15 | -32.96 | -33.32 | FULL
G5 | 504.74 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 507.36 | 507.44 | 6268.67 | 506.33 | -316.95 | FULL
G6 | -283.26 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 508.31 | 508.33 | 6318.26 | -282.26 | 190.87 | FULL
G7 | 295.82 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 508.34 | 508.37 | 6250.08 | 297.73 | -102.04 | FULL
G8 | 840.58 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 507.4 | 507.31 | 6270.21 | 842.26 | -391.42 | FULL
G9 | 317.38 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 508.82 | 508.73 | 6320.83 | 318.13 | 62.1 | FULL
G10 | 863.44 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 507.97 | 507.99 | 6257.17 | 863.7 | -219.72 | FULL
G11 | 1402.23 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 507.35 | 507.23 | 6278.4 | 1404.38 | -507.64 | FULL
G12 | 827.88 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 508.72 | 508.71 | 6327.6 | 829.57 | -76.56 | FULL
G13 | 1367.89 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 507.66 | 507.7 | 6265.12 | 1368.04 | -355.52 | FULL
G14 | 1951.13 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 507.74 | 507.79 | 6288.23 | 1951.16 | -660.94 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -363 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 495.61 | 495.63 | 6039.26 | -362.35 | 67.73 | FULL
G1 | 207.75 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 495.36 | 495.43 | 5970.89 | 208.49 | -219.84 | FULL
G2 | 744.07 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 494.5 | 494.52 | 5993.11 | 745.82 | -505.22 | FULL
G3 | -122.97 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 496.07 | 496.07 | 6035.09 | -121.73 | -0.2 | FULL
G4 | 435.54 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 495.52 | 495.44 | 5970.94 | 436.29 | -285.91 | FULL
G5 | 965.5 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 494.79 | 494.8 | 5993.65 | 964.11 | -566.17 | FULL
G6 | 216.77 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 496.42 | 496.42 | 6034.35 | 217.41 | -71.45 | FULL
G7 | 755.51 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 495.59 | 495.48 | 5972.56 | 754.75 | -348.5 | FULL
G8 | 1311.12 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 495.2 | 495.21 | 5995.99 | 1310.82 | -642.38 | FULL
G9 | 782.6 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 496.08 | 496.1 | 6041.64 | 783.27 | -188.57 | FULL
G10 | 1325.2 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 495.32 | 495.26 | 5980.82 | 1325.23 | -469.76 | FULL
G11 | 1873.37 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 495.03 | 495.06 | 6005.04 | 1874.09 | -760.2 | FULL
G12 | 1286.53 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 495.78 | 495.72 | 6049.69 | 1286.41 | -323.62 | FULL
G13 | 1844.68 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 495 | 495.02 | 5990.57 | 1844.83 | -622.91 | FULL
G14 | 2365.64 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 494.48 | 494.57 | 6016.01 | 2365.41 | -892.56 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1547.14 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 475.33 | 475.37 | 4986.65 | 1546.91 | -912.31 | FULL
G1 | 2103.15 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 475.09 | 475.06 | 4936.41 | 2104.73 | -1205.86 | FULL
G2 | 2582.73 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 474.24 | 474.31 | 4970.09 | 2582.35 | -1458.33 | FULL
G3 | 1772.31 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 474.55 | 474.65 | 4989.87 | 1772.22 | -971.67 | FULL
G4 | 2314.82 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 474.18 | 474.18 | 4940.78 | 2314.56 | -1253.64 | FULL
G5 | 2918.87 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.05 | -2410.86 | -2410.14 | 4974.75 | 2918.4 | -1588.47 | CTG_FAIL_IN_FULL
G6 | 2034.25 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 474.59 | 474.66 | 4992.2 | 2033.9 | -1014.03 | FULL
G7 | 2615.57 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 475.01 | 474.96 | 4942.72 | 2617.13 | -1318.42 | FULL
G8 | 2864.72 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.45 | -2240.71 | -2241.53 | 4966.16 | 2864.33 | -1435.12 | FULL
G9 | 2601.02 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 474.68 | 474.78 | 5003.39 | 2600.79 | -1132.05 | FULL
G10 | 3139.14 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 474.13 | 474.05 | 4955.83 | 3138.92 | -1421.18 | FULL
G11 | 3306.72 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3277.28 | 3275 | 4970.62 | 3306.31 | -1484.33 | FULL
G12 | 2046.16 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.55 | -425.42 | -425.35 | 4981.53 | 2046.15 | -651.36 | FULL
G13 | 1948.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.55 | -426.94 | -426.94 | 4911.06 | 1946.58 | -568.25 | FULL
G14 | 1796.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.55 | -421.7 | -421.62 | 4922.27 | 1796.6 | -445.31 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2003.65 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 459.39 | 459.43 | 4665.81 | 2004.48 | -1147.13 | FULL
G1 | 2435.92 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.45 | -2144.37 | -2145.85 | 4614.82 | 2433.74 | -1369.88 | FULL
G2 | 2439.67 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.45 | -2123.77 | -2124.78 | 4628.38 | 2440.39 | -1345.78 | FULL
G3 | 2219.03 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 459.48 | 459.58 | 4668.92 | 2218.46 | -1212.54 | FULL
G4 | 2546.01 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.45 | -2137.57 | -2139.14 | 4615.17 | 2545.71 | -1363.25 | FULL
G5 | 2564.84 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.45 | -2149.1 | -2150.82 | 4625.42 | 2565.44 | -1347.78 | FULL
G6 | 2536 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.18 | 459.29 | 459.38 | 4672.7 | 2535.69 | -1273.59 | FULL
G7 | 2744.19 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.45 | -2142.49 | -2143.12 | 4613.37 | 2741.73 | -1355.86 | FULL
G8 | 2785.14 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.45 | -2167.3 | -2166.07 | 4625.6 | 2782.68 | -1356.19 | FULL
G9 | 3038.02 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.45 | -2149.21 | -2147.75 | 4684.37 | 3035.43 | -1360.38 | FULL
G10 | 3058.44 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.45 | -2151.92 | -2150.5 | 4615.06 | 3058.02 | -1341.3 | FULL
G11 | 3078.02 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.45 | -2145.03 | -2143.52 | 4628.32 | 3075.84 | -1312.14 | FULL
G12 | 1811.73 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.55 | -424.84 | -424.78 | 4642.57 | 1811.19 | -487.05 | FULL
G13 | 1702.63 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.55 | -422.79 | -422.74 | 4573.01 | 1702.76 | -384.66 | FULL
G14 | 1596.7 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.55 | -422.05 | -422 | 4586.07 | 1596.89 | -291.58 | FULL
014WINTER09v1SNH