## Sheet1
calculates heat load into the pipe
units
|  | length of transfer line | 40 | meters
|  | OD of liquid supply pipe | 0.005 | m | 0.19685 | inches
|  | OD of vacuum jacket pipe | 0.075 | m | 2.9528 | inches
|  | surface area of OD vacuum jacket pipe | 9.4248 | m^2
|  | Surface area of OD transport/inner pipe | 0.62832 | m^2
|  | Room temperature | 293 | K
|  | surface of OD vacuum pipe temperature | 292.0456 | K | 19.0456 | deg C
|  | Surface of ID coolant line | 80.0673 | K
|  | coolant temperature | 80 | K
|  | heat transfer coef. OD of pipe to air | 5 | W/m^2/K
|  | K - conductivity of stainless steel | 14 | W/M/K
|  | e- emissivity of stainless steel (OD of the coolant pipe) without mylar | 0.15 | arb.
|  | e- emissivity of stainless steel (id of the vacuum jacket) | 0.15 | arb.
|  | e- emissivity of stainless steel (OD of the vacuum jacket) | 0.65 | arb.
|  | Fe-pg 386 | 0.14196
|  | stefan boltzman constant | 5.67e-08 | w/m/k/K^4
|  | vacuum pressure | 0.1 | Pa | 0.00075188 | torr | 1.4503e-05 | psi
|  | accommodation coeficent for air | 0.9
|  | accom. Factor Fa | 0.8996
|  | gas mean free path l=u/p *(piRT/2gc).5 | 0.066905 | meter | 2.6341 | inches | free molecular conduction occurs
|  | cp | 1006 | J/KG.K @200K
|  | R=Ru/M | 577.3847 | J/mol.K /kg/mol
|  | cv=3/2R | 866.0771 | J/KG.K
|  | g, specific heat ratio cp/cv | 1.1616
|  | G-gas conduction parameter=g+1/g-1*(gR/8piMT)^.5 | 3.3758 | M/sec.K
Calculate the cooling on the vacuum jacket due to radiation and "conduction" from the liquid pipe
radiation
|  | Q=Fe*A*s*(T^4-T^4) | 36.5819 | watts radiated off inner surface |  | Watt
conduction
|  | Q=G*p*A1*(dT) | 44.976 | watts conducted thru vacuum |  | Watt
|  | total lost | 81.5579 |  |  | Watt
Calculate the heating due to convection and radiation of the outer pipe
convection
|  | Q=h*A*(dT) | 44.976 | watts into the OD surface |  | Watt
radiation
|  | Q=e*A*s*(T^4-T^4) | 33.1931 | watts radiated into the vacuum
convection into the gas
|  | Q=h*A*(dT) | 44.976 | watts into the ID surface
|  | Total | 123.1451 |  |  | Watt
|  | Total normal Q;s no radiation | 44.976 | watts
Gas temp at inlet to tranfer line at edge of straw tubes Flow rate is divided by 7
units
|  | length of transfer line | 3 | meters
|  | OD of liquid supply pipe | 0.005 | m | 0.19685 | inches
|  | OD of vacuum jacket pipe | 0.012 | m | 0.47244 | inches
|  | surface area of OD vacuum jacket pipe | 0.1131 | m^2
|  | Surface area of OD transport/inner pipe | 0.047124 | m^2
|  | Room temperature | 293 | K
|  | surface of OD vacuum pipe temperature | 287.2196 | K | 14.2196 | deg C
|  | surface of ID transfer line | 80.6366 | K
|  | coolant temperature | 80 | K
|  | heat transfer coef. OD of pipe to air | 5 | W/m^2/K
|  | K - conductivity of stainless steel | 14 | W/M/K
|  | e- emissivity of stainless steel (OD of the coolant pipe) without mylar | 0.15 | arb.
|  | e- emissivity of stainless steel (id of the vacuum jacket) | 0.15 | arb.
|  | e- emissivity of stainless steel (OD of the vacuum jacket) | 0.65 | arb.
|  | Fe-pg 386 | 0.11077
|  | stefan boltzman constant | 5.67e-08 | w/m/k/K^4
|  | vacuum pressure | 0.1 | Pa | 0.00075188 | torr | 1.4503e-05
|  | accommodation coeficent for air | 0.9
|  | accom. Factor Fa | 0.88464
|  | gas mean free path l=u/p *(piRT/2gc).5 | 0.06635 | meter | 2.6122 | inches | free molecular conduction occurs
|  | cp | 1006 | J/KG.K @200K
|  | R=Ru/M | 577.3847 | J/mol.K /kg/mol
|  | cv=3/2R | 866.0771 | J/KG.K
|  | g, specific heat ratio cp/cv | 1.1616
|  | G-gas conduction parameter=g+1/g-1*(gR/8piMT)^.5 | 3.3474 | M/sec.K
Calculate the cooling on the vacuum jacket due to radiation and "conduction" from the liquid pipe
radiation
|  | Q=Fe*A*s*(T^4-T^4) | 2.0021 | watt lost |  | Watt
conduction
|  | Q=G*p*A1*(dT) | 3.2687 | watt lost |  | Watt
|  | total lost | 5.2708 |  |  | Watt
Calculate the heating due to convection and radiation of the outer pipe
convection
|  | Q=h*A*(dT) | 3.2687 | watt disappated |  | Watt
radiation
|  | Q=e*A*s*(T^4-T^4) | 2.3534 | watt disappated
|  | Q=h*A*(dT) | 3.2687
|  | Total | 5.6221 |  |  | Watt
|  | total without radiation | 3.2687
Split each of the 7 lines 4 ways, one for each quadrant
split is foam insulated
|  | liquid temp | 80 | K
|  | inner foam wall | 84.1701 | K | -188.8299 | C
|  | outer foam wall | 283.9124 | K | 10.9124 | C
|  | ambient air | 293 | K
|  | inner diameter | 0.003 | meters | 0.11811 | inches
|  | outer diameter | 0.05 | meters | 1.9685 | inches
|  | wall | 0.0235 | meters | 0.9252 | inches
|  | inner surface area | 0.047124 | meters surface area
|  | outer wall surface area | 0.7854 | meters surface area
|  | length of pipes | 5 | meters
|  | h | 5 | w/m.K from ambient to foam
|  | K | 0.016 | w/m^2.K | foam conduction
|  | h guess | 181.6 | w/m.k | from pipe to the gas
|  |  | 35.6867 | watts | into foam
|  |  | 35.6867 |  | thru foam
|  |  | 35.6867 |  | into gas
Heat load due to silicon strips
|  |  | 40 | watts | electrical
Thermal heat load on the chamber
|  | inner chamber temperature | 263 | K | -10 | C
|  | inner foam wall | 266.9491 | K | -6.0509 | C
|  | outer foam wall | 289.4099 | K | 16.4099 | C
|  | ambient air | 293 | K
|  | surface of flat shell | 0.38485 | meters | 15.1514 | inches
|  | surface of round shell | 0.21991 | meters | 8.6579 | inches
|  | wall | 0.013 | meters | 0.51181 | inches
|  | inner surface area | 0.9896 | meters surface area
|  | h inside of chamber guess | 7 | w/m.K from ambient to foam
|  | K | 0.016 | w/m^2.K | foam conduction
|  | h outside of chamber guess | 7 | w/m.k | from pipe to the gas
|  | Q=hAdT | 27.3565 | watts | outside surface of chamber
|  | Q=KAdT/L | 27.3565 |  | thru foam
|  | Q=hAdT | 27.3565 |  | inside surface of chamber
|  | TOTAL SYSTEM HEAT LOAD | 1538.5814 | watts
BINGO
Head Pressure into dewar
| controls flow rate |  | 151690 | N/M^2 | 22 | psi
|  | flow rate | 5.8294e-06 | M^3/sec | Liquid flow rate…..
|  |  | 0.0058294 | lpsec
|  |  | 0.34976 | lpm
|  |  | 0.012352 | c.feet/minute
|  |  | 795.1 | KG/M^3 | fluid density | [6 empty] | Fit for the gas density of nitrogen
|  |  | 0.0046349 | Kg/sec | mass flow rate
[12 empty] | Temp | density
[12 empty] | K | kg/m^3
|  |  | 0.02 | dollars/liter cost | [7 empty] | 100 | 3.4388
|  |  | 0.00011659 | dollars/sec | [7 empty] | 150 | 2.2594
|  |  | 3676.6937 | dollars/year | [7 empty] | 200 | 1.6883
[12 empty] | 250 | 1.3488
|  | heat of vaporization | 188000 | J/Kg | [7 empty] | 300 | 1.1233
|  |  | 871.3657 | watts to vaporize all the liquid ?? | [7 empty] | 350 | 0.9625
|  | heat capacity of gas | 1043 | J/kg.K average heat capacity of the nitrogen gas
|  |  | 667.2157 | watts required to warmup the gas from 85K to 263 K (178 dT) | [5 empty] | temp of gas inside manifold
|  |  | 178 | delta T | [5 empty] | 471.4957 | watts inside the chambers
|  |  | 1.2897 | kg/m^3 density of nitroge gas inside the chamber | [5 empty] | 125.7858 | temp drop in the manifold (gas
|  |  | 0.0035939 | m^3/sec gas flow rate | [5 empty] | 137.2142 | Kelvin gas temp inside manifold
|  |  | 3.5939 | lpsec
|  |  | 215.632 | lpm
|  |  | 7.615 | c.feet/minute
|  | Total heat capacity of Nitrogen | 1538.5814 | watts | [7 empty] | 263 | 1.2897
minus10c=1539 watts=.349lpm = 215 lpm gas = 9.5 psi .007 inch hole at manifold
minus20C=1602 watts=.379 lpm liquid = 225 lpm gas = 12 psi .007 inch manifold hole
minus100c=2113 watts=.679 lpm liquid =274 lpm gas
FOOTNOTES
Calculating the heat transfer coeff from the pipe into the transfer gas
pressure drop from dewar to the 7 way split
Liquid Nitrogen @80K
|  | Row -coolant density | 795.1 | KG/M^3 | fluid density
|  | viscosity-coolant | 0.000141 | N*sec/m^2
|  | v-kinematic viscosity | 1.7734e-07 | m^2/sec | viscosity/density
|  | Heat capacity | 2063 | J/kg.K
|  | Thermal Conductivity | 0.1362 | w/m.K
|  | pr | 2.1357
|  | ID | 0.005 | m | 0.19685 | inches
|  | Flow | 5.8294e-06 | m^3/sec
|  | linear flow velocity | 0.29689 | m/sec
|  | renolds number=4Q/pi*v*D | 8370.7352 | unitless | turbulent
|  | friction factor | 0.03 | friction factor
|  | gh=f(L/D)(V^2/2) | 10.577 | m^2/sec^2
|  | length of pipe | 40 | m | 131.2336 | ft
|  | Pressure loss horizontal run | 8409.7854 | N/m^s | 1.2197 | PSI | 33.7611 | in h20 | 2.8134 | feet h20
due to friction
|  | Nu | 39.0572 | turbulent flow |  | 39.0572 | Turbulent flow
|  | h | 1063.919 | watts / M^2.K heat transfer coefficent
Calculating the heat transfer coeff from the pipe into the transfer gas
Liquid Nitrogen @80K
|  | Row -coolant density | 795.1 | KG/M^3 | fluid density
|  | viscosity-coolant | 0.000141 | N*sec/m^2
|  | v-kinematic viscosity | 1.7734e-07 | m^2/sec | viscosity/density
|  | Heat capacity | 2063 | J/kg.K
|  | Thermal Conductivity | 0.1362 | w/m.K
|  | pr | 2.1357
|  | ID | 0.005 | m | 0.19685 | inches
|  | Flow | 8.3277e-07 | m^3/sec
|  | linear flow velocity | 0.042412 | m/sec
|  | renolds number=4Q/pi*v*D | 1195.8193 | unitless | laminar
|  | friction factor | 0.05352 | friction factor
|  | gh=f(L/D)(V^2/2) | 0.028882 | m^2/sec^2
|  | length of pipe | 3 | m | 9.8425 | ft
|  | Pressure loss horizontal run | 22.9638 | N/m^s | 0.0033305 | PSI | 0.092188 | in h20 | 0.0076823 | feet h20
due to friction
|  | Nu | 4 | laminar |  |  | 1.6623 | nu-low R turbulent
|  | h | 108.96 | watts / M^2.K heat transfer coefficent
|  | h=4k/D | 108.96 | laminar flow
Calculating the heat transfer coeff from the pipe into the transfer gas -4by transfer line - foam jacketed
Liquid Nitrogen @80K
|  | Row -coolant density | 795.1 | KG/M^3 | fluid density
|  | viscosity-coolant | 0.000141 | N*sec/m^2
|  | v-kinematic viscosity | 1.7734e-07 | m^2/sec | viscosity/density
|  | Heat capacity | 2063 | J/kg.K
|  | Thermal Conductivity | 0.1362 | w/m.K
|  | pr | 2.1357
|  | ID | 0.003 | m | 0.11811 | inches
|  | Flow | 2.0819e-07 | m^3/sec
|  | linear flow velocity | 0.029453 | m/sec
|  | renolds number=4Q/pi*v*D | 498.258 | unitless | laminar
|  | friction factor | 0.12845 | friction factor
|  | gh=f(L/D)(V^2/2) | 0.092855 | m^2/sec^2
|  | length of pipe | 5 | m | 16.4042 | ft
|  | Pressure loss horizontal run | 73.829 | N/m^s | 0.010708 | PSI | 0.29639 | in h20 | 0.024699 | feet h20
due to friction
|  | Nu | 4 | laminar |  |  | -8.3593 | nu-low R turbulent
|  | h | 181.6 | watts / M^2.K heat transfer coefficent
|  | h=4k/D | 181.6 | laminar flow
Calculating the heat transfer coeff from the pipe into the transfer gas -4by transfer line - foam jacketed
DOUBLE CHECKING TO SEE IF THE GAS TERMS SHOULD BE USED INSTEAD OF LIQUID
gas Nitrogen @100K
|  | Row -coolant density | 3.431 | KG/M^3 | fluid density
|  | viscosity-coolant | 6.88e-06 | N*sec/m^2
|  | v-kinematic viscosity | 2.0052e-06 | m^2/sec | viscosity/density
|  | Heat capacity | 1070 | J/kg.K
|  | Thermal Conductivity | 0.00958 | w/m.K
|  | pr | 0.76843
|  | ID | 0.003 | m | 0.11811 | inches
|  | Flow | 0.00012835 | m^3/sec
|  | linear flow velocity | 18.1581 | m/sec
|  | renolds number=4Q/pi*v*D | 27166.3544 | unitless | turbulent
|  | friction factor | 0.025 | friction factor
|  | gh=f(L/D)(V^2/2) | 6869.1316 | m^2/sec^2
|  | length of pipe | 5 | m | 16.4042 | ft
|  | Pressure loss horizontal run | 23568.3319 | N/m^s | 3.4182 | PSI | 94.6151 | in h20 | 7.8846 | feet h20
due to friction
|  | Nu | 4 | laminar |  |  | 70.9381 | nu-low R turbulent
|  | h | 226.5289 | watts / M^2.K heat transfer coefficent
|  | h=4k/D | 12.7733 | laminar flow
outgassing rates for kynar - assume material is moisture
|  | surface area | 0.16022 | m^2
|  |  | 1602.2123 | cm^2
|  |  | 11215.4858 | time 7 lines
|  | outgassing rate | 1.3e-10 | g/cm^2.sec
|  |  | 1.458e-06 | g/sec
|  |  | 18 | g/mole
|  |  | 22.4 | l/mol
|  |  | 1.8144e-06 | liters/sec
MANIFOLD PRESSURE DROPS BASED ON WARM NITROGEN GAS FLOW
Density of nitrogen gas at
|  |  | 137.2142 | Kelvin | -135.7858 | Celsius
|  |  | 2.4903 | Kg/M^3
|  | manifold diameter | 0.006 | M | 0.23622 | inches
|  | flow rate thru 1 orifice | 3.5653e-06 | M^3/sec |  |  | 0.0035653 | lpsec | 0.21392 | liters/min
|  | orifice diameter | 0.00018 | M | 0.0070866 | inches |  |  | 12.8352 | liters per hour
[9 empty] | 0.0075545 | cfm
[9 empty] | 0.45327 | scfh
Throat Velocity
|  | 4*Q/PI*Dt^2 | 140.1092 | m/sec
|  | B ratio - Dt/Dnom | 0.03
|  | K | 2.7 | table 7.31 page 530 , fluid mechanics
|  | pressure drop | 65995.4886 | N/m^s | 9.5715 | PSI