## MADC Assigns
COMPENDIUM of ANALOG MONITOR CHANNELS for NuMI | [12 empty] | 2005-08-10
# 65 | MADC ASSIGNMENTS FOR NuMI MI-60 South, MADC #65, Crate $63 N23, Rack MI60124
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #65, Crate $63 N23, Rack MI60124 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 | x |  | JBE | SAT4 | I:LM701 | P1 LINE BLM @Q701 | 0 | x |  | JBE | I:LM701 | P1 LINE BLM @Q701
| 1 | x |  | JBE | SAT4 | I:LM702 | P1 LINE BLM @Q702 | 1 | x |  | JBE | I:LM702 | P1 LINE BLM @Q702
| 2 | x |  | JBE | SAT4 | I:LM703 | P1 LINE BLM @Q703 | 2 | x |  | JBE | I:LM703 | P1 LINE BLM @Q703
| 3 | x |  | JBE | SAT4 | I:LM707 | P1 LINE BLM @Q707 | 3 | x |  | JBE | I:LM707 | P1 LINE BLM @Q707
| 4 | x |  | JBE | SAT4 | I:LM708 | P1 LINE BLM @Q708 | 4 | x |  | JBE | I:LM708 | P1 LINE BLM @Q708
| 5 | x |  | BE | SAT5 | I:KPS6NF | NuMI Extr Kicker Ref | 5 | x |  | BE | I:KPS6NF | NuMI Extr Kicker Ref
| 6 | x |  | JBE | SAT4 | I:BNKG | Beam in NuMI Kicker Gap | 6 | x |  | JBE | I:BNKG | Beam in NuMI Kicker Gap
| 7 | x | [5 empty] | 7 | x
| 8 | x | [5 empty] | 8 | x
| 9 | x | [5 empty] | 9 | x
| 10 | x | [5 empty] | 10 | x
| 11 | x | [5 empty] | 11 | x
| 12 |  | x | BE | SAT5 | I:KPS6NE | NuMI Extr Kickr Bufr Ref | 12 |  | x | BE | I:KPS6NE | NuMI Extr Kickr Bufr Ref
| 13 |  | x | BE | SAT2 | I:KPS6N | NuMI Extr Kickr Voltage | 13 |  | x | BE | I:KPS6N | NuMI Extr Kickr Voltage
| 14 |  | x | AE | SAT3 | I:KPS6NI | NuMI Extr Kickr Smpld I | 14 |  | x | AE | I:KPS6NI | NuMI Extr Kickr Smpld I
| 15 |  | x | C | SAT1 | I:K6FTR | Flourinert Temp Ref | 15 |  | x | C | I:K6FTR | Flourinert Temp Ref
| 16 |  | x | C | SAT1 | I:K6FTE | Flourinert Temp Error | 16 |  | x | C | I:K6FTE | Flourinert Temp Error
| 17 |  | x |  |  | I:K6FT1 | Heat Exchngr Output Temp | 17 |  | x |  | I:K6FT1 | Heat Exchngr Output Temp
| 18 |  | x | C | SAT1 | I:K6FT2 | Filter/Return Temperature | 18 |  | x | C | I:K6FT2 | Filter/Return Temperature
| 19 |  | x |  |  | I:K6FLT1 | KMagnet B Load Temp | 19 |  | x |  | I:K6FLT1 | KMagnet B Load Temp
| 20 |  | x |  |  | I:K6FLT2 | KMagnet B Load Temp | 20 |  | x |  | I:K6FLT2 | KMagnet B Load Temp
| 21 |  | x |  |  | I:K6FLT3 | KMagnet C Load Temp | 21 |  | x |  | I:K6FLT3 | KMagnet C Load Temp
| 22 |  | x |  |  | I:K6FLT4 | KMagnet C Load Temp | 22 |  | x |  | I:K6FLT4 | KMagnet C Load Temp
| 23 |  | x |  |  | I:K6FLOW | Pump Flow Rate | 23 |  | x |  | I:K6FLOW | Pump Flow Rate
| 24 |  | x |  |  | I:K6PRES | Pump Output Pressure | 24 |  | x |  | I:K6PRES | Pump Output Pressure
| 25 |  | x |  |  | I:K6CWP1 | UpStr Chilled Water Pres | 25 |  | x |  | I:K6CWP1 | UpStr Chilled Water Pres
| 26 |  | x |  |  | I:K6CWP2 | DnStr Chilled Water Pres | 26 |  | x |  | I:K6CWP2 | DnStr Chilled Water Pres
| 27 |  | x |  |  |  |  | 27 |  | x
| 28 |  | x |  |  |  |  | 28 |  | x
| 29 |  | x |  |  | I:TT602D | Quad 602 Tunnel Temp Int | 29 |  | x
| 30 |  | x |  |  |  |  | 30 |  | x
| 31 |  | x |  |  |  |  | 31 |  | x
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 65 | MADC ASSIGNMENTS FOR NuMI MI-60 South, MADC #65, Crate $63 N23, Rack MI60124
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #65, Crate $63 N23, Rack MI60124 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 | x |  |  |  | I:K6ATL | KM602A Body Temperature | 32 | x |  |  | I:K6ATL | KM602A Body Temperature
| 33 | x |  |  |  | I:K6BTL | KM602B Body Temperature | 33 | x |  |  | I:K6BTL | KM602B Body Temperature
| 34 | x |  |  |  | I:K6CTL | KM602C Body Temperature | 34 | x |  |  | I:K6CTL | KM602C Body Temperature
| 35 | x | [5 empty] | 35 | x
| 36 | x | [5 empty] | 36 | x
| 37 | x | [5 empty] | 37 | x
| 38 | x | [5 empty] | 38 | x
| 39 | x | [5 empty] | 39 | x
| 40 | x | [5 empty] | 40 | x
| 41 | x | [5 empty] | 41 | x
| 42 | x | [5 empty] | 42 | x
| 43 | x | [5 empty] | 43 | x
| 44 | x | [5 empty] | 44 | x
| 45 | x | [5 empty] | 45 | x
| 46 | x | [5 empty] | 46 | x
| 47 | x | [5 empty] | 47 | x
| 48 | x |  |  |  | I:TT601 | MI TUNNEL TEMP Q601 | 48 | x
| 49 | x |  |  |  | I:TH601 | MI TUNNEL HUMIDITY Q601 | 49 | x
| 50 | x | [5 empty] | 50 | x
| 51 | x | [5 empty] | 51 | x
| 52 | x | [5 empty] | 52 | x
| 53 | x |  |  |  | I:ERT60C | MI-60 CONTRL RM TEMP | 53 | x
| 54 | x |  |  |  | I:ERH60C | MI-60 CONTRL RM HUMIDITY | 54 | x
| 55 | x |  |  |  | I:ERT60S | MI-60 SE EQUIP RM TEMP | 55 | x
| 56 | x |  |  |  | I:ERH60S | MI-60 SE EQUIP RM HUMID | 56 | x
| 57 | x | [5 empty] | 57 | x
| 58 | x |  |  |  | I:TOR714 | P1 DNSTREAM INT | 58 | x
| 59 | x |  |  |  | I:TR714S | P1 DS INT X100 FOR PBARS | 59 | x
| 60 | x |  |  |  | I:61AIRP | MI VAC AIR PRES AT MI60S | 60 | x
| 61 | x |  |  |  | I:PRT60S | South PS Room Temp | 61 | x |  |  | I:PRT60S | South PS Room Temp
| 62 | x |  |  |  | I:PRH60S | South PS Room Humidty | 62 | x |  |  | I:PRH60S | South PS Room Humidty
| 63 | x |  |  |  | I:K6PFNT | NuMI Kicker PFN Temp | 63 | x |  |  | I:K6PFNT | NuMI Kicker PFN Temp
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 44 | MADC ASSIGNMENTS FOR NuMI MI-60 North, MADC #44, Crate $70 N23, Rack MI60226
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #44, Crate $70 N23, Rack MI60226 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 | x |  | BP TST BJBE | SAT5 | I:HI608N | HInt for NuMI Orbit Verf | 0 | x |  | BP TST BJBE | I:HI608N | HInt for NuMI Orbit Verf
| 1 | x |  | BJBE | SAT5 | I:LMQ612 | MI Loss Mon at Q612 | 1 | x |  | BJBE | I:LMQ612 | MI Loss Mon at Q612
| 2 | x |  | C | SAT1 | I:CPS6NV | Trim Elem PS Bulk Volts | 2 | x |  | C | I:CPS6NV | Trim Elem PS Bulk Volts
| 3 | x |  | C | SAT1 | E:LMHV1O | Reg Loss Mon Ch#1 HV Out | 3 | x |  | C | E:LMHV1O | Reg Loss Mon Ch#1 HV Out
| 4 | x |  | C | SAT1 | E:LMHV1R | Reg Loss Mon Ch#1 HV Ret | 4 | x |  | C | E:LMHV1R | Reg Loss Mon Ch#1 HV Ret
| 5 | x |  | AE | SAT3 | I:LMNKMA | Loss Monitor #1 at KM602A | 5 | x |  | AE | I:LMNKMA | Loss Monitor #1 at KM602A
| 6 | x |  | AE | SAT3 | I:LMNKMB | Loss Monitor #2 at KM602B | 6 | x |  | AE | I:LMNKMB | Loss Monitor #2 at KM602B
| 7 | x |  | AE | SAT3 | I:LMNKMC | Loss Monitor #3 at KM602C | 7 | x |  | AE | I:LMNKMC | Loss Monitor #3 at KM602C
| 8 | x |  | AE | SAT3 | I:LML60 | Loss Monitor #4 at LAM60 | 8 | x |  | AE | I:LML60 | Loss Monitor #4 at LAM60
| 9 | x |  | AE | SAT3 | I:LML61A | Loss Monitor #5 at LAM61A | 9 | x |  | AE | I:LML61A | Loss Monitor #5 at LAM61A
| 10 | x |  | AE | SAT3 | I:LML61B | Loss Monitor #6 at LAM61B | 10 | x |  | AE | I:LML61B | Loss Monitor #6 at LAM61B
| 11 | x |  | AE | SAT3 | E:LMV100 | Loss Monitor #7 at V100 | 11 | x |  | AE | E:LMV100 | Loss Monitor #7 at V100
| 12 | x |  | AE | SAT3 | E:LMQ101 | Loss Monitor #8 at Q101 | 12 | x |  | AE | E:LMQ101 | Loss Monitor #8 at Q101
| 13 | x |  | AE | SAT3 | E:LM1011 | Loss Monitor #9 at HV101-1 | 13 | x |  | AE | E:LM1011 | Loss Monitor #9 at HV101-1
| 14 | x |  | AE | SAT3 | E:LM1012 | Loss Monitor #10 at HV101-2 | 14 | x |  | AE | E:LM1012 | Loss Monitor #10 at HV101-2
| 15 | x |  | AE | SAT3 | E:LMQ102 | Loss Monitor #11 at Q102 | 15 | x |  | AE | E:LMQ102 | Loss Monitor #11 at Q102
| 16 | x |  | C | SAT1 | E:LMHV2O | Reg Loss Mon Ch#2 HV Out | 16 | x |  | C | E:LMHV2O | Reg Loss Mon Ch#2 HV Out
| 17 | x |  | C | SAT1 | E:LMHV2R | Reg Loss Mon Ch#2 HV Ret | 17 | x |  | C | E:LMHV2R | Reg Loss Mon Ch#2 HV Ret
| 18 | x |  | AE | SAT3 | E:LM1013 | Loss Monitor #1 at HV101-3 | 18 | x |  | AE | E:LM1013 | Loss Monitor #1 at HV101-3
| 19 | x |  | AE | SAT3 | E:LM1014 | Loss Monitor #2 at HV101-4 | 19 | x |  | AE | E:LM1014 | Loss Monitor #2 at HV101-4
| 20 | x |  | AE | SAT3 | E:LM1015 | Loss Monitor #3 at HV101-5 | 20 | x |  | AE | E:LM1015 | Loss Monitor #3 at HV101-5
| 21 | x |  | AE | SAT3 | E:LMQ103 | Loss Monitor #4 at Q103 | 21 | x |  | AE | E:LMQ103 | Loss Monitor #4 at Q103
| 22 | x |  | AE | SAT3 | E:LM1016 | Loss Monitor #5 at HV101-6 | 22 | x |  | AE | E:LM1016 | Loss Monitor #5 at HV101-6
| 23 | x |  | AE | SAT3 | E:LMQ104 | Loss Monitor #6 at Q104 | 23 | x |  | AE | E:LMQ104 | Loss Monitor #6 at Q104
| 24 | x |  | AE | SAT3 | E:LMHT04 | Loss Monitor #7 at HT104 | 24 | x |  | AE | E:LMHT04 | Loss Monitor #7 at HT104
| 25 | x |  | AE | SAT3 | E:LMQ105 | Loss Monitor #8 at Q105 | 25 | x |  | AE | E:LMQ105 | Loss Monitor #8 at Q105
| 26 | x |  | AE | SAT3 | E:LMQ106 | Loss Monitor #9 at Q106 | 26 | x |  | AE | E:LMQ106 | Loss Monitor #9 at Q106
| 27 | x |  | AE | SAT3 | E:LMQ107 | Loss Monitor #10 at Q107 | 27 | x |  | AE | E:LMQ107 | Loss Monitor #10 at Q107
| 28 | x |  | C | SAT1 | I:LMHV6O | MIQ Loss Mon Ch#6 HV Out | 28 | x |  | C | I:LMHV6O | MIQ Loss Mon Ch#6 HV Out
| 29 | x |  | C | SAT1 | I:LMHV6R | MIQ Loss Mon Ch#6 HV Ret | 29 | x |  | C | I:LMHV6R | MIQ Loss Mon Ch#6 HV Ret
| 30 | x |  |  |  | R:H602F | H602 Reference | 30 | x
| 31 | x |  |  |  | R:H606F | H606 Reference | 31 | x
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 44 | MADC ASSIGNMENTS FOR NuMI MI-60 North, MADC #44, Crate $70 N23, Rack MI60226
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #44, Crate $70 N23, Rack MI60226 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 | x |  |  |  | E:NTMP1 | NuMI Temp DS V100 | 32 | x |  |  | E:NTMP1 | NuMI Temp DS V100
| 33 | x |  |  |  | E:NTMP2 | NuMI Temp Mid EPB-1 | 33 | x |  |  | E:NTMP2 | NuMI Temp Mid EPB-1
| 34 | x |  |  |  | E:NTMP3 | NuMI Temp US Q102 High | 34 | x |  |  | E:NTMP3 | NuMI Temp US Q102 High
| 35 | x |  |  |  | E:NTMP4 | NuMI Temp US Q102 Low | 35 | x |  |  | E:NTMP4 | NuMI Temp US Q102 Low
| 36 | x |  |  |  | E:NTMP5 | NuMI Temp DS EPB-4 | 36 | x |  |  | E:NTMP5 | NuMI Temp DS EPB-4
| 37 | x |  |  |  | E:NTMP6 | NuMI Temp Mid EPB-5 | 37 | x |  |  | E:NTMP6 | NuMI Temp Mid EPB-5
| 38 | x |  |  |  | E:NTMP7 | NuMI Temp US Q103 High | 38 | x |  |  | E:NTMP7 | NuMI Temp US Q103 High
| 39 | x |  |  |  | E:NTMP8 | NuMI Temp US Q103 Low | 39 | x |  |  | E:NTMP8 | NuMI Temp US Q103 Low
| 40 | x |  |  |  | E:NTMP9 | NuMI Temp US Q104 High | 40 | x |  |  | E:NTMP9 | NuMI Temp US Q104 High
| 41 | x |  |  |  | E:PM101V | PM101 Clearing Voltage | 41 | x |  |  | E:PM101V | PM101 Clearing Voltage
| 42 | x |  |  |  | E:PM105V | PM105 Clearing Voltage | 42 | x |  |  | E:PM105V | PM105 Clearing Voltage
| 43 | x |  |  |  | E:PM107V | PM107 Clearing Voltage | 43 | x |  |  | E:PM107V | PM107 Clearing Voltage
| 44 | x |  |  |  | E:PM108V | PM108 Clearing Voltage | 44 | x |  |  | E:PM108V | PM108 Clearing Voltage
| 45 | x |  |  |  | E:PM112V | PM112 Clearing Voltage | 45 | x |  |  | E:PM112V | PM112 Clearing Voltage
| 46 | x |  | BJBE | SAT5 | I:LMQ608 | MI Loss Mon at Q608 | 46 | x |  | BJBE | I:LMQ608 | MI Loss Mon at Q608
| 47 | x |  | AE | SAT3 | E:TOR101 | NuMI UpStrm Intn at Q101 | 47 | x |  | AE | E:TOR101 | NuMI UpStrm Intn at Q101
| 48 |  | x |  |  | R:H602T | H602 F(t) Table | 48 |  | x
| 49 |  | x |  |  | R:V603T | V603 F(t) Table | 49 |  | x
| 50 |  | x |  |  | R:H604T | H604 F(t) Table | 50 |  | x
| 51 |  | x |  |  | R:V605T | V605 F(t) Table | 51 |  | x
| 52 |  | x |  |  | R:H606T | H606 F(t) Table | 52 |  | x
| 53 |  | x |  |  | R:V607T | V607 F(t) Table | 53 |  | x
| 54 |  | x | BJBE | SAT5 | I:HP606N | HPos for NuMI Orbit Verf | 54 |  | x | BJBE | I:HP606N | HPos for NuMI Orbit Verf
| 55 |  | x | BJBE | SAT5 | I:VP607N | VPos for NuMI Orbit Verf | 55 |  | x | BJBE | I:VP607N | VPos for NuMI Orbit Verf
| 56 |  | x | BJBE | SAT5 | I:HP608N | HPos for NuMI Orbit Verf | 56 |  | x | BJBE | I:HP608N | HPos for NuMI Orbit Verf
| 57 |  | x | BJBE | SAT5 | I:VP609N | VPos for NuMI Orbit Verf | 57 |  | x | BJBE | I:VP609N | VPos for NuMI Orbit Verf
| 58 |  | x |  |  | R:H608T | H608 F(t) Table | 58 |  | x
| 59 |  | x |  |  | I:HI606N | HInt for NuMI Orbit Verf | 59 |  | x |  | I:HI606N | HInt for NuMI Orbit Verf
| 60 |  | x | JBE | SAT4 | I:VI607N | VInt for NuMI Orbit Verf | 60 |  | x | JBE | I:VI607N | VInt for NuMI Orbit Verf
| 61 |  | x |  |  |  |  | 61 |  | x
| 62 |  | x |  |  | I:VI609N | VInt for NuMI Orbit Verf | 62 |  | x |  | I:VI609N | VInt for NuMI Orbit Verf
| 63 |  | x |  |  |  |  | 63 |  | x
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 38 | MADC ASSIGNMENTS FOR NuMI MI-60 North, MADC #38, Crate $73 N23, Rack MI60219
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #38, Crate $73 N23, Rack MI60219 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 |  | x | BE | SAT2 | I:LAM60F | LAM60 Reference | 0 |  | x | BE | I:LAM60F | LAM60 Reference
| 1 |  | x | BE | SAT2 | I:LAM60 | LAM60 Current | 1 |  | x | BE | I:LAM60 | LAM60 Current
| 2 |  | x | BE | SAT2 | I:LAM60E | LAM60 Current Error | 2 |  | x | BE | I:LAM60E | LAM60 Current Error
| 3 |  | x |  |  | I:LM60UU | LAM60 Unfltrd Volts Out | 3 |  | x |  | I:LM60UU | LAM60 Unfltrd Volts Out
| 4 |  | x |  |  | I:LAM60V | LAM60 Filterd Volts Out | 4 |  | x |  | I:LAM60V | LAM60 Filterd Volts Out
| 5 |  | x | BE | SAT2 | I:LAM61F | LAM61 Reference | 5 |  | x | BE | I:LAM61F | LAM61 Reference
| 6 |  | x | BE | SAT2 | I:LAM61 | LAM61 Current | 6 |  | x | BE | I:LAM61 | LAM61 Current
| 7 |  | x | BE | SAT2 | I:LAM61E | LAM61 Current Error | 7 |  | x | BE | I:LAM61E | LAM61 Current Error
| 8 |  | x |  |  | I:LAM61P | LAM61 Pos Volts to Gnd | 8 |  | x |  | I:LAM61P | LAM61 Pos Volts to Gnd
| 9 |  | x |  |  | I:LAM61N | LAM61 Neg Volts to Gnd | 9 |  | x |  | I:LAM61N | LAM61 Neg Volts to Gnd
| 10 |  | x |  |  | I:LAM61V | LAM61 Filterd Volts Out | 10 |  | x |  | I:LAM61V | LAM61 Filterd Volts Out
| 11 |  | x | BE | SAT2 | E:V100F | V100 C Mag Reference | 11 |  | x | BE | E:V100F | V100 C Mag Reference
| 12 |  | x | BE | SAT2 | E:V100 | V100 C Mag Current | 12 |  | x | BE | E:V100 | V100 C Mag Current
| 13 |  | x | BE | SAT2 | E:V100E | V100 Current Error | 13 |  | x | BE | E:V100E | V100 Current Error
| 14 |  | x |  |  | E:V100UU | V100 Unfltrd Volts Out | 14 |  | x |  | E:V100UU | V100 Unfltrd Volts Out
| 15 |  | x |  |  | E:V100V | V100 Filterd Volts Out | 15 |  | x |  | E:V100V | V100 Filterd Volts Out
| 16 |  | x |  |  | E:HV01AF | HV101A Reference | 16 |  | x |  | E:HV01AF | HV101A Reference
| 17 |  | x |  |  | E:HV01BF | HV101B Reference | 17 |  | x |  | E:HV01BF | HV101B Reference
| 18 |  | x |  |  |  |  | 18 |  | x
| 19 |  | x | BE | SAT2 | E:HV101 | HV101 EPB String Current | 19 |  | x | BE | E:HV101 | HV101 EPB String Current
| 20 |  | x | BE | SAT2 | E:HV101E | HV101 Current Error | 20 |  | x | BE | E:HV101E | HV101 Current Error
| 21 |  | x |  |  | E:HV101P | HV101 Pos Volts to Gnd | 21 |  | x |  | E:HV101P | HV101 Pos Volts to Gnd
| 22 |  | x |  |  | E:HV101N | HV101 Neg Volts to Gnd | 22 |  | x |  | E:HV101N | HV101 Neg Volts to Gnd
| 23 |  | x |  |  | E:HV101V | HV101 Filtered Voltage Out | 23 |  | x |  | E:HV101V | HV101 Filtered Voltage Out
| 24 |  | x |  |  | E:HV01AU | HV101A Unfltrd Volts Out | 24 |  | x |  | E:HV01AU | HV101A Unfltrd Volts Out
| 25 |  | x | BE | SAT2 | E:HV101F | HV101 Reference | 25 |  | x | BE | E:HV101F | HV101 Reference
| 26 |  | x |  |  |  |  | 26 |  | x
| 27 |  | x | BE | SAT2 | E:QD101F | QD101 Reference | 27 |  | x | BE | E:QD101F | QD101 Reference
| 28 |  | x | BE | SAT2 | E:QD101 | QD101 Current | 28 |  | x | BE | E:QD101 | QD101 Current
| 29 |  | x |  |  | E:QD101E | QD101 Current Error | 29 |  | x |  | E:QD101E | QD101 Current Error
| 30 |  | x |  |  | E:QD101V | QD101 Voltage | 30 |  | x |  | E:QD101V | QD101 Voltage
| 31 |  | x | BE | SAT2 | E:QF102F | QF102 Reference | 31 |  | x | BE | E:QF102F | QF102 Reference
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 38 | MADC ASSIGNMENTS FOR NuMI MI-60 North, MADC #38, Crate $73 N23, Rack MI60219
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #38, Crate $73 N23, Rack MI60219 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 |  | x | BE | SAT2 | E:QF102 | QF102 Current | 32 |  | x | BE | E:QF102 | QF102 Current
| 33 |  | x |  |  | E:QF102E | QF102 Current Error | 33 |  | x |  | E:QF102E | QF102 Current Error
| 34 |  | x |  |  | E:QF102V | QF102 Voltage | 34 |  | x |  | E:QF102V | QF102 Voltage
| 35 |  | x | BE | SAT2 | E:QD103F | QD103 Reference | 35 |  | x | BE | E:QD103F | QD103 Reference
| 36 |  | x | BE | SAT2 | E:QD103 | QD103 Current | 36 |  | x | BE | E:QD103 | QD103 Current
| 37 |  | x |  |  | E:QD103E | QD103 Current Error | 37 |  | x |  | E:QD103E | QD103 Current Error
| 38 |  | x |  |  | E:QD103V | QD103 Voltage | 38 |  | x |  | E:QD103V | QD103 Voltage
| 39 |  | x | BE | SAT2 | E:QF104F | QF104 Reference | 39 |  | x | BE | E:QF104F | QF104 Reference
| 40 |  | x | BE | SAT2 | E:QF104 | QF104 Current | 40 |  | x | BE | E:QF104 | QF104 Current
| 41 |  | x |  |  | E:QF104E | QF104 Current Error | 41 |  | x |  | E:QF104E | QF104 Current Error
| 42 |  | x |  |  | E:QF104V | QF104 Voltage | 42 |  | x |  | E:QF104V | QF104 Voltage
| 43 |  | x | BE | SAT2 | E:QF105F | QF105 Reference | 43 |  | x | BE | E:QF105F | QF105 Reference
| 44 |  | x | BE | SAT2 | E:QF105 | QF105 Current | 44 |  | x | BE | E:QF105 | QF105 Current
| 45 |  | x |  |  | E:QF105E | QF105 Current Error | 45 |  | x |  | E:QF105E | QF105 Current Error
| 46 |  | x |  |  | E:QF105V | QF105 Voltage | 46 |  | x |  | E:QF105V | QF105 Voltage
| 47 |  | x | BE | SAT2 | E:QD106F | QD106 Reference | 47 |  | x | BE | E:QD106F | QD106 Reference
| 48 |  | x | BE | SAT2 | E:QD106 | QD106 Current | 48 |  | x | BE | E:QD106 | QD106 Current
| 49 |  | x |  |  | E:QD106E | QD106 Current Error | 49 |  | x |  | E:QD106E | QD106 Current Error
| 50 |  | x |  |  | E:QD106V | QD106 Voltage | 50 |  | x |  | E:QD106V | QD106 Voltage
| 51 |  | x |  |  | E:H104F | H104 Trim Ref | 51 |  | x |  | E:H104F | H104 Trim Ref
| 52 |  | x |  |  | E:H104 | H104 Trim Current | 52 |  | x |  | E:H104 | H104 Trim Current
| 53 |  | x |  |  | E:H104E | H104 Trim Current Error | 53 |  | x |  | E:H104E | H104 Trim Current Error
| 54 |  | x |  |  | E:H104V | H104 Trim Voltage | 54 |  | x |  | E:H104V | H104 Trim Voltage
| 55 |  | x |  |  | E:100CUR | NuMI SAMPLED CURRENT | 55 |  | x
| 56 | x |  |  |  | I:TOR914 | A1 DNSTREAM INT | 56 | x |  |  | Above Highlighted Channels are Not Active. The Associated 20 kW PEI Supply is Now a Hot Spare. H104 is Now HT104 and is Wired Up as a Trim Element.
| 57 | x |  |  |  | E:100REF | NuMI SAMPLED REFERENCE | 57 | x
| 58 | x |  |  |  | R:CF60UV | ICF Volts US BPMs | 58 | x
| 59 | x |  |  |  | R:CF60C1 | ICF nAmps US BPMs A | 59 | x
| 60 | x |  |  |  | R:CF60C2 | ICF nAmps US BPMS B | 60 | x
| 61 | x |  |  |  | R:CF60DV | ICF Volts DS BPMs | 61 | x
| 62 | x |  |  |  | R:CF60C3 | ICF nAMPs DS BPMs A | 62 | x
| 63 | x |  |  |  | R:CF60C4 | ICF nAmps DS BPMs B | 63 | x
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 59 | MADC ASSIGNMENTS FOR NuMI MI-60 North, MADC #59, Crate $71 N23, Rack MI60204
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #59, Crate $71 N23, Rack MI60204 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 |  | x | Not Available |  | I:PS60LP | MI60 LOWR PS + V TO G | 0 |  | x | NA
| 1 |  | x | Not Available |  | I:PS60LN | MI60 LOWR PS - V TO G | 1 |  | x | NA
| 2 |  | x | Not Available |  | I:PS60LV | MI60 LOWR PS FILT V | 2 |  | x | NA
| 3 |  | x | Not Available |  | I:PS60LE | MI60 LOWR PS VOLT ERR | 3 |  | x | NA
| 4 |  | x | Not Available |  | I:PS60LF | MI60 LOWR PS VOLT REF | 4 |  | x | NA
| 5 |  | x | Not Available |  | I:PS60LU | MI60 LOWR PS UNFILT V | 5 |  | x | NA
| 6 |  | x | Not Available |  | I:PS60QP | MI60 QUAD PS + V TO G | 6 |  | x | NA
| 7 |  | x | Not Available |  | I:PS60QN | MI60 QUAD PS - V TO G | 7 |  | x | NA
| 8 |  | x | Not Available |  | I:PS60QV | MI60 QUD PS FILT V | 8 |  | x | NA
| 9 |  | x | Not Available |  | I:PS60QE | MI60 QUAD PS VOLT ERR | 9 |  | x | NA
| 10 |  | x | Not Available |  | I:PS60QF | MI60 QUAD PS VOLT REF | 10 |  | x | NA
| 11 |  | x | Not Available |  | I:PS60QU | MI60 QUAD PS UNFILT V | 11 |  | x | NA
| 12 |  | x | Not Available |  |  |  | 12 |  | x | NA
| 13 |  | x | Not Available |  | I:ILB | MI60 LOWER BEND I | 13 |  | x | NA
| 14 |  | x | Not Available |  | I:IQF | MI60 QF BUS I | 14 |  | x | NA
| 15 |  | x | Not Available |  | I:IQD | MI60 QD BUS I | 15 |  | x | NA
| 16 |  | x | Not Available |  | I:IQF-IB | MI60 QF-BEND DIFF I | 16 |  | x | NA
| 17 |  | x | Not Available |  | I:IQD-IB | MI60 QD-BEND DIFF I | 17 |  | x | NA
| 18 |  | x | Not Available |  | I:IBE | MI60 UPPR BEND I ERR | 18 |  | x | NA
| 19 |  | x | Not Available |  | I:ILBE | MI60 LOWR BEND I ERR | 19 |  | x | NA
| 20 |  | x | Not Available |  |  |  | 20 |  | x | NA
| 21 |  | x | Not Available |  |  |  | 21 |  | x | NA
| 22 |  | x | Not Available |  |  |  | 22 |  | x | NA
| 23 |  | x | Not Available |  |  |  | 23 |  | x | NA
| 24 |  | x | Not Available |  |  |  | 24 |  | x | NA
| 25 |  | x | Not Available |  |  |  | 25 |  | x | NA
| 26 |  | x | Not Available |  |  |  | 26 |  | x | NA
| 27 |  | x | Not Available |  |  |  | 27 |  | x | NA
| 28 |  | x | Not Available |  |  |  | 28 |  | x | NA
| 29 |  | x | Not Available |  |  |  | 29 |  | x | NA
| 30 |  | x | Not Available |  |  |  | 30 |  | x | NA
| 31 |  | x | Not Available |  |  |  | 31 |  | x | NA
# 59 | MADC ASSIGNMENTS FOR NuMI MI-60 North, MADC #59, Crate $71 N23, Rack MI60204
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #59, Crate $71 N23, Rack MI60204 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 | x |  | Not Available |  | I:LM910 | A1 LINE BLM @Q910 | 32 | x |  | NA
| 33 | x |  | Not Available |  | I:LM911 | A1 LINE BLM @Q911 | 33 | x |  | NA
| 34 | x |  | Not Available |  | I:LM912 | A1 LINE BLM @Q912 | 34 | x |  | NA
| 35 | x |  | Not Available |  | I:LM913 | A1 LINE BLM @Q913 | 35 | x |  | NA
| 36 | x |  | Not Available |  | I:LM914 | A1 LINE BLM @Q914 | 36 | x |  | NA
| 37 | x |  | Not Available |  | I:LMAC2U | A1 LINE BLM @C2 UPSTM | 37 | x |  | NA
| 38 | x |  | Not Available |  | I:LMAC2D | A1 LINE BLM @C2 DNSTM | 38 | x |  | NA
| 39 | x |  | Not Available |  | E:FLXH1 | Horiz Flux Mid HV101-1 | 39 | x |  | NA | E:FLXH1 | Horiz Flux Mid HV101-1
| 40 | x |  | Not Available |  | E:FLXV2 | Vert Flux Mid HV101-1 | 40 | x |  | NA | E:FLXV2 | Vert Flux Mid HV101-1
| 41 | x |  | Not Available |  | E:FLXH3 | Horiz Flux at DS HV101-1 | 41 | x |  | NA | E:FLXH3 | Horiz Flux at DS HV101-1
| 42 | x |  | Not Available |  | E:FLXV4 | Vert Flux DS HV101-1 | 42 | x |  | NA | E:FLXV4 | Vert Flux DS HV101-1
| 43 | x |  | Not Available |  | E:FLXH5 | Horiz Flux Mid HV101-6 | 43 | x |  | NA | E:FLXH5 | Horiz Flux Mid HV101-6
| 44 | x |  | Not Available |  | E:FLXV6 | Vert Flux Mid HV101-6 | 44 | x |  | NA | E:FLXV6 | Vert Flux Mid HV101-6
| 45 | x |  | Not Available |  | E:FLXH7 | Horiz Flux at DS HV101-6 | 45 | x |  | NA | E:FLXH7 | Horiz Flux at DS HV101-6
| 46 | x |  | Not Available |  | E:FLXV8 | Vert Flux DS HV101-6 | 46 | x |  | NA | E:FLXV8 | Vert Flux DS HV101-6
| 47 | x |  | Not Available |  | I:PS60QR | MI60 QUD PS FILT V 1hz | 47 | x |  | NA
| 48 | x |  | Not Available |  | I:TT609 | MI TUNNEL TEMP Q609 | 48 | x |  | NA
| 49 | x |  | Not Available |  | I:TH609 | MI TUNNEL HUMIDITY Q609 | 49 | x |  | NA
| 50 | x |  | Not Available |  | I:ERT60N | MI-60 NW EQUIP RM TEMP | 50 | x |  | NA
| 51 | x |  | Not Available |  | I:ERH60N | MI-60 NW EQUIP RM HUMID | 51 | x |  | NA
| 52 | x |  | Not Available |  |  |  | 52 | x |  | NA
| 53 | x |  | Not Available |  |  |  | 53 | x |  | NA
| 54 | x |  | Not Available |  | I:QXRCH0 | QXR DAC OUT CH0 | 54 | x |  | NA
| 55 | x |  | Not Available |  | I:QXRCH1 | QXR DAC OUT CH1 | 55 | x |  | NA
| 56 | x |  | Not Available |  | I:QXRCH2 | QXR DAC OUT CH2 | 56 | x |  | NA
| 57 | x |  | Not Available |  | I:QXRCH3 | QXR DAC OUT CH3 | 57 | x |  | NA
| 58 | x |  | Not Available |  | I:QXRCH4 | QXR DAC OUT CH4 | 58 | x |  | NA
| 59 | x |  | Not Available |  | I:QXRCH5 | QXR DAC OUT CH5 | 59 | x |  | NA
| 60 | x |  | Not Available |  | I:QXRCH6 | QXR DAC OUT CH6 | 60 | x |  | NA
| 61 | x |  | Not Available |  | I:QXRCH7 | QXR DAC OUT CH7 | 61 | x |  | NA
| 62 | x |  | Not Available |  | I:FFSPIL | BUCKER FEEDBACK | 62 | x |  | NA
| 63 | x |  | Not Available |  | I:MSPILL | QXR BUCKER MEMORY | 63 | x |  | NA
# 77 | MADC ASSIGNMENTS FOR NuMI MI-60 North, MADC #77, Crate $74 N21, Rack MI60205
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #77, Crate $74 N21, Rack MI60205 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 | Direct |  | Not Available |  | E:HT101F | HT101 Reference | 0 | Direct |  | NA | E:HT101F | HT101 Reference
| 1 | Direct |  | Not Available |  | E:HT101K | HT101 F(t) Table | 1 | Direct |  | NA | E:HT101K | HT101 F(t) Table
| 2 | Direct |  | Not Available |  | E:HT101V | HT101 Voltage Out | 2 | Direct |  | NA | E:HT101V | HT101 Voltage Out
| 3 | Direct |  | Not Available |  | E:HT101I | HT101 RMS Current | 3 | Direct |  | NA | E:HT101I | HT101 RMS Current
| 4 | Direct |  | Not Available |  | E:VT103F | VT103 Reference | 4 | Direct |  | NA | E:VT103F | VT103 Reference
| 5 | Direct |  | Not Available |  | E:VT103K | VT103 F(t) Table | 5 | Direct |  | NA | E:VT103K | VT103 F(t) Table
| 6 | Direct |  | Not Available |  | E:VT103V | VT103 Voltage Out | 6 | Direct |  | NA | E:VT103V | VT103 Voltage Out
| 7 | Direct |  | Not Available |  | E:VT103I | VT103 RMS Current | 7 | Direct |  | NA | E:VT103I | VT103 RMS Current
| 8 | Direct |  | Not Available |  | E:HT105F | HT105 Reference | 8 | Direct |  | NA | E:HT105F | HT105 Reference
| 9 | Direct |  | Not Available |  | E:HT105K | HT105 F(t) Table | 9 | Direct |  | NA | E:HT105K | HT105 F(t) Table
| 10 | Direct |  | Not Available |  | E:HT105V | HT105 Voltage Out | 10 | Direct |  | NA | E:HT105V | HT105 Voltage Out
| 11 | Direct |  | Not Available |  | E:HT105I | HT105 RMS Current | 11 | Direct |  | NA | E:HT105I | HT105 RMS Current
| 12 | Direct |  | Not Available |  | E:VT106F | VT106 Reference | 12 | Direct |  | NA | E:VT106F | VT106 Reference
| 13 | Direct |  | Not Available |  | E:VT106K | VT106 F(t) Table | 13 | Direct |  | NA | E:VT106K | VT106 F(t) Table
| 14 | Direct |  | Not Available |  | E:VT106V | VT106 Voltage Out | 14 | Direct |  | NA | E:VT106V | VT106 Voltage Out
| 15 | Direct |  | Not Available |  | E:VT106I | VT106 RMS Current | 15 | Direct |  | NA | E:VT106I | VT106 RMS Current
| 16 | Direct |  | Not Available |  | E:HT107F | HT107 Reference | 16 | Direct |  | NA | E:HT107F | HT107 Reference
| 17 | Direct |  | Not Available |  | E:HT107K | HT107 F(t) Table | 17 | Direct |  | NA | E:HT107K | HT107 F(t) Table
| 18 | Direct |  | Not Available |  | E:HT107V | HT107 Voltage Out | 18 | Direct |  | NA | E:HT107V | HT107 Voltage Out
| 19 | Direct |  | Not Available |  | E:HT107I | HT107 RMS Current | 19 | Direct |  | NA | E:HT107I | HT107 RMS Current
| 20 | Direct |  | Not Available |  | E:VT108F | VT108 Reference | 20 | Direct |  | NA | E:VT108F | VT108 Reference
| 21 | Direct |  | Not Available |  | E:VT108K | VT108 F(t) Table | 21 | Direct |  | NA | E:VT108K | VT108 F(t) Table
| 22 | Direct |  | Not Available |  | E:VT108V | VT108 Voltage Out | 22 | Direct |  | NA | E:VT108V | VT108 Voltage Out
| 23 | Direct |  | Not Available |  | E:VT108I | VT108 RMS Current | 23 | Direct |  | NA | E:VT108I | VT108 RMS Current
| 24 | Direct |  | Not Available |  | E:HT109F | HT109 Reference | 24 | Direct |  | NA | E:HT109F | HT109 Reference
| 25 | Direct |  | Not Available |  | E:HT109K | HT109 F(t) Table | 25 | Direct |  | NA | E:HT109K | HT109 F(t) Table
| 26 | Direct |  | Not Available |  | E:HT109V | HT109 Voltage Out | 26 | Direct |  | NA | E:HT109V | HT109 Voltage Out
| 27 | Direct |  | Not Available |  | E:HT109I | HT109 RMS Current | 27 | Direct |  | NA | E:HT109I | HT109 RMS Current
| 28 | Direct |  | Not Available |  | E:VT110F | VT110 Reference | 28 | Direct |  | NA | E:VT110F | VT110 Reference
| 29 | Direct |  | Not Available |  | E:VT110K | VT110 F(t) Table | 29 | Direct |  | NA | E:VT110K | VT110 F(t) Table
| 30 | Direct |  | Not Available |  | E:VT110V | VT110 Voltage Out | 30 | Direct |  | NA | E:VT110V | VT110 Voltage Out
| 31 | Direct |  | Not Available |  | E:VT110I | VT110 RMS Current | 31 | Direct |  | NA | E:VT110I | VT110 RMS Current
# 77 | MADC ASSIGNMENTS FOR NuMI MI-60 North, MADC #77, Crate $74 N21, Rack MI60205
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #77, Crate $74 N21, Rack MI60205 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 | Direct |  | Not Available |  | E:VT111F | VT111 Reference | 32 | Direct |  | NA | E:VT111F | VT111 Reference
| 33 | Direct |  | Not Available |  | E:VT111K | VT111 F(t) Table | 33 | Direct |  | NA | E:VT111K | VT111 F(t) Table
| 34 | Direct |  | Not Available |  | E:VT111V | VT111 Voltage Out | 34 | Direct |  | NA | E:VT111V | VT111 Voltage Out
| 35 | Direct |  | Not Available |  | E:VT111I | VT111 RMS Current | 35 | Direct |  | NA | E:VT111I | VT111 RMS Current
| 36 | Direct |  | Not Available |  | E:HT112F | HT112 Reference | 36 | Direct |  | NA | E:HT112F | HT112 Reference
| 37 | Direct |  | Not Available |  | E:HT112K | HT112 F(t) Table | 37 | Direct |  | NA | E:HT112K | HT112 F(t) Table
| 38 | Direct |  | Not Available |  | E:HT112V | HT112 Voltage Out | 38 | Direct |  | NA | E:HT112V | HT112 Voltage Out
| 39 | Direct |  | Not Available |  | E:HT112I | HT112 RMS Current | 39 | Direct |  | NA | E:HT112I | HT112 RMS Current
| 40 | Direct |  | Not Available |  | E:HT104F | HT104 Reference | 40 | Direct |  | NA | E:HT104F | HT104 Reference
| 41 | Direct |  | Not Available |  | E:HT104K | HT104 F(t) Table | 41 | Direct |  | NA | E:HT104K | HT104 F(t) Table
| 42 | Direct |  | Not Available |  | E:HT104V | HT104 Voltage Out | 42 | Direct |  | NA | E:HT104V | HT104 Voltage Out
| 43 | Direct |  | Not Available |  | E:HT104I | HT104 RMS Current | 43 | Direct |  | NA | E:HT104I | HT104 RMS Current
| 44 | Direct |  | Not Available |  |  |  | 44 |  |  | NA
| 45 | Direct |  | Not Available |  | E:CPS6N | Trim Elem PS Bulk I | 45 | Direct |  | NA | E:CPS6N | Trim Elem PS Bulk I
| 46 | Direct |  | Not Available |  | E:CPS6NI | Trim Elem PS Bulk RMS I | 46 | Direct |  | NA | E:CPS6NI | Trim Elem PS Bulk RMS I
| 47 | Direct |  | Not Available |  |  |  | 47 |  |  | NA
| 48 | Direct |  | Not Available |  | R:QCLF | QCL Reference | 48 |  |  | NA
| 49 | Direct |  | Not Available |  | R:QCLPF | Quad Corr Loop Calib PS | 49 |  |  | NA
| 50 | Direct |  | Not Available |  | R:QCLV | QCL Voltage | 50 |  |  | NA
| 51 | Direct |  | Not Available |  | R:QCLI | QCL RMS Current | 51 |  |  | NA
| 52 | Direct |  | Not Available |  | R:CPS6NV | R:CPS6N Voltage | 52 |  |  | NA
| 53 | Direct |  | Not Available |  | R:CPS6N | R:CPS6N Current | 53 |  |  | NA
| 54 | Direct |  | Not Available |  | R:CPS6NI | R:CPS6N RMS Current | 54 |  |  | NA
| 55 | Direct |  | Not Available |  |  |  | 55 |  |  | NA
| 56 | Direct |  | Not Available |  |  |  | 56 |  |  | NA
| 57 | Direct |  | Not Available |  |  |  | 57 |  |  | NA
| 58 | Direct |  | Not Available |  |  |  | 58 |  |  | NA
| 59 | Direct |  | Not Available |  |  |  | 59 |  |  | NA
| 60 | Direct |  | Not Available |  |  |  | 60 |  |  | NA
| 61 | Direct |  | Not Available |  |  |  | 61 |  |  | NA
| 62 | Direct |  | Not Available |  |  |  | 62 |  |  | NA
| 63 | Direct |  | Not Available |  |  |  | 63 |  |  | NA
# 79 | MADC ASSIGNMENTS FOR NuMI MI-62 Service Building, MADC #79, Crate $6C N23, Rack MI62107
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #79, Crate $6C N23, Rack MI62107 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 | x |  | C | SAT1 | E:LMHV3O | Reg Loss Mon Ch#3 HV Out | 0 | x |  | C | E:LMHV3O | Reg Loss Mon Ch#3 HV Out
| 1 | x |  | C | SAT1 | E:LMHV3R | Reg Loss Mon Ch#3 HV Ret | 1 | x |  | C | E:LMHV3R | Reg Loss Mon Ch#3 HV Ret
| 2 | x |  | AE | SAT3 | E:LMQ108 | Loss Monitor #1 at Q108 | 2 | x |  | AE | E:LMQ108 | Loss Monitor #1 at Q108
| 3 | x |  | AE | SAT3 | E:LM1081 | Loss Monitor #2 at V108-1 | 3 | x |  | AE | E:LM1081 | Loss Monitor #2 at V108-1
| 4 | x |  | AE | SAT3 | E:LM1082 | Loss Monitor #3 at V108-2 | 4 | x |  | AE | E:LM1082 | Loss Monitor #3 at V108-2
| 5 | x |  | AE | SAT3 | E:LMQ109 | Loss Monitor #4 at Q109 | 5 | x |  | AE | E:LMQ109 | Loss Monitor #4 at Q109
| 6 | x |  | AE | SAT3 | E:LM1083 | Loss Monitor #5 at V108-3 | 6 | x |  | AE | E:LM1083 | Loss Monitor #5 at V108-3
| 7 | x |  | AE | SAT3 | E:LM1084 | Loss Monitor #6 at V108-4 | 7 | x |  | AE | E:LM1084 | Loss Monitor #6 at V108-4
| 8 | x |  | AE | SAT3 | E:LMQ110 | Loss Monitor #7 at Q110 | 8 | x |  | AE | E:LMQ110 | Loss Monitor #7 at Q110
| 9 | x |  | AE | SAT3 | E:LM1085 | Loss Monitor #8 at V108-5 | 9 | x |  | AE | E:LM1085 | Loss Monitor #8 at V108-5
| 10 | x |  | AE | SAT3 | E:LM1086 | Loss Monitor #9 at V108-6 | 10 | x |  | AE | E:LM1086 | Loss Monitor #9 at V108-6
| 11 | x |  | AE | SAT3 | E:LMQ111 | Loss Monitor #10 at Q111 | 11 | x |  | AE | E:LMQ111 | Loss Monitor #10 at Q111
| 12 | x |  | AE | SAT3 | E:LMQ112 | Loss Monitor #11 at Q112 | 12 | x |  | AE | E:LMQ112 | Loss Monitor #11 at Q112
| 13 | x |  | AE | SAT3 | E:TLMNS | Total Loss Mon NuMI Stub | 13 | x |  | AE | E:TLMNS | Total Loss Mon NuMI Stub
| 14 | x |  | AE | SAT3 | E:TLMCTU | Total Loss Mon Upr Hobbt | 14 | x |  | AE | E:TLMCTU | Total Loss Mon Upr Hobbt
| 15 | x |  | AE | SAT3 | E:TLMCTD | Total Loss Mon Lwr Hobbt | 15 | x |  | AE | E:TLMCTD | Total Loss Mon Lwr Hobbt
| 16 | x |  | AE | SAT3 | E:TLMPT | Total Loss Mon Pre-Targt | 16 | x |  | AE | E:TLMPT | Total Loss Mon Pre-Targt
| 17 | x |  | C | SAT1 | E:TLMHVO | Total Loss Mon HV Out | 17 | x |  | C | E:TLMHVO | Total Loss Mon HV Out
| 18 | x |  | C | SAT1 | E:TLMHVR | Total Loss Mon HV Ret | 18 | x |  | C | E:TLMHVR | Total Loss Mon HV Ret
| 19 | x |  | AE | SAT3 | E:LMBBBP | LMon Begin Big Beam Pipe | 19 | x |  | AE | E:LMBBBP | LMon Begin Big Beam Pipe
| 20 | x | [5 empty] | 20 | x
| 21 | x | [5 empty] | 21 | x
| 22 | x | [5 empty] | 22 | x
| 23 | x | [5 empty] | 23 | x
| 24 | x | [5 empty] | 24 | x
| 25 | x | [5 empty] | 25 | x
| 26 | x | [5 empty] | 26 | x
| 27 |  | x |  |  |  |  | 27 |  | x
| 28 |  | x |  |  |  |  | 28 |  | x
| 29 |  | x |  |  |  |  | 29 |  | x
| 30 |  | x |  |  |  |  | 30 |  | x
| 31 |  | x |  |  |  |  | 31 |  | x
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 79 | MADC ASSIGNMENTS FOR NuMI MI-62 Service Building, MADC #79, Crate $6C N23, Rack MI62107
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #79, Crate $6C N23, Rack MI62107 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 |  | x | BE | SAT2 | E:V108F | V108 Reference | 32 |  | x | BE | E:V108F | V108 Reference
| 33 |  | x | BE | SAT2 | E:V108 | V108 B2 String Current | 33 |  | x | BE | E:V108 | V108 B2 String Current
| 34 |  | x | BE | SAT2 | E:V108E | V108 Current Error | 34 |  | x | BE | E:V108E | V108 Current Error
| 35 |  | x |  |  | E:V108UV | V108 Unfltred Volts Out | 35 |  | x |  | E:V108UV | V108 Unfltred Volts Out
| 36 |  | x |  |  | E:V108V | V108 Filtred Volts Out | 36 |  | x |  | E:V108V | V108 Filtred Volts Out
| 37 |  | x |  |  | E:V108P | V108 Pos Volts to Gnd | 37 |  | x |  | E:V108P | V108 Pos Volts to Gnd
| 38 |  | x |  |  | E:V108N | V108 Neg Volts to Gnd | 38 |  | x |  | E:V108N | V108 Neg Volts to Gnd
| 39 |  | x | BE | SAT2 | E:QF107F | QF107 Reference | 39 |  | x | BE | E:QF107F | QF107 Reference
| 40 |  | x | BE | SAT2 | E:QF107 | QF107 Current | 40 |  | x | BE | E:QF107 | QF107 Current
| 41 |  | x |  |  | E:QF107E | QF107 Current Error | 41 |  | x |  | E:QF107E | QF107 Current Error
| 42 |  | x |  |  | E:QF107V | QF107 Voltage | 42 |  | x |  | E:QF107V | QF107 Voltage
| 43 |  | x | BE | SAT2 | E:QD108F | QD108 Reference | 43 |  | x | BE | E:QD108F | QD108 Reference
| 44 |  | x | BE | SAT2 | E:QD108 | QD108 Current | 44 |  | x | BE | E:QD108 | QD108 Current
| 45 |  | x |  |  | E:QD108E | QD108 Current Error | 45 |  | x |  | E:QD108E | QD108 Current Error
| 46 |  | x |  |  | E:QD108V | QD108 Voltage | 46 |  | x |  | E:QD108V | QD108 Voltage
| 47 |  | x | BE | SAT2 | E:QF109F | QF109 Reference | 47 |  | x | BE | E:QF109F | QF109 Reference
| 48 |  | x | BE | SAT2 | E:QF109 | QF109 Current | 48 |  | x | BE | E:QF109 | QF109 Current
| 49 |  | x |  |  | E:QF109E | QF109 Current Error | 49 |  | x |  | E:QF109E | QF109 Current Error
| 50 |  | x |  |  | E:QF109V | QF109 Voltage | 50 |  | x |  | E:QF109V | QF109 Voltage
| 51 |  | x | BE | SAT2 | E:QD110F | QD110 Reference | 51 |  | x | BE | E:QD110F | QD110 Reference
| 52 |  | x | BE | SAT2 | E:QD110 | QD110 Current | 52 |  | x | BE | E:QD110 | QD110 Current
| 53 |  | x |  |  | E:QD110E | QD110 Current Error | 53 |  | x |  | E:QD110E | QD110 Current Error
| 54 |  | x |  |  | E:QD110V | QD110 Voltage | 54 |  | x |  | E:QD110V | QD110 Voltage
| 55 |  | x | BE | SAT2 | E:QD111F | QD111 Reference | 55 |  | x | BE | E:QD111F | QD111 Reference
| 56 |  | x | BE | SAT2 | E:QD111 | QD111 Current | 56 |  | x | BE | E:QD111 | QD111 Current
| 57 |  | x |  |  | E:QD111E | QD111 Current Error | 57 |  | x |  | E:QD111E | QD111 Current Error
| 58 |  | x |  |  | E:QD111V | QD111 Voltage | 58 |  | x |  | E:QD111V | QD111 Voltage
| 59 |  | x | BE | SAT2 | E:QF112F | QF112 Reference | 59 |  | x | BE | E:QF112F | QF112 Reference
| 60 |  | x | BE | SAT2 | E:QF112 | QF112 Current | 60 |  | x | BE | E:QF112 | QF112 Current
| 61 |  | x |  |  | E:QF112E | QF112 Current Error | 61 |  | x |  | E:QF112E | QF112 Current Error
| 62 |  | x |  |  | E:QF112V | QF112 Voltage | 62 |  | x |  | E:QF112V | QF112 Voltage
| 63 |  | x |  |  |  |  | 63 |  | x
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 67 | MADC ASSIGNMENTS FOR NuMI MI-62 Service Building, MADC #67, Crate $6B N23, Rack MI62106
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #67, Crate $6B N23, Rack MI62106 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 | x |  | Not Available |  | I:TT624 | MI TUNNEL TEMP Q624 | 0 | x |  | NA
| 1 | x |  | Not Available |  | I:TH624 | MI TUNNEL HUMIDITY Q624 | 1 | x |  | NA
| 2 | x |  | Not Available |  | I:KRT62 | MI-62 KICKR RM TEMP | 2 | x |  | NA
| 3 | x |  | Not Available |  | I:KRH62 | MI-62 KICKR RM HUMIDITY | 3 | x |  | NA
| 4 | x |  | Not Available |  |  |  | 4 | x |  | NA
| 5 | x |  | Not Available |  | I:TOR902 | A1 UPSTREAM INT | 5 | x |  | NA
| 6 | x |  | Not Available |  | E:TTNSTB | MI NuMI Stub Temp | 6 | x |  | NA | E:TTNSTB | MI NuMI Stub Temp
| 7 | x |  | Not Available |  | E:THNSTB | MI NuMI Stub Humidity | 7 | x |  | NA | E:THNSTB | MI NuMI Stub Humidity
| 8 | x |  | Not Available |  |  |  | 8 | x |  | NA
| 9 | x |  | Not Available |  |  |  | 9 | x |  | NA
| 10 | x |  | Not Available |  | R:V631F | V631 Reference | 10 | x |  | NA
| 11 | x |  | Not Available |  | R:V627F | V627 Reference | 11 | x |  | NA
| 12 | x |  | Not Available |  | R:V619F | V619 Reference | 12 | x |  | NA
| 13 | x |  | Not Available |  | R:H624F | H624 Reference | 13 | x |  | NA
| 14 | x |  | Not Available |  | R:H634F | H634 Reference | 14 | x |  | NA
| 15 | x |  | Not Available |  | R:H622F | H622 Reference | 15 | x |  | NA
| 16 |  | x | Not Available |  | R:H628T | H628 F(t) Table | 16 |  | x | NA
| 17 |  | x | Not Available |  | R:V629T | V629 F(t) Table | 17 |  | x | NA
| 18 |  | x | Not Available |  | R:H630T | H630 F(t) Table | 18 |  | x | NA
| 19 |  | x | Not Available |  | R:V631T | V631 F(t) Table | 19 |  | x | NA
| 20 |  | x | Not Available |  | R:V621T | V621 F(t) Table | 20 |  | x | NA
| 21 |  | x | Not Available |  | R:V623T | V623 F(t) Table | 21 |  | x | NA
| 22 |  | x | Not Available |  | R:V613T | V613 F(t) Table | 22 |  | x | NA
| 23 |  | x | Not Available |  | R:V615T | V615 F(t) Table | 23 |  | x | NA
| 24 |  | x | Not Available |  | R:V617T | V617 F(t) Table | 24 |  | x | NA
| 25 |  | x | Not Available |  | R:V619T | V619 F(t) Table | 25 |  | x | NA
| 26 |  | x | Not Available |  | R:V625T | V625 F(t) Table | 26 |  | x | NA
| 27 |  | x | Not Available |  | R:V627T | V627 F(t) Table | 27 |  | x | NA
| 28 |  | x | Not Available |  | R:V633T | V633 F(t) Table | 28 |  | x | NA
| 29 |  | x | Not Available |  | R:V635T | V635 F(t) Table | 29 |  | x | NA
| 30 |  | x | Not Available |  | R:H620T | H620 F(t) Table | 30 |  | x | NA
| 31 |  | x | Not Available |  | R:H624T | H624 F(t) Table | 31 |  | x | NA
# 67 | MADC ASSIGNMENTS FOR NuMI MI-62 Service Building, MADC #67, Crate $6B N23, Rack MI62106
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #67, Crate $6B N23, Rack MI62106 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 |  | x | Not Available |  | R:H632T | H632 F(t) Table | 32 |  | x | NA
| 33 |  | x | Not Available |  | R:S630T | S630 F(t) Table | 33 |  | x | NA
| 34 |  | x | Not Available |  | R:H614T | H614 F(t) Table | 34 |  | x | NA
| 35 |  | x | Not Available |  | R:H616T | H616 F(t) Table | 35 |  | x | NA
| 36 |  | x | Not Available |  | R:H618T | H618 F(t) Table | 36 |  | x | NA
| 37 |  | x | Not Available |  | R:H622T | H622 F(t) Table | 37 |  | x | NA
| 38 |  | x | Not Available |  | R:H626T | H626 F(t) Table | 38 |  | x | NA
| 39 |  | x | Not Available |  | R:H634T | H634 F(t) Table | 39 |  | x | NA
| 40 |  | x | Not Available |  |  |  | 40 |  | x | NA
| 41 |  | x | Not Available |  |  |  | 41 |  | x | NA
| 42 |  | x | Not Available |  |  |  | 42 |  | x | NA
| 43 |  | x | Not Available |  |  |  | 43 |  | x | NA
| 44 |  | x | Not Available |  |  |  | 44 |  | x | NA
| 45 |  | x | Not Available |  |  |  | 45 |  | x | NA
| 46 |  | x | Not Available |  |  |  | 46 |  | x | NA
| 47 |  | x | Not Available |  |  |  | 47 |  | x | NA
| 48 |  | x | Not Available |  |  |  | 48 |  | x | NA
| 49 |  | x | Not Available |  |  |  | 49 |  | x | NA
| 50 |  | x | Not Available |  |  |  | 50 |  | x | NA
| 51 |  | x | Not Available |  |  |  | 51 |  | x | NA
| 52 |  | x | Not Available |  |  |  | 52 |  | x | NA
| 53 |  | x | Not Available |  |  |  | 53 |  | x | NA
| 54 |  | x | Not Available |  |  |  | 54 |  | x | NA
| 55 |  | x | Not Available |  |  |  | 55 |  | x | NA
| 56 |  | x | Not Available |  | I:LAM62F | LAM62 467 Reference | 56 |  | x | NA
| 57 |  | x | Not Available |  | I:LAM62 | MI PBAR LAM PS @622 | 57 |  | x | NA
| 58 |  | x | Not Available |  | I:LAM62U | LAM62 Unfiltered Voltage | 58 |  | x | NA
| 59 |  | x | Not Available |  | I:LAM62E | LAM62 Current Error | 59 |  | x | NA
| 60 |  | x | Not Available |  | I:V901AU | V901A Unfiltered Voltage | 60 |  | x | NA
| 61 |  | x | Not Available |  | I:V901BU | V901B Unfiltered Voltage | 61 |  | x | NA
| 62 |  | x | Not Available |  | I:V901F | V901 467 Reference | 62 |  | x | NA
| 63 |  | x | Not Available |  | I:V901S | V901 467 Scale Fctr | 63 |  | x | NA
# 85 | MADC ASSIGNMENTS FOR NuMI MI-65 Service Building, MADC #85, Crate $E4 N23, Rack MI65103
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #85, Crate $E4 N23, Rack MI65103 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 |  | x | BP TST AE | SAT6 | E:HI121P | Horz Inten for BPS Check | 0 |  | x | BP TST AE | E:HI121P | Horz Inten for BPS Check
| 1 |  | x |  |  | E:V118BF | V118B Reference | 1 |  | x |  | E:V118BF | V118B Reference
| 2 |  | x |  |  | E:V118CF | V118C Reference | 2 |  | x |  | E:V118CF | V118C Reference
| 3 |  | x | BE | SAT2 | E:V118 | V118 B2 String Current | 3 |  | x | BE | E:V118 | V118 B2 String Current
| 4 |  | x | BE | SAT2 | E:V118E | V118 Current Error | 4 |  | x | BE | E:V118E | V118 Current Error
| 5 |  | x |  |  | E:V118P | V118 Pos Volts to Gnd | 5 |  | x |  | E:V118P | V118 Pos Volts to Gnd
| 6 |  | x |  |  | E:V118N | V118 Neg Volts to Gnd | 6 |  | x |  | E:V118N | V118 Neg Volts to Gnd
| 7 |  | x |  |  | E:V118V | V118 Filtered Volts Out | 7 |  | x |  | E:V118V | V118 Filtered Volts Out
| 8 |  | x |  |  | E:V118AU | V118A Unfilterd Volts Out | 8 |  | x |  | E:V118AU | V118A Unfilterd Volts Out
| 9 |  | x | BE | SAT2 | E:V118F | V118 Reference | 9 |  | x | BE | E:V118F | V118 Reference
| 10 |  | x |  |  | E:V118CU | V118C Unfilterd Volts Out | 10 |  | x |  | E:V118CU | V118C Unfilterd Volts Out
| 11 |  | x | BE | SAT2 | E:QD113F | QD113 Reference | 11 |  | x | BE | E:QD113F | QD113 Reference
| 12 |  | x | BE | SAT2 | E:QD113 | QD113 Current | 12 |  | x | BE | E:QD113 | QD113 Current
| 13 |  | x |  |  | E:QD113E | QD113 Current Error | 13 |  | x |  | E:QD113E | QD113 Current Error
| 14 |  | x |  |  | E:QD113V | QD113 Voltage | 14 |  | x |  | E:QD113V | QD113 Voltage
| 15 |  | x | BE | SAT2 | E:QF114F | QF114 Reference | 15 |  | x | BE | E:QF114F | QF114 Reference
| 16 |  | x | BE | SAT2 | E:QF114 | QF114 Current | 16 |  | x | BE | E:QF114 | QF114 Current
| 17 |  | x |  |  | E:QF114E | QF114 Current Error | 17 |  | x |  | E:QF114E | QF114 Current Error
| 18 |  | x |  |  | E:QF114V | QF114 Voltage | 18 |  | x |  | E:QF114V | QF114 Voltage
| 19 |  | x | BE | SAT2 | E:QF115F | QF115 Reference | 19 |  | x | BE | E:QF115F | QF115 Reference
| 20 |  | x | BE | SAT2 | E:QF115 | QF115 Current | 20 |  | x | BE | E:QF115 | QF115 Current
| 21 |  | x |  |  | E:QF115E | QF115 Current Error | 21 |  | x |  | E:QF115E | QF115 Current Error
| 22 |  | x |  |  | E:QF115V | QF115 Voltage | 22 |  | x |  | E:QF115V | QF115 Voltage
| 23 |  | x | BE | SAT2 | E:QD116F | QD116 Reference | 23 |  | x | BE | E:QD116F | QD116 Reference
| 24 |  | x | BE | SAT2 | E:QD116 | QD116 Current | 24 |  | x | BE | E:QD116 | QD116 Current
| 25 |  | x |  |  | E:QD116E | QD116 Current Error | 25 |  | x |  | E:QD116E | QD116 Current Error
| 26 |  | x |  |  | E:QD116V | QD116 Voltage | 26 |  | x |  | E:QD116V | QD116 Voltage
| 27 |  | x | BE | SAT2 | E:QF117F | QF117 Reference | 27 |  | x | BE | E:QF117F | QF117 Reference
| 28 |  | x | BE | SAT2 | E:QF117 | QF117 Current | 28 |  | x | BE | E:QF117 | QF117 Current
| 29 |  | x |  |  | E:QF117E | QF117 Current Error | 29 |  | x |  | E:QF117E | QF117 Current Error
| 30 |  | x |  |  | E:QF117V | QF117 Voltage | 30 |  | x |  | E:QF117V | QF117 Voltage
| 31 |  | x | BE | SAT2 | E:QD118F | QD118 Reference | 31 |  | x | BE | E:QD118F | QD118 Reference
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 85 | MADC ASSIGNMENTS FOR NuMI MI-65 Service Building, MADC #85, Crate $E4 N23, Rack MI65103
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #85, Crate $E4 N23, Rack MI65103 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 |  | x | BE | SAT2 | E:QD118 | QD118 Current | 32 |  | x | BE | E:QD118 | QD118 Current
| 33 |  | x |  |  | E:QD118E | QD118 Current Error | 33 |  | x |  | E:QD118E | QD118 Current Error
| 34 |  | x |  |  | E:QD118V | QD118 Voltage | 34 |  | x |  | E:QD118V | QD118 Voltage
| 35 |  | x | BE | SAT2 | E:QF119F | QF119 Reference | 35 |  | x | BE | E:QF119F | QF119 Reference
| 36 |  | x | BE | SAT2 | E:QF119 | QF119 Current | 36 |  | x | BE | E:QF119 | QF119 Current
| 37 |  | x |  |  | E:QF119E | QF119 Current Error | 37 |  | x |  | E:QF119E | QF119 Current Error
| 38 |  | x |  |  | E:QF119V | QF119 Voltage | 38 |  | x |  | E:QF119V | QF119 Voltage
| 39 |  | x | BE | SAT2 | E:QD120F | QD120 Reference | 39 |  | x | BE | E:QD120F | QD120 Reference
| 40 |  | x | BE | SAT2 | E:QD120 | QD120 Current | 40 |  | x | BE | E:QD120 | QD120 Current
| 41 |  | x |  |  | E:QD120E | QD120 Current Error | 41 |  | x |  | E:QD120E | QD120 Current Error
| 42 |  | x |  |  | E:QD120V | QD120 Voltage | 42 |  | x |  | E:QD120V | QD120 Voltage
| 43 |  | x | BE | SAT2 | E:QF121F | QF121 Reference | 43 |  | x | BE | E:QF121F | QF121 Reference
| 44 |  | x | BE | SAT2 | E:QF121 | QF121 Current | 44 |  | x | BE | E:QF121 | QF121 Current
| 45 |  | x |  |  | E:QF121E | QF121 Current Error | 45 |  | x |  | E:QF121E | QF121 Current Error
| 46 |  | x |  |  | E:QF121V | QF121 Voltage | 46 |  | x |  | E:QF121V | QF121 Voltage
| 47 |  | x | BE | SAT2 | E:H117F | H117 Trim Dipole Ref | 47 |  | x | BE | E:H117F | H117 Trim Dipole Ref
| 48 |  | x | BE | SAT2 | E:H117 | H117 Trim Current | 48 |  | x | BE | E:H117 | H117 Trim Current
| 49 |  | x |  |  | E:H117E | H117 Trim Current Error | 49 |  | x |  | E:H117E | H117 Trim Current Error
| 50 |  | x |  |  | E:H117V | H117 Trim Voltage | 50 |  | x |  | E:H117V | H117 Trim Voltage
| 51 |  | x |  |  | E:V118AF | V118A Reference | 51 |  | x |  | E:V118AF | V118A Reference
| 52 |  | x | AE | SAT6 | E:HP121P | HPos 121 for BPS Check | 52 |  | x | AE | E:HP121P | HPos 121 for BPS Check
| 53 |  | x | AE | SAT6 | E:VP121P | VPos 121 for BPS Check | 53 |  | x | AE | E:VP121P | VPos 121 for BPS Check
| 54 |  | x | AE | SAT6 | E:HPTGTP | HPos TGT for BPS Check | 54 |  | x | AE | E:HPTGTP | HPos TGT for BPS Check
| 55 |  | x | AE | SAT6 | E:VPTGTP | VPos TGT for BPS Check | 55 |  | x | AE | E:VPTGTP | VPos TGT for BPS Check
| 56 | x |  | C | SAT1 | E:CPS65V | Trim Elem PS Bulk Volts | 56 | x |  | C | E:CPS65V | Trim Elem PS Bulk Volts
| 57 | x |  | BE | SAT2 | E:65BPMB | MI65 BPM Stat Before Ext | 57 | x |  | BE | E:65BPMB | MI65 BPM Stat Before Ext
| 58 | x |  | AE | SAT6 | E:65BPMA | MI65 BPM Stat After Ext | 58 | x |  | AE | E:65BPMA | MI65 BPM Stat After Ext
| 59 | x | [5 empty] | 59 | x
| 60 | x | [5 empty] | 60 | x
| 61 | x | [5 empty] | 61 | x
| 62 | x | [5 empty] | 62 | x
| 63 | x | [5 empty] | 63 | x
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 86 | MADC ASSIGNMENTS FOR NuMI MI-65 Service Building, MADC #86, Crate $E5 N23, Rack MI65108
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #86, Crate $E5 N23, Rack MI65108 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 | Direct |  | Not Available |  | E:VT114F | VT114 Reference | 0 | Direct |  | NA | E:VT114F | VT114 Reference
| 1 | Direct |  | Not Available |  | E:VT114K | VT114 F(t) Table | 1 | Direct |  | NA | E:VT114K | VT114 F(t) Table
| 2 | Direct |  | Not Available |  | E:VT114V | VT114 Voltage Out | 2 | Direct |  | NA | E:VT114V | VT114 Voltage Out
| 3 | Direct |  | Not Available |  | E:VT114I | VT114 RMS Current | 3 | Direct |  | NA | E:VT114I | VT114 RMS Current
| 4 | Direct |  | Not Available |  | E:HT114F | HT114 Reference | 4 | Direct |  | NA | E:HT114F | HT114 Reference
| 5 | Direct |  | Not Available |  | E:HT114K | HT114 F(t) Table | 5 | Direct |  | NA | E:HT114K | HT114 F(t) Table
| 6 | Direct |  | Not Available |  | E:HT114V | HT114 Voltage Out | 6 | Direct |  | NA | E:HT114V | HT114 Voltage Out
| 7 | Direct |  | Not Available |  | E:HT114I | HT114 RMS Current | 7 | Direct |  | NA | E:HT114I | HT114 RMS Current
| 8 | Direct |  | Not Available |  | E:HT115F | HT115 Reference | 8 | Direct |  | NA | E:HT115F | HT115 Reference
| 9 | Direct |  | Not Available |  | E:HT115K | HT115 F(t) Table | 9 | Direct |  | NA | E:HT115K | HT115 F(t) Table
| 10 | Direct |  | Not Available |  | E:HT115V | HT115 Voltage Out | 10 | Direct |  | NA | E:HT115V | HT115 Voltage Out
| 11 | Direct |  | Not Available |  | E:HT115I | HT115 RMS Current | 11 | Direct |  | NA | E:HT115I | HT115 RMS Current
| 12 | Direct |  | Not Available |  | E:VT116F | VT116 Reference | 12 | Direct |  | NA | E:VT116F | VT116 Reference
| 13 | Direct |  | Not Available |  | E:VT116K | VT116 F(t) Table | 13 | Direct |  | NA | E:VT116K | VT116 F(t) Table
| 14 | Direct |  | Not Available |  | E:VT116V | VT116 Voltage Out | 14 | Direct |  | NA | E:VT116V | VT116 Voltage Out
| 15 | Direct |  | Not Available |  | E:VT116I | VT116 RMS Current | 15 | Direct |  | NA | E:VT116I | VT116 RMS Current
| 16 | Direct |  | Not Available |  | E:HT117F | HT117 Reference | 16 | Direct |  | NA | E:HT117F | HT117 Reference
| 17 | Direct |  | Not Available |  | E:HT117K | HT117 F(t) Table | 17 | Direct |  | NA | E:HT117K | HT117 F(t) Table
| 18 | Direct |  | Not Available |  | E:HT117V | HT117 Voltage Out | 18 | Direct |  | NA | E:HT117V | HT117 Voltage Out
| 19 | Direct |  | Not Available |  | E:HT117I | HT117 RMS Current | 19 | Direct |  | NA | E:HT117I | HT117 RMS Current
| 20 | Direct |  | Not Available |  | E:VT118F | VT118 Reference | 20 | Direct |  | NA | E:VT118F | VT118 Reference
| 21 | Direct |  | Not Available |  | E:VT118K | VT118 F(t) Table | 21 | Direct |  | NA | E:VT118K | VT118 F(t) Table
| 22 | Direct |  | Not Available |  | E:VT118V | VT118 Voltage Out | 22 | Direct |  | NA | E:VT118V | VT118 Voltage Out
| 23 | Direct |  | Not Available |  | E:VT118I | VT118 RMS Current | 23 | Direct |  | NA | E:VT118I | VT118 RMS Current
| 24 | Direct |  | Not Available |  | E:HT119F | HT119 Reference | 24 | Direct |  | NA | E:HT119F | HT119 Reference
| 25 | Direct |  | Not Available |  | E:HT119K | HT119 F(t) Table | 25 | Direct |  | NA | E:HT119K | HT119 F(t) Table
| 26 | Direct |  | Not Available |  | E:HT119V | HT119 Voltage Out | 26 | Direct |  | NA | E:HT119V | HT119 Voltage Out
| 27 | Direct |  | Not Available |  | E:HT119I | HT119 RMS Current | 27 | Direct |  | NA | E:HT119I | HT119 RMS Current
| 28 | Direct |  | Not Available |  | E:HT121F | HT121 Reference | 28 | Direct |  | NA | E:HT121F | HT121 Reference
| 29 | Direct |  | Not Available |  | E:HT121K | HT121 F(t) Table | 29 | Direct |  | NA | E:HT121K | HT121 F(t) Table
| 30 | Direct |  | Not Available |  | E:HT121V | HT121 Voltage Out | 30 | Direct |  | NA | E:HT121V | HT121 Voltage Out
| 31 | Direct |  | Not Available |  | E:HT121I | HT121 RMS Current | 31 | Direct |  | NA | E:HT121I | HT121 RMS Current
# 86 | MADC ASSIGNMENTS FOR NuMI MI-65 Service Building, MADC #86, Crate $E5 N23, Rack MI65108
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #86, Crate $E5 N23, Rack MI65108 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 | Direct |  | Not Available |  | E:VT121F | VT121 Reference | 32 | Direct |  | NA | E:VT121F | VT121 Reference
| 33 | Direct |  | Not Available |  | E:VT121K | VT121 F(t) Table | 33 | Direct |  | NA | E:VT121K | VT121 F(t) Table
| 34 | Direct |  | Not Available |  | E:VT121V | VT121 Voltage Out | 34 | Direct |  | NA | E:VT121V | VT121 Voltage Out
| 35 | Direct |  | Not Available |  | E:VT121I | VT121 RMS Current | 35 | Direct |  | NA | E:VT121I | VT121 RMS Current
| 36 | Direct |  | Not Available |  |  |  | 36 | Direct |  | NA
| 37 | Direct |  | Not Available |  |  |  | 37 | Direct |  | NA
| 38 | Direct |  | Not Available |  |  |  | 38 | Direct |  | NA
| 39 | Direct |  | Not Available |  |  |  | 39 | Direct |  | NA
| 40 | Direct |  | Not Available |  |  |  | 40 | Direct |  | NA
| 41 | Direct |  | Not Available |  |  |  | 41 | Direct |  | NA
| 42 | Direct |  | Not Available |  |  |  | 42 | Direct |  | NA
| 43 | Direct |  | Not Available |  |  |  | 43 | Direct |  | NA
| 44 | Direct |  | Not Available |  |  |  | 44 | Direct |  | NA
| 45 | Direct |  | Not Available |  |  |  | 45 | Direct |  | NA
| 46 | Direct |  | Not Available |  | E:CPS65 | Trim Elem PS Bulk I | 46 | Direct |  | NA | E:CPS65 | Trim Elem PS Bulk I
| 47 | Direct |  | Not Available |  | E:CPS65I | Trim Elem PS Bulk RMS I | 47 | Direct |  | NA | E:CPS65I | Trim Elem PS Bulk RMS I
| 48 | x |  | Not Available |  | E:PM114V | PM114 Clearing Voltage | 48 | x |  | NA | E:PM114V | PM114 Clearing Voltage
| 49 | x |  | Not Available |  | E:PM115V | PM115 Clearing Voltage | 49 | x |  | NA | E:PM115V | PM115 Clearing Voltage
| 50 | x |  | Not Available |  | E:PM117V | PM117 Clearing Voltage | 50 | x |  | NA | E:PM117V | PM117 Clearing Voltage
| 51 | x |  | Not Available |  | E:PM121V | PM121 Clearing Voltage | 51 | x |  | NA | E:PM121V | PM121 Clearing Voltage
| 52 | x |  | Not Available |  | E:PMTGTV | PMTGT Clearing Voltage | 52 | x |  | NA | E:PMTGTV | PMTGT Clearing Voltage
| 53 | x |  | Not Available |  | E:CBT65 | MI65 Crane Bay Temp | 53 | x |  | NA | E:CBT65 | MI65 Crane Bay Temp
| 54 | x |  | Not Available |  | E:CBH65 | MI65 Crane Bay Humidity | 54 | x |  | NA | E:CBH65 | MI65 Crane Bay Humidity
| 55 | x |  | Not Available |  | E:TTUHOB | NuMI Upper Hobbit Temp | 55 | x |  | NA | E:TTUHOB | NuMI Upper Hobbit Temp
| 56 | x |  | Not Available |  | E:THUHOB | NuMI Upper Hobbit Humid | 56 | x |  | NA | E:THUHOB | NuMI Upper Hobbit Humid
| 57 | x |  | Not Available |  | E:TTLHOB | NuMI Lower Hobbit Temp | 57 | x |  | NA | E:TTLHOB | NuMI Lower Hobbit Temp
| 58 | x |  | Not Available |  | E:THLHOB | NuMI Lower Hobbit Humid | 58 | x |  | NA | E:THLHOB | NuMI Lower Hobbit Humid
| 59 | x |  | Not Available |  | E:TTPTGT | NuMI Pre-Tgt Temp | 59 | x |  | NA | E:TTPTGT | NuMI Pre-Tgt Temp
| 60 | x |  | Not Available |  | E:THPTGT | NuMI Pre-Tgt Humidity | 60 | x |  | NA | E:THPTGT | NuMI Pre-Tgt Humidity
| 61 | x |  | Not Available |  | E:ERT65E | MI65 Elec Rm Temp | 61 | x |  | NA | E:ERT65E | MI65 Elec Rm Temp
| 62 | x |  | Not Available |  | E:ERT65P | MI65 PS Rm Temp | 62 | x |  | NA | E:ERT65P | MI65 PS Rm Temp
| 63 | x |  | Not Available |  | E:ERH65P | MI65 PS Rm Humidity | 63 | x |  | NA | E:ERH65P | MI65 PS Rm Humidity
# 87 | MADC ASSIGNMENTS FOR NuMI MI-65 Underground - PS Support Room, MADC #87, Crate $E6 N23, Rack THSR103
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #87, Crate $E6 N23, Rack THSR103 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 | x |  | JBE | SAT4 | E:HSLI | Horn Stripline Current | 0 | x |  | JBE | E:HSLI | Horn Stripline Current
| 1 | x |  | BE | SAT5 | E:NHSAF | NuMI Horn Pwr Sply A Ref | 1 | x |  | BE | E:NHSAF | NuMI Horn Pwr Sply A Ref
| 2 | x |  | BE | SAT5 | E:NHSBF | NuMI Horn Pwr Sply B Ref | 2 | x |  | BE | E:NHSBF | NuMI Horn Pwr Sply B Ref
| 3 | x |  | BE | SAT5 | E:NHSASF | Horn PS A Slow Strt Ref | 3 | x |  | BE | E:NHSASF | Horn PS A Slow Strt Ref
| 4 | x |  | BE | SAT5 | E:NHSBSF | Horn PS B Slow Strt Ref | 4 | x |  | BE | E:NHSBSF | Horn PS B Slow Strt Ref
| 5 | x |  | AE | SAT3 | E:HSLIP | Peak Horn Stripline Current | 5 | x |  | AE | E:HSLIP | Peak Horn Stripline Current
| 6 | x |  | C | SAT1 | E:LMHV4O | Reg Loss Mon Ch#4 HV Out | 6 | x |  | C | E:LMHV4O | Reg Loss Mon Ch#4 HV Out
| 7 | x |  | C | SAT1 | E:LMHV4R | Reg Loss Mon Ch#4 HV Ret | 7 | x |  | C | E:LMHV4R | Reg Loss Mon Ch#4 HV Ret
| 8 | x |  | AE | SAT3 | E:LMQ113 | Loss Monitor #1 at Q113 | 8 | x |  | AE | E:LMQ113 | Loss Monitor #1 at Q113
| 9 | x |  | AE | SAT3 | E:LMQ114 | Loss Monitor #2 at Q114 | 9 | x |  | AE | E:LMQ114 | Loss Monitor #2 at Q114
| 10 | x |  | AE | SAT3 | E:LMQ115 | Loss Monitor #3 at Q115 | 10 | x |  | AE | E:LMQ115 | Loss Monitor #3 at Q115
| 11 | x |  | AE | SAT3 | E:LMQ116 | Loss Monitor #4 at Q116 | 11 | x |  | AE | E:LMQ116 | Loss Monitor #4 at Q116
| 12 | x |  | AE | SAT3 | E:LMQ117 | Loss Monitor #5 at Q117 | 12 | x |  | AE | E:LMQ117 | Loss Monitor #5 at Q117
| 13 | x |  | AE | SAT3 | E:LMH117 | Loss Monitor #6 at H117 | 13 | x |  | AE | E:LMH117 | Loss Monitor #6 at H117
| 14 | x |  | AE | SAT3 | E:LMQ118 | Loss Monitor #7 at Q118 | 14 | x |  | AE | E:LMQ118 | Loss Monitor #7 at Q118
| 15 | x |  | AE | SAT3 | E:LM1181 | Loss Monitor #8 at V118-1 | 15 | x |  | AE | E:LM1181 | Loss Monitor #8 at V118-1
| 16 | x |  | AE | SAT3 | E:LM1182 | Loss Monitor #9 at V118-2 | 16 | x |  | AE | E:LM1182 | Loss Monitor #9 at V118-2
| 17 | x |  | AE | SAT3 | E:LMQ119 | Loss Monitor #10 at Q119 | 17 | x |  | AE | E:LMQ119 | Loss Monitor #10 at Q119
| 18 | x |  |  |  | E:TORTGT | NuMI DnStrm Intn at TGT | 18 | x |  |  | E:TORTGT | NuMI DnStrm Intn at TGT
| 19 | x |  |  |  | E:ROCK87 | Readout Check at MADC 87 | 19 | x |  |  | E:ROCK87 | Readout Check at MADC 87
| 20 | x |  |  |  | E:TRETHF | Tgt RAW Exp Tank He Flow | 20 | x |  |  | E:TRETHF | Tgt RAW Exp Tank He Flow
| 21 | x | [5 empty] | 21 | x
| 22 | x | [5 empty] | 22 | x
| 23 | x | [5 empty] | 23 | x
| 24 | x | [5 empty] | 24 | x
| 25 | x | [5 empty] | 25 | x
| 26 | x | [5 empty] | 26 | x
| 27 | x | [5 empty] | 27 | x
| 28 | x | [5 empty] | 28 | x
| 29 | x | [5 empty] | 29 | x
| 30 | x | [5 empty] | 30 | x
| 31 | x | [5 empty] | 31 | x
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 87 | MADC ASSIGNMENTS FOR NuMI MI-65 Underground - PS Support Room, MADC #87, Crate $E6 N23, Rack THSR103
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #87, Crate $E6 N23, Rack THSR103 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 |  | x |  |  |  |  | 32 |  | x |  | E:NHSA | NuMI Horn PS A Current
| 33 |  | x |  |  |  |  | 33 |  | x |  | E:NHSB | NuMI Horn PS B Current
| 34 |  | x | C | SAT1 | E:BAFT1 | Baffle Temperature #1 | 34 |  | x | C | E:BAFT1 | Baffle Temperature #1
| 35 |  | x | C | SAT1 | E:BAFT2 | Baffle Temperature #2 | 35 |  | x | C | E:BAFT2 | Baffle Temperature #2
| 36 |  | x |  |  | E:TGTT1 | Target Temperature #1 | 36 |  | x |  | E:TGTT1 | Target Temperature #1
| 37 |  | x |  |  | E:TGTT2 | Target Temperature #2 | 37 |  | x |  | E:TGTT2 | Target Temperature #2
| 38 |  | x |  |  | E:TGTGZ | Target to Gnd Impedance | 38 |  | x |  | E:TGTGZ | Target to Gnd Impedance
| 39 |  | x |  |  | E:PGTGT | Target Vacuum Pirani | 39 |  | x |  | E:PGTGT | Target Vacuum Pirani
| 40 |  | x |  |  |  |  | 40 |  | x
| 41 |  | x |  |  | E:HFVSL | Horz Fin VertScan LoGain | 41 |  | x |  | E:HFVSL | Horz Fin VertScan LoGain
| 42 |  | x |  |  | E:HFVSH | Horz Fin VertScan HiGain | 42 |  | x |  | E:HFVSH | Horz Fin VertScan HiGain
| 43 |  | x |  |  | E:VFHSL | Vert Fin HorzScan LoGain | 43 |  | x |  | E:VFHSL | Vert Fin HorzScan LoGain
| 44 |  | x |  |  | E:VFHSH | Vert Fin HorzScan HiGain | 44 |  | x |  | E:VFHSH | Vert Fin HorzScan HiGain
| 45 |  | x | C | SAT1 | E:TPCFDP | Targt Pile Fan Diff Pres | 45 |  | x | C | E:TPCFDP | Targt Pile Fan Diff Pres
| 46 |  | x | C | SAT1 | E:TPCAST | Targt Pile Air Sply Temp | 46 |  | x | C | E:TPCAST | Targt Pile Air Sply Temp
| 47 |  | x |  |  | E:HSQAII | Horn SL Quad A Crnt Intg | 47 |  | x |  | E:HSQAII | Horn SL Quad A Crnt Intg
| 48 |  | x |  |  | E:HSQBII | Horn SL Quad B Crnt Intg | 48 |  | x |  | E:HSQBII | Horn SL Quad B Crnt Intg
| 49 |  | x |  |  | E:HSQCII | Horn SL Quad C Crnt Intg | 49 |  | x |  | E:HSQCII | Horn SL Quad C Crnt Intg
| 50 |  | x |  |  | E:HSQDII | Horn SL Quad D Crnt Intg | 50 |  | x |  | E:HSQDII | Horn SL Quad D Crnt Intg
| 51 |  | x |  |  |  |  | 51 |  | x
| 52 |  | x | C | SAT1 | E:TGTHFR | Target Helium Flow Rough | 52 |  | x | C | E:TGTHFR | Target Helium Flow Rough
| 53 |  | x |  |  | E:TGTHFF | Target Helium Flow Fine | 53 |  | x |  | E:TGTHFF | Target Helium Flow Fine
| 54 |  | x |  |  |  |  | 54 |  | x
| 55 |  | x |  |  |  |  | 55 |  | x
| 56 |  | x |  |  |  |  | 56 |  | x
| 57 |  | x |  |  |  |  | 57 |  | x
| 58 |  | x |  |  |  |  | 58 |  | x
| 59 |  | x |  |  |  |  | 59 |  | x
| 60 |  | x |  |  |  |  | 60 |  | x |  | E:HSLIB | Horn SL Crnt at Beam Arv
| 61 |  | x |  |  |  |  | 61 |  | x | AE | E:NOCLU1 | Arrival of Beam wrt Clock
| 62 |  | x |  |  |  |  | 62 |  | x | AE | E:NOCLU2 | Horn BDOT Zero wrt Clock
| 63 |  | x |  |  |  |  | 63 |  | x | AE | E:NOCLU3 | Beam Arvl - BDOT Zero
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 88 | MADC ASSIGNMENTS FOR NuMI MI-65 Underground - PS Support Room, MADC #88, Crate $E6 N22, Rack THSR104
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #88, Crate $E6 N22, Rack THSR104 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 | x |  | C | SAT1 | E:LMHV5O | Reg Loss Mon Ch#5 HV Out | 0 | x |  | C | E:LMHV5O | Reg Loss Mon Ch#5 HV Out
| 1 | x |  | C | SAT1 | E:LMHV5R | Reg Loss Mon Ch#5 HV Ret | 1 | x |  | C | E:LMHV5R | Reg Loss Mon Ch#5 HV Ret
| 2 | x |  | AE | SAT3 | E:LM1183 | Loss Monitor #1 at V118-3 | 2 | x |  | AE | E:LM1183 | Loss Monitor #1 at V118-3
| 3 | x |  | AE | SAT3 | E:LM1184 | Loss Monitor #2 at V118-4 | 3 | x |  | AE | E:LM1184 | Loss Monitor #2 at V118-4
| 4 | x |  | AE | SAT3 | E:LMQ120 | Loss Monitor #3 at Q120 | 4 | x |  | AE | E:LMQ120 | Loss Monitor #3 at Q120
| 5 | x |  | AE | SAT3 | E:LMQ121 | Loss Monitor #4 at Q121 | 5 | x |  | AE | E:LMQ121 | Loss Monitor #4 at Q121
| 6 | x |  |  |  | E:H1ALV | Horn 1 Alignmnt LM HV | 6 | x |  |  | E:H1ALV | Horn 1 Alignmnt LM HV
| 7 | x |  |  |  | E:H2ALV | Horn 2 Alignmnt LM HV | 7 | x |  |  | E:H2ALV | Horn 2 Alignmnt LM HV
| 8 | x |  | AE | SAT3 | E:LMTGTT | Loss Mon at NuMI TORTGT | 8 | x |  | AE | E:LMTGTT | Loss Mon at NuMI TORTGT
| 9 | x |  | AE | SAT3 | E:LMTSW | LMon at Tgt Shield Wall | 9 | x |  | AE | E:LMTSW | LMon at Tgt Shield Wall
| 10 | x |  |  |  | E:H1ALM | Horn 1 Alignmnt Loss Mon | 10 | x |  |  | E:H1ALM | Horn 1 Alignmnt Loss Mon
| 11 | x |  |  |  | E:H2ALM | Horn 2 Alignmnt Loss Mon | 11 | x |  |  | E:H2ALM | Horn 2 Alignmnt Loss Mon
| 12 | x |  |  |  | E:ROCK88 | Readout Check at MADC 88 | 12 | x |  |  | E:ROCK88 | Readout Check at MADC 88
| 13 | x | [5 empty] | 13 | x
| 14 | x | [5 empty] | 14 | x
| 15 | x | [5 empty] | 15 | x
| 16 | x | [5 empty] | 16 | x
| 17 | x | [5 empty] | 17 | x
| 18 | x | [5 empty] | 18 | x
| 19 | x | [5 empty] | 19 | x |  |  | E:TQD113 | Temp Mon at QD113
| 20 | x | [5 empty] | 20 | x |  |  | E:TQF114 | Temp Mon at QF114
| 21 | x | [5 empty] | 21 | x |  |  | E:TQF117 | Temp Mon at QF117
| 22 | x | [5 empty] | 22 | x |  |  | E:TH117 | Temp Mon at H117
| 23 | x | [5 empty] | 23 | x |  |  | E:TQD118 | Temp Mon at QD118
| 24 | x | [5 empty] | 24 | x |  |  | E:TQD120 | Temp Mon at QD120
| 25 | x | [5 empty] | 25 | x |  |  | E:TQF121 | Temp Mon at QF121
| 26 | x | [5 empty] | 26 | x |  |  | E:TTGTBS | Temp Mon at TGT BPM Stnd
| 27 | x |  |  |  | E:TTPSSR | NuMI PS Sprt Rm Temp | 27 | x |  |  | E:TTPSSR | NuMI PS Sprt Rm Temp
| 28 | x |  |  |  | E:THPSSR | NuMI PS Sprt Rm Humid | 28 | x |  |  | E:THPSSR | NuMI PS Sprt Rm Humid
| 29 | x |  |  |  | E:TTRAWR | NuMI RAW Room Temp | 29 | x |  |  | E:TTRAWR | NuMI RAW Room Temp
| 30 | x |  |  |  | E:TTTGTH | NuMI Target Hall Temp | 30 | x |  |  | E:TTTGTH | NuMI Target Hall Temp
| 31 | x |  |  |  | E:THTGTH | NuMI Target Hall Humidty | 31 | x |  |  | E:THTGTH | NuMI Target Hall Humidty
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 88 | MADC ASSIGNMENTS FOR NuMI MI-65 Underground - PS Support Room, MADC #88, Crate $E6 N22, Rack THSR104
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #88, Crate $E6 N22, Rack THSR104 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 |  | x |  |  | E:H1FLXL | Horn 1 Left Flux Wave | 32 |  | x |  | E:H1FLXL | Horn 1 Left Flux Wave
| 33 |  | x |  |  | E:H1FLXT | Horn 1 Top Flux Wave | 33 |  | x |  | E:H1FLXT | Horn 1 Top Flux Wave
| 34 |  | x |  |  | E:H1FLXR | Horn 1 Right Flux Wave | 34 |  | x |  | E:H1FLXR | Horn 1 Right Flux Wave
| 35 |  | x |  |  | E:H2FLXL | Horn 2 Left Flux Wave | 35 |  | x |  | E:H2FLXL | Horn 2 Left Flux Wave
| 36 |  | x |  |  | E:H2FLXT | Horn 2 Top Flux Wave | 36 |  | x |  | E:H2FLXT | Horn 2 Top Flux Wave
| 37 |  | x |  |  | E:H2FLXR | Horn 2 Right Flux Wave | 37 |  | x |  | E:H2FLXR | Horn 2 Right Flux Wave
| 38 |  | x |  |  | E:H1FPKL | Horn 1 Left Flux Peak | 38 |  | x |  | E:H1FPKL | Horn 1 Left Flux Peak
| 39 |  | x |  |  | E:H1FPKT | Horn 1 Top Flux Peak | 39 |  | x |  | E:H1FPKT | Horn 1 Top Flux Peak
| 40 |  | x |  |  | E:H1FPKR | Horn 1 Right Flux Peak | 40 |  | x |  | E:H1FPKR | Horn 1 Right Flux Peak
| 41 |  | x |  |  | E:H2FPKL | Horn 2 Left Flux Peak | 41 |  | x |  | E:H2FPKL | Horn 2 Left Flux Peak
| 42 |  | x |  |  | E:H2FPKT | Horn 2 Top Flux Peak | 42 |  | x |  | E:H2FPKT | Horn 2 Top Flux Peak
| 43 |  | x |  |  | E:H2FPKR | Horn 2 Right Flux Peak | 43 |  | x |  | E:H2FPKR | Horn 2 Right Flux Peak
| 44 |  | x |  |  | E:H1INTL | Horn 1 Left Flux Intgrl | 44 |  | x |  | E:H1INTL | Horn 1 Left Flux Intgrl
| 45 |  | x |  |  | E:H1INTT | Horn 1Top Flux Intgrl | 45 |  | x |  | E:H1INTT | Horn 1Top Flux Intgrl
| 46 |  | x |  |  | E:H1INTR | Horn 1 Right Flux Intgrl | 46 |  | x |  | E:H1INTR | Horn 1 Right Flux Intgrl
| 47 |  | x |  |  | E:H2INTL | Horn 2 Left Flux Intgrl | 47 |  | x |  | E:H2INTL | Horn 2 Left Flux Intgrl
| 48 |  | x |  |  | E:H2INTT | Horn 2 Top Flux Intgrl | 48 |  | x |  | E:H2INTT | Horn 2 Top Flux Intgrl
| 49 |  | x |  |  | E:H2INTR | Horn 2 Right Flux Intgrl | 49 |  | x |  | E:H2INTR | Horn 2 Right Flux Intgrl
| 50 |  | x |  |  |  |  | 50 |  | x
| 51 |  | x |  |  |  |  | 51 |  | x
| 52 |  | x |  |  | E:HSQAI | Horn SL Quad A Current | 52 |  | x |  | E:HSQAI | Horn SL Quad A Current
| 53 |  | x |  |  | E:HSQBI | Horn SL Quad B Current | 53 |  | x |  | E:HSQBI | Horn SL Quad B Current
| 54 |  | x |  |  | E:HSQCI | Horn SL Quad C Current | 54 |  | x |  | E:HSQCI | Horn SL Quad C Current
| 55 |  | x |  |  | E:HSQDI | Horn SL Quad D Current | 55 |  | x |  | E:HSQDI | Horn SL Quad D Current
| 56 |  | x |  |  | E:HSQAIP | Horn SL Quad A Crnt Peak | 56 |  | x |  | E:HSQAIP | Horn SL Quad A Crnt Peak
| 57 |  | x |  |  | E:HSQBIP | Horn SL Quad B Crnt Peak | 57 |  | x |  | E:HSQBIP | Horn SL Quad B Crnt Peak
| 58 |  | x |  |  | E:HSQCIP | Horn SL Quad C Crnt Peak | 58 |  | x |  | E:HSQCIP | Horn SL Quad C Crnt Peak
| 59 |  | x |  |  | E:HSQDIP | Horn SL Quad D Crnt Peak | 59 |  | x |  | E:HSQDIP | Horn SL Quad D Crnt Peak
| 60 |  | x |  |  |  |  | 60 |  | x
| 61 |  | x |  |  |  |  | 61 |  | x
| 62 |  | x |  |  |  |  | 62 |  | x
| 63 |  | x |  |  |  |  | 63 |  | x
| PCI Codes: Continuos - Before Extraction - Just Before Extraction - After Extraction | [7 empty] | JBE in the PCI Column Indicates Preference for Assignment at or Close to Channel 0
# 89 | MADC ASSIGNMENTS FOR NuMI MINOS Service Building, MADC #1, Crate $E7 N23, Rack MSB101
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #89, Crate $E7 N23, Rack MSB101 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 | x |  | Not Available |  | E:MSP1I | MINOS Sump 1 Current | 0 | x |  | NA | E:MSP1I | MINOS Sump 1 Current
| 1 | x |  | Not Available |  | E:MSP2I | MINOS Sump 2 Current | 1 | x |  | NA | E:MSP2I | MINOS Sump 2 Current
| 2 | x |  | Not Available |  | E:MESP3I | MINOS ESump 3 Current | 2 | x |  | NA | E:MESP3I | MINOS ESump 3 Current
| 3 | x |  | Not Available |  |  |  | 3 | x |  | NA
| 4 | x |  | Not Available |  |  |  | 4 | x |  | NA
| 5 | x |  | Not Available |  |  |  | 5 | x |  | NA
| 6 | x |  | Not Available |  |  |  | 6 | x |  | NA
| 7 | x |  | Not Available |  |  |  | 7 | x |  | NA
| 8 | x |  | Not Available |  |  |  | 8 | x |  | NA
| 9 | x |  | Not Available |  |  |  | 9 | x |  | NA
| 10 | x |  | Not Available |  |  |  | 10 | x |  | NA
| 11 | x |  | Not Available |  |  |  | 11 | x |  | NA
| 12 | x |  | Not Available |  |  |  | 12 | x |  | NA
| 13 | x |  | Not Available |  |  |  | 13 | x |  | NA
| 14 | x |  | Not Available |  |  |  | 14 | x |  | NA
| 15 | x |  | Not Available |  |  |  | 15 | x |  | NA
| 16 |  | x | Not Available |  |  |  | 16 |  | x | NA
| 17 |  | x | Not Available |  |  |  | 17 |  | x | NA
| 18 |  | x | Not Available |  |  |  | 18 |  | x | NA
| 19 |  | x | Not Available |  |  |  | 19 |  | x | NA
| 20 |  | x | Not Available |  |  |  | 20 |  | x | NA
| 21 |  | x | Not Available |  |  |  | 21 |  | x | NA
| 22 |  | x | Not Available |  |  |  | 22 |  | x | NA
| 23 |  | x | Not Available |  |  |  | 23 |  | x | NA
| 24 |  | x | Not Available |  |  |  | 24 |  | x | NA
| 25 |  | x | Not Available |  |  |  | 25 |  | x | NA
| 26 |  | x | Not Available |  |  |  | 26 |  | x | NA
| 27 |  | x | Not Available |  |  |  | 27 |  | x | NA
| 28 |  | x | Not Available |  |  |  | 28 |  | x | NA
| 29 |  | x | Not Available |  |  |  | 29 |  | x | NA
| 30 |  | x | Not Available |  |  |  | 30 |  | x | NA
| 31 |  | x | Not Available |  |  |  | 31 |  | x | NA
# 89 | MADC ASSIGNMENTS FOR NuMI MINOS Service Building, MADC #1, Crate $E7 N23, Rack MSB101
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #89, Crate $E7 N23, Rack MSB101 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 |  | x | Not Available |  |  |  | 32 |  | x | NA
| 33 |  | x | Not Available |  |  |  | 33 |  | x | NA
| 34 |  | x | Not Available |  |  |  | 34 |  | x | NA
| 35 |  | x | Not Available |  |  |  | 35 |  | x | NA
| 36 |  | x | Not Available |  |  |  | 36 |  | x | NA
| 37 |  | x | Not Available |  |  |  | 37 |  | x | NA
| 38 |  | x | Not Available |  |  |  | 38 |  | x | NA
| 39 |  | x | Not Available |  |  |  | 39 |  | x | NA
| 40 |  | x | Not Available |  |  |  | 40 |  | x | NA
| 41 |  | x | Not Available |  |  |  | 41 |  | x | NA
| 42 |  | x | Not Available |  |  |  | 42 |  | x | NA
| 43 |  | x | Not Available |  |  |  | 43 |  | x | NA
| 44 |  | x | Not Available |  |  |  | 44 |  | x | NA
| 45 |  | x | Not Available |  |  |  | 45 |  | x | NA
| 46 |  | x | Not Available |  |  |  | 46 |  | x | NA
| 47 |  | x | Not Available |  |  |  | 47 |  | x | NA
| 48 |  | x | Not Available |  |  |  | 48 |  | x | NA
| 49 |  | x | Not Available |  |  |  | 49 |  | x | NA
| 50 |  | x | Not Available |  |  |  | 50 |  | x | NA
| 51 |  | x | Not Available |  |  |  | 51 |  | x | NA
| 52 |  | x | Not Available |  |  |  | 52 |  | x | NA
| 53 |  | x | Not Available |  |  |  | 53 |  | x | NA
| 54 |  | x | Not Available |  |  |  | 54 |  | x | NA
| 55 |  | x | Not Available |  |  |  | 55 |  | x | NA
| 56 |  | x | Not Available |  |  |  | 56 |  | x | NA
| 57 |  | x | Not Available |  |  |  | 57 |  | x | NA
| 58 |  | x | Not Available |  |  |  | 58 |  | x | NA
| 59 |  | x | Not Available |  |  |  | 59 |  | x | NA
| 60 |  | x | Not Available |  |  |  | 60 |  | x | NA
| 61 |  | x | Not Available |  |  |  | 61 |  | x | NA
| 62 |  | x | Not Available |  |  |  | 62 |  | x | NA
| 63 |  | x | Not Available |  |  |  | 63 |  | x | NA
# 90 | MADC ASSIGNMENTS FOR NuMI MINOS Underground - Detector Hall, MADC #2, Crate $E8 N23, Rack MND101
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #90, Crate $E8 N23, Rack MND101 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 | x |  | Not Available |  | E:NDMAGF | ND Magnet PS Reference | 0 | x |  | NA | E:NDMAGF | ND Magnet PS Reference
| 1 | x |  | Not Available |  |  |  | 1 | x |  | NA
| 2 | x |  | Not Available |  |  |  | 2 | x |  | NA
| 3 | x |  | Not Available |  |  |  | 3 | x |  | NA
| 4 | x |  | Not Available |  |  |  | 4 | x |  | NA
| 5 | x |  | Not Available |  |  |  | 5 | x |  | NA
| 6 | x |  | Not Available |  |  |  | 6 | x |  | NA
| 7 | x |  | Not Available |  |  |  | 7 | x |  | NA
| 8 | x |  | Not Available |  |  |  | 8 | x |  | NA
| 9 | x |  | Not Available |  |  |  | 9 | x |  | NA
| 10 | x |  | Not Available |  |  |  | 10 | x |  | NA
| 11 | x |  | Not Available |  |  |  | 11 | x |  | NA
| 12 | x |  | Not Available |  |  |  | 12 | x |  | NA
| 13 | x |  | Not Available |  |  |  | 13 | x |  | NA
| 14 | x |  | Not Available |  |  |  | 14 | x |  | NA
| 15 | x |  | Not Available |  |  |  | 15 | x |  | NA
| 16 | x |  | Not Available |  |  |  | 16 | x |  | NA
| 17 | x |  | Not Available |  |  |  | 17 | x |  | NA
| 18 | x |  | Not Available |  |  |  | 18 | x |  | NA
| 19 | x |  | Not Available |  |  |  | 19 | x |  | NA
| 20 | x |  | Not Available |  |  |  | 20 | x |  | NA
| 21 | x |  | Not Available |  |  |  | 21 | x |  | NA
| 22 | x |  | Not Available |  |  |  | 22 | x |  | NA
| 23 | x |  | Not Available |  |  |  | 23 | x |  | NA
| 24 | x |  | Not Available |  |  |  | 24 | x |  | NA
| 25 | x |  | Not Available |  |  |  | 25 | x |  | NA
| 26 | x |  | Not Available |  |  |  | 26 | x |  | NA
| 27 | x |  | Not Available |  |  |  | 27 | x |  | NA
| 28 | x |  | Not Available |  |  |  | 28 | x |  | NA
| 29 | x |  | Not Available |  |  |  | 29 | x |  | NA
| 30 | x |  | Not Available |  |  |  | 30 | x |  | NA
| 31 | x |  | Not Available |  |  |  | 31 | x |  | NA
# 90 | MADC ASSIGNMENTS FOR NuMI MINOS Underground - Detector Hall, MADC #2, Crate $E8 N23, Rack MND101
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #90, Crate $E8 N23, Rack MND101 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 |  | x | Not Available |  | E:NDMAG | ND Magnet PS Current | 32 |  | x | NA | E:NDMAG | ND Magnet PS Current
| 33 |  | x | Not Available |  | E:NDMAGV | ND Magnet PS Voltage | 33 |  | x | NA | E:NDMAGV | ND Magnet PS Voltage
| 34 |  | x | Not Available |  |  |  | 34 |  | x | NA
| 35 |  | x | Not Available |  |  |  | 35 |  | x | NA
| 36 |  | x | Not Available |  |  |  | 36 |  | x | NA
| 37 |  | x | Not Available |  |  |  | 37 |  | x | NA
| 38 |  | x | Not Available |  |  |  | 38 |  | x | NA
| 39 |  | x | Not Available |  |  |  | 39 |  | x | NA
| 40 |  | x | Not Available |  |  |  | 40 |  | x | NA
| 41 |  | x | Not Available |  |  |  | 41 |  | x | NA
| 42 |  | x | Not Available |  |  |  | 42 |  | x | NA
| 43 |  | x | Not Available |  |  |  | 43 |  | x | NA
| 44 |  | x | Not Available |  |  |  | 44 |  | x | NA
| 45 |  | x | Not Available |  |  |  | 45 |  | x | NA
| 46 |  | x | Not Available |  |  |  | 46 |  | x | NA
| 47 |  | x | Not Available |  |  |  | 47 |  | x | NA
| 48 |  | x | Not Available |  |  |  | 48 |  | x | NA
| 49 |  | x | Not Available |  |  |  | 49 |  | x | NA
| 50 |  | x | Not Available |  |  |  | 50 |  | x | NA
| 51 |  | x | Not Available |  |  |  | 51 |  | x | NA
| 52 |  | x | Not Available |  |  |  | 52 |  | x | NA
| 53 |  | x | Not Available |  |  |  | 53 |  | x | NA
| 54 |  | x | Not Available |  |  |  | 54 |  | x | NA
| 55 |  | x | Not Available |  |  |  | 55 |  | x | NA
| 56 |  | x | Not Available |  |  |  | 56 |  | x | NA
| 57 |  | x | Not Available |  |  |  | 57 |  | x | NA
| 58 |  | x | Not Available |  |  |  | 58 |  | x | NA
| 59 |  | x | Not Available |  |  |  | 59 |  | x | NA
| 60 |  | x | Not Available |  |  |  | 60 |  | x | NA
| 61 |  | x | Not Available |  |  |  | 61 |  | x | NA
| 62 |  | x | Not Available |  |  |  | 62 |  | x | NA
| 63 |  | x | Not Available |  |  |  | 63 |  | x | NA
# 91 | MADC ASSIGNMENTS FOR NuMI MINOS Underground - Absorber Area, MADC #3, Crate $E9 N23, Rack AAT103
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #91, Crate $E9 N23, Rack AAT103 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 0 | x |  | Not Available |  | E:HMHV1 | Hadron Mon HV PS 1 | 0 | x |  | NA | E:HMHV1 | Hadron Mon HV PS 1
| 1 | x |  | Not Available |  | E:HMHV2 | Hadron Mon HV PS 2 | 1 | x |  | NA | E:HMHV2 | Hadron Mon HV PS 2
| 2 | x |  | Not Available |  | E:HMHV3 | Hadron Mon HV PS 3 | 2 | x |  | NA | E:HMHV3 | Hadron Mon HV PS 3
| 3 | x |  | Not Available |  | E:HMHV4 | Hadron Mon HV PS 4 | 3 | x |  | NA | E:HMHV4 | Hadron Mon HV PS 4
| 4 | x |  | Not Available |  | E:HMHV5 | Hadron Mon HV PS 5 | 4 | x |  | NA | E:HMHV5 | Hadron Mon HV PS 5
| 5 | x |  | Not Available |  | E:HMHV6 | Hadron Mon HV PS 6 | 5 | x |  | NA | E:HMHV6 | Hadron Mon HV PS 6
| 6 | x |  | Not Available |  | E:HMHV7 | Hadron Mon HV PS 7 | 6 | x |  | NA | E:HMHV7 | Hadron Mon HV PS 7
| 7 | x |  | Not Available |  | E:MM1HV1 | Alcv 1 MMon HV PS 1 | 7 | x |  | NA | E:MM1HV1 | Alcv 1 MMon HV PS 1
| 8 | x |  | Not Available |  | E:MM1HV2 | Alcv 1 MMon HV PS 2 | 8 | x |  | NA | E:MM1HV2 | Alcv 1 MMon HV PS 2
| 9 | x |  | Not Available |  | E:MM1HV3 | Alcv 1 MMon HV PS 3 | 9 | x |  | NA | E:MM1HV3 | Alcv 1 MMon HV PS 3
| 10 | x |  | Not Available |  | E:MM2HV1 | Alcv 2 MMon HV PS 1 | 10 | x |  | NA | E:MM2HV1 | Alcv 2 MMon HV PS 1
| 11 | x |  | Not Available |  | E:MM2HV2 | Alcv 2 MMon HV PS 2 | 11 | x |  | NA | E:MM2HV2 | Alcv 2 MMon HV PS 2
| 12 | x |  | Not Available |  | E:MM2HV3 | Alcv 2 MMon HV PS 3 | 12 | x |  | NA | E:MM2HV3 | Alcv 2 MMon HV PS 3
| 13 | x |  | Not Available |  | E:MM3HV1 | Alcv 3 MMon HV PS 1 | 13 | x |  | NA | E:MM3HV1 | Alcv 3 MMon HV PS 1
| 14 | x |  | Not Available |  | E:MM3HV2 | Alcv 3 MMon HV PS 2 | 14 | x |  | NA | E:MM3HV2 | Alcv 3 MMon HV PS 2
| 15 | x |  | Not Available |  | E:MM3HV3 | Alcv 3 MMon HV PS 3 | 15 | x |  | NA | E:MM3HV3 | Alcv 3 MMon HV PS 3
| 16 | x |  | Not Available |  | E:HMGPR | HadMon Rack Gas Pres | 16 | x |  | NA | E:HMGPR | HadMon Rack Gas Pres
| 17 | x |  | Not Available |  | E:HMGPD | HadMon Detector Gas Pres | 17 | x |  | NA | E:HMGPD | HadMon Detector Gas Pres
| 18 | x |  | Not Available |  | E:MM1GPR | AL1 MM Rack Gas Pres | 18 | x |  | NA | E:MM1GPR | AL1 MM Rack Gas Pres
| 19 | x |  | Not Available |  | E:MM1GPD | AL1 MM Detector Gas Pres | 19 | x |  | NA | E:MM1GPD | AL1 MM Detector Gas Pres
| 20 | x |  | Not Available |  | E:MM2GPR | AL2 MM Rack Gas Pres | 20 | x |  | NA | E:MM2GPR | AL2 MM Rack Gas Pres
| 21 | x |  | Not Available |  | E:MM2GPD | AL2 MM Detector Gas Pres | 21 | x |  | NA | E:MM2GPD | AL2 MM Detector Gas Pres
| 22 | x |  | Not Available |  | E:MM3GPR | AL3 MM Rack Gas Pres | 22 | x |  | NA | E:MM3GPR | AL3 MM Rack Gas Pres
| 23 | x |  | Not Available |  | E:MM3GPD | AL3 MM Detector Gas Pres | 23 | x |  | NA | E:MM3GPD | AL3 MM Detector Gas Pres
| 24 | x |  | Not Available |  | E:TTHADM | NuMI Hadron Mon Temp | 24 | x |  | NA | E:TTHADM | NuMI Hadron Mon Temp
| 25 | x |  | Not Available |  | E:TTMA1 | NuMI Muon Alcove 1 Temp | 25 | x |  | NA | E:TTMA1 | NuMI Muon Alcove 1 Temp
| 26 | x |  | Not Available |  | E:TTMA2 | NuMI Muon Alcove 2 Temp | 26 | x |  | NA | E:TTMA2 | NuMI Muon Alcove 2 Temp
| 27 | x |  | Not Available |  | E:TTMA3 | NuMI Muon Alcove 3 Temp | 27 | x |  | NA | E:TTMA3 | NuMI Muon Alcove 3 Temp
| 28 | x |  | Not Available |  | E:TTAATU | NuMI Upper AAT Temp | 28 | x |  | NA | E:TTAATU | NuMI Upper AAT Temp
| 29 | x |  | Not Available |  | E:THAATU | NuMI Upper AAT Humidity | 29 | x |  | NA | E:THAATU | NuMI Upper AAT Humidity
| 30 | x |  | Not Available |  | E:TTAATL | NuMI Lower AAT Temp | 30 | x |  | NA | E:TTAATL | NuMI Lower AAT Temp
| 31 | x |  | Not Available |  | E:THAATL | NuMI Lower AAT Humidity | 31 | x |  | NA | E:THAATL | NuMI Lower AAT Humidity
# 91 | MADC ASSIGNMENTS FOR NuMI MINOS Underground - Absorber Area, MADC #3, Crate $E9 N23, Rack AAT103
| ENTERED for NuMI |  |  |  |  | or ALREADY ENTERED BY OTHERS |  | ASSIGNMENT DESIRED for NuMI - Including Reassignment of Others
MADC #91, Crate $E9 N23, Rack AAT103 | Chan | BNC | Twin | PCI | SAT | Name | Description ( 24 Characters Max ) | Chan | BNC | Twin | PCI | Name | Description
| 32 | x |  | Not Available |  | E:HMGF | HadMon Detector Gas Flow | 32 | x |  | NA | E:HMGF | HadMon Detector Gas Flow
| 33 | x |  | Not Available |  | E:MM1GF | AL1 MM Detector Gas Flow | 33 | x |  | NA | E:MM1GF | AL1 MM Detector Gas Flow
| 34 | x |  | Not Available |  | E:MM2GF | AL2 MM Detector Gas Flow | 34 | x |  | NA | E:MM2GF | AL2 MM Detector Gas Flow
| 35 | x |  | Not Available |  | E:MM3GF | AL3 MM Detector Gas Flow | 35 | x |  | NA | E:MM3GF | AL3 MM Detector Gas Flow
| 36 | x |  | Not Available |  | E:MGO2I | Monitor Gas O2 Impurity | 36 | x |  | NA | E:MGO2I | Monitor Gas O2 Impurity
| 37 | x |  | Not Available |  | E:MGSP | Monitor Gas Supply Pres | 37 | x |  | NA | E:MGSP | Monitor Gas Supply Pres
| 38 | x |  | Not Available |  |  |  | 38 | x |  | NA | E:HMMRCI | Had/Muon Mon Ref Chambr I
| 39 | x |  | Not Available |  | E:HMRTD | Hadron Monitor RTD | 39 | x |  | NA | E:HMRTD | Hadron Monitor RTD
| 40 | x |  | Not Available |  | E:MM1RTD | Muon Mon Alcove 1 RTD | 40 | x |  | NA | E:MM1RTD | Muon Mon Alcove 1 RTD
| 41 | x |  | Not Available |  | E:MM2RTD | Muon Mon Alcove 2 RTD | 41 | x |  | NA | E:MM2RTD | Muon Mon Alcove 2 RTD
| 42 | x |  | Not Available |  | E:MM3RTD | Muon Mon Alcove 3 RTD | 42 | x |  | NA | E:MM3RTD | Muon Mon Alcove 3 RTD
| 43 | x |  | Not Available |  |  |  | 43 | x |  | NA
| 44 | x |  | Not Available |  |  |  | 44 | x |  | NA
| 45 | x |  | Not Available |  |  |  | 45 | x |  | NA
| 46 | x |  | Not Available |  |  |  | 46 | x |  | NA
| 47 | x |  | Not Available |  |  |  | 47 | x |  | NA
| 48 | x |  | Not Available |  |  |  | 48 | x |  | NA
| 49 | x |  | Not Available |  |  |  | 49 | x |  | NA
| 50 | x |  | Not Available |  |  |  | 50 | x |  | NA
| 51 | x |  | Not Available |  |  |  | 51 | x |  | NA
| 52 | x |  | Not Available |  |  |  | 52 | x |  | NA
| 53 | x |  | Not Available |  |  |  | 53 | x |  | NA
| 54 | x |  | Not Available |  |  |  | 54 | x |  | NA
| 55 | x |  | Not Available |  |  |  | 55 | x |  | NA
| 56 | x |  | Not Available |  |  |  | 56 | x |  | NA
| 57 | x |  | Not Available |  |  |  | 57 | x |  | NA
| 58 | x |  | Not Available |  |  |  | 58 | x |  | NA
| 59 | x |  | Not Available |  |  |  | 59 | x |  | NA
| 60 | x |  | Not Available |  |  |  | 60 | x |  | NA
| 61 | x |  | Not Available |  |  |  | 61 | x |  | NA
| 62 | x |  | Not Available |  |  |  | 62 | x |  | NA
| 63 | x |  | Not Available |  |  |  | 63 | x |  | NA

## Overall Requirements
CONTROLS REQUIREMENTS FOR NuMI
2005-08-10
Ref # | System / Device | Name | Controller | MADC Twinax | MADC BNC/TWIN | MADC BNC | Beam Permit | Controls Assignments | Comments | Contact
MI-60 Service Building - South " 60S" | [8 empty] | Existing Controls Infrastructure is Thought to be Adequate Here for NuMI Requirements.
1 | Single Turn Extraction Kicker | I:KPS6N | 466 | 3 |  | 1 | 4A 1D | CC $63 N7 | PS in South PS Room. Controls for PS in South Equipment Room. ~MI60124 | Chris Jensen
2 | Main Injector Performance Parameters | [7 empty] | Alberto is the Lead Here and Will Be Joined by Others | Alberto Marchionni
2-1 | Beam in the NuMI Kicker Gap Before NuMI Extraction (Unwanted Beam from P-Bar Production or Misplaced Beam) | I:BNKG | Custom |  |  | 1 | 1A 1D | I:BNKGST Associated Sample Time | Planning on a Direct Connection to the 200 Module as Well as Supervision by C204/PCI. Alexei's Hardware in Rack MI60004. | Alberto March. Alexei Semenov
2-2 | P-Bar Extraction Through P150 Line Not Exceptionally Lossy | I:LM701 I:LM702 I:LM703 I:LM707 I:LM708 |  |  |  | 5 |  |  | Channels Relocated to MADC #65, Channels 0 to 4 to Get Really Fast Service. In Consultation with Sam Childress on May 31, 2005, Decided NOT to Have the Beam Permit System Monitor these P1 Line Loss Monitors. | Alberto Marchionni
3 | Flourinert Cooling System with Local PID Controller | I:K6COOL | 217 | 10 |  |  | 3A | CC $63 N8 | Skid in South Power Supply Room | Chris Jensen Scott Reeves
4 | NuMI Clock Event Scaler |  | 333 |  |  |  |  | CC $63 N17 | Custom Configured Module 333 Version 7.0 | Rupe Crouch Bob Ducar
4-1 | NuMI Beam Cycle Counter | E:NBCCNT | [5 empty] | CC $63 N17 A(0) | $A5->$19->$52->$22->$A9 | Rupe Crouch Bob Ducar
4-2 | Begin NuMI Cycle (Coincident with Main Injector $23 Reset) | E:EA5CNT | [5 empty] | CC $63 N17 A(1) | $A5 | Rupe Crouch Bob Ducar
4-3 | Booster Beam Reset for NuMI (With or Without Actual Beam) | E:E19CNT | [5 empty] | CC $63 N17 A(2) | 19 | Rupe Crouch Bob Ducar
4-4 | Booster Beam Reset for NuMI (With Actual Beam) | E:E19BMC | [5 empty] | CC $63 N17 A(3) | $19 -> $52 | Rupe Crouch Bob Ducar
4-5 | NuMI Cycle Sample Time | E:EA4CNT | [5 empty] | CC $63 N17 A(4) | $A4 | Rupe Crouch Bob Ducar
4-6 | Reflected MIBS $74 (Extract NuMI Beam from Main Injector) | E:EEA9CNT | [5 empty] | CC $63 N17 A(5) | $A9 | Rupe Crouch Bob Ducar
4-7 | NuMI Beam Permit Fall (Transition to Inhibit Beam) | E:EA6CNT | [5 empty] | CC $63 N17 A(6) | $A6 | Rupe Crouch Bob Ducar
4-8 | NuMI Beam Permit Sytem Reset (Event Issued Twice Upon Reset) | E:EA8CNT | [5 empty] | CC $63 N17 A(7) | $A8 (Parameter has Scaling of 0.5) | Rupe Crouch Bob Ducar
4-9 | Reset All Above Parameters to Zero Count | E:NCECR | [5 empty] | CC $63 N17 |  | Kent Triplett Bob Ducar
5 | NuMI Clock Event Scaler |  | 333 |  |  |  |  | CC $63 N16 | Custom Configured Module 333 Version 10.0 | Kent Triplett Rupe Crouch
5-1 | I:BNKG NuMI Beam Permit C200 Input Trip Counter | I:BNKGCT | 333 |  |  |  |  | CC $63 N16 A(7) |  | Kent Triplett Rupe Crouch
6 | MIBS Timing Channel Ref $74 | I:K6NKD0 | 479 |  |  |  |  | CC $63 N20 A(0) | Actually Fires the Kicker. NuMI BP ANDed with Pulse Output within the Module. | Greg Vogel Bob Ducar
7 | TCLK Timer: MIBS $74 Request, Ref $A5 | I:MINX | 377 |  |  |  |  | CC $94 N3 A2 | Channel Already Assigned by Vogel | Chris Jensen Greg Vogel
8 | TCLK Timer |  | 377 |  |  |  |  | CC $63 N19 | May Not Be Needed If Other Channels Are Free | Greg Vogel Bob Ducar
9 | Digital In - Digital Out Facility |  | 284 |  |  |  |  | CC $63 N1 | Potential for Control and Monitor of Local Systems. May Be Needed for Flourinert Cooling System. | Greg Vogel Bob Ducar
10 | MADC Facility - Existing in Rack MI60124 | MADC #65 | 290 |  |  |  |  | CC $63 N23 | 14 Bit Resolution MADC Is Required Here and Is Already Installed. Lots of Free Channels Currently Available. | Ryan Hagler Rupe Crouch
11 | NuMI Beam Permit |  | 200 |  |  |  |  | CC $63 N22 | This Location is the End of the Beam Permit "Loop". Location of 201 is at MINOS Service Building. | Greg Vogel Bob Ducar
11-1 | Radiation Safety System Beam Permit Input | [5 empty] | 1D |  | Best Location for Connection to Beam Permit System | Chuck Worel Bob Ducar
12 | Beam Permit Process Channel Interface and Controller |  | 204 | Connects to MADC #65 |  |  | 1D | CC $63 N21 | Output to Local 200 Beam Permit Module. | Al Franck Bob Ducar
13 | Ethernet Connectivity | [7 empty] | Already Exists at this Location | Dan Stenman
14 | VME with Connection to Ethernet | [7 empty] | Already Exists at this Location | Dan Stenman
15 | ACNET Console X Terminal | [7 empty] | Already Exists at this Location | Dan Stenman
MI-60 Service Bldg - North "60N" | [8 empty] | Existing Controls Infrastructure is Thought to be Adequate Here for Most NuMI Requirements.
1 | Lambertson Power Supply for LAM60 | I:LAM60 | 468 | 5 ** |  |  | 3A 1D | CC $73 N2-3 | 500 kW PEI in North Equipment Gallery with Output Filter. Ramped. Critical Device | Steve Hays
2 | Lambertson Power Supply for LAM61A and LAM61B | I:LAM61 | 468 | 6 *** |  |  | 3A 1D | CC $73 N4-5 | 500 kW PEI in North Equipment Gallery with Output Filter. Ramped. Critical Device | Steve Hays
3 | C Magnet Power Supply | E:V100 | 468 | 5 ** |  |  | 3A 1D | CC $73 N6-7 | 500 kW PEI in North Equipment Gallery with Output Filter. Ramped. | Steve Hays
4 | EPB Dipole String (6) | E:HV101 | 468 | 8 **** |  |  | 3A 1D | CC $73 N8-9 | Two Series 500 kW PEIs in North Equipment Gallery with Output Filter. Ramped. Critical Device | Steve Hays
4-1 | Local PLC for Extended Power Supply Status | [7 empty] | Status Supplied to Associated 468 Module | Steve Hays
5 | Quadrupole Power Supply (3Q120) | E:QD101 | 466 | 4 * |  |  | 2A | CC $73 N10 | 20 kW PEI. In North Equipment Gallery. | Steve Hays
6 | Quadrupole Power Supply (3Q120) | E:QF102 | 466 | 4 * |  |  | 2A | CC $73 N11 | 20 kW PEI. In North Equipment Gallery. | Steve Hays
7 | Quadrupole Power Supply (3Q120) | E:QD103 | 466 | 4 * |  |  | 2A | CC $73 N12 | 20 kW PEI. In North Equipment Gallery. | Steve Hays
8 | Quadrupole Power Supply (3Q60) | E:QF104 | 466 | 4 * |  |  | 2A | CC $73 N13 | 20 kW PEI. In North Equipment Gallery. Not Planning to Ramp this Quad. | Steve Hays
9 | Quadrupole Power Supply (3Q120) | E:QF105 | 466 | 4 * |  |  | 2A | CC $73 N14 | 20 kW PEI. In North Equipment Gallery. | Steve Hays
10 | Quadrupole Power Supply (3Q120) | E:QD106 | 466 | 4 * |  |  | 2A | CC $73 N15 | 20 kW PEI. In North Equipment Gallery. | Steve Hays
| Spare 20 kW PEI Controller Formerly Dedicated to E:H104 | Spare | 466 | 4 * |  |  | 2A | CC $73 N16 | 20 kW PEI. In North Equipment Gallery. Being Decommissioned in Favor of E:HT104 | Steve Hays
* | MADC #38 Monitors for Q101 thru Q106 | Current Reference (F), Current Out, Current Error (E) and Voltage Out (V). First Two Analog Monitors Examined by Beam Permit.
** | MADC #38 Monitors for LAM60 and V100 | Current Reference (F), Current Out, Current Error (E), Unfiltered Voltage Out (U), and Filtered Voltage Out (V). First Three Monitors Examined by Beam Permit. "In Regulation" Digital Status Also to Beam Permit.
*** | MADC #38 Monitors for LAM61 | Current Reference (F), Current Out, Current Error (E), Plus Volts to Gnd (P), Neg Volts to Gnd (N), and Filtered Voltage Out (V). First Three Monitors Examined by Beam Permit. "In Regulation" Digital Status Also to Beam Permit.
**** | MADC #38 Monitors for HV101 | Current Reference (F), Current Out, Current Error (E), Plus Volts to Gnd (P), Neg Volts to Gnd (N), Filtered Voltage Out (V), and 2 x Unfiltered Voltage Out (AU & BU). First Three Monitors Examined by Beam Permit. "In Regulation" Digital Status Also to Beam Permit.
11 | Trim Element Regulators (11) | The CAMAC 453 Slot Assignments Reflect a Reordering Suggested by Leon Bartelson to Align Controls Modules with Regulator Placement. | [6 empty] | These Trims Elements Controlled from Existing MI Regulator System at MI-60 North in Equipment Rack MI60205 | Leon Bartelson
11-1 | Horizontal Trim Element #1 Located Upstream of HV101-1 EPB Dipole | E:HT101 | .25 x 453 | 4 * |  |  | No | CC $74 N12-13 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
11-2 | Vertical Trim Element #2 Located Upstream of Q103 | E:VT103 | .25 x 453 | 4 * |  |  | No | CC $74 N12-13 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
11-3 | Horizontal Trim Element #3 Located Downstream of Q105 | E:HT105 | .25 x 453 | 4 * |  |  | No | CC $74 N12-13 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
11-4 | Vertical Trim Element #4 Located Downstream of Q106 | E:VT106 | .25 x 453 | 4 * |  |  | No | CC $74 N12-13 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
11-5 | Horizontal Trim Element #5 Located Downstream of Q107 | E:HT107 | .25 x 453 | 4 * |  |  | No | CC $74 N14-15 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
11-6 | Vertical Trim Element #6 Located Upstream of Q108 | E:VT108 | .25 x 453 | 4 * |  |  | No | CC $74 N14-15 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
11-7 | Horizontal Trim Element #7 Located Upstream of Q109 | E:HT109 | .25 x 453 | 4 * |  |  | No | CC $74 N14-15 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
11-8 | Vertical Trim Element #8 Located Upstream of Q110 | E:VT110 | .25 x 453 | 4 * |  |  | No | CC $74 N14-15 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
11-9 | Vertical Trim Element #9 Located Upstream of Q111 | E:VT111 | .25 x 453 | 4 * |  |  | No | CC $74 N16-17 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
11-10 | Horizontal Trim Element #10 Located Upstream of Q112 | E:HT112 | .25 x 453 | 4 * |  |  | No | CC $74 N16-17 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
11-11 | Horizontal Trim Element #11 Located Downstream of Q104 | E:HT104 | .25 x 453 | 4 * |  |  | No | CC $74 N16-17 | This Spare Channel Now Assigned to HT104 to Attain Bipolar Operation of the Trim | Leon Bartelson
11-12 | Spare Channel |  | .25 x 453 |  |  |  |  | CC $74 N16-17 |  | Leon Bartelson
11-13 | Trim Element Bulk Power Supply Voltage Output | I:CPS6NV |  |  |  | 1 | 1A | MADC #44 | Tee Off Existing Monitor Channel | Leon Bartelson
* | MADC Monitors for Trim Elements | All MADC Monitors Wire Directly to MADC #77 in Rack MI60205. Analog Monitors Include: Vref, Vout, I out, I rms. "Tracking" Status Bit Not Readily Available for Examination by Beam Permit. Installation of 204/PCI Not Viewed Favorably. Consider an ACNET Software Solution to Solving Beam Permit Problem.
12 | Beam Position Detectors (13 Total) | [7 empty] | Located Here at MI-60N to Save 8K Ft of Cable. Using 3/8" Andrew Heliax LDF2RN-50 Cable. Suggest Positioning VME Crate in Rack MI60203. | Peter Prieto Sam Childress
12-1 | Vertical BPM Downstream of Q101 | E:VP101 | VME Ethrnt |  |  |  | No |  | Four BPMs per VME Module | Peter Prieto Sam Childress
12-2 | Horizontal BPM Downstream of Q101 | E:HP101 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
12-3 | Horizontal BPM Downstream of Q102 | E:HP102 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
12-4 | Vertical BPM Downstream of Q103 | E:VP103 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
12-5 | Horizontal BPM Upstream of Q104 | E:HP104 | VME Ethrnt |  |  |  | No |  | Four BPMs per VME Module | Peter Prieto Sam Childress
12-6 | Horizontal BPM Upstream of Q105 | E:HP105 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
12-7 | Vertical BPM Upstream of Q106 | E:VP106 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
12-8 | Horizontal BPM Upstream of Q107 | E:HP107 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
12-9 | Vertical BPM Upstream of Q108 | E:VP108 | VME Ethrnt |  |  |  | No |  | Four BPMs per VME Module | Peter Prieto Sam Childress
12-10 | Horizontal BPM Downstream of Q109 | E:HP109 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
12-11 | Vertical BPM Downstream of Q110 | E:VP110 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
12-12 | Vertical BPM Downstream of Q111 | E:VP111 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
12-13 | Horizontal BPM Downstream of Q112 | E:HP112 | VME Ethrnt |  |  |  | No |  | Four BPMs per VME Module | Peter Prieto Sam Childress
13 | Main Injector Beam Position Detectors for Orbit Verification (4 Total) | [8 empty] | Peter Prieto Duane Voy Sam Childress
13-1 | Horizontal Position at Q606 for MI Orbit Verification Before NuMI Extraction | I:HP606N I:HI606N | VME Ethrnt | 2 |  |  | 1 | MADC #44 | VME Crate Located in Rack MI60210 | Peter Prieto Duane Voy Sam Childress
13-2 | Vertical Position at Q607 for MI Orbit Verification Before NuMI Extraction | I:VP607N I:VI607N | VME Ethrnt | 2 |  |  | 2 | MADC #44 | VME Crate Located in Rack MI60210 | Peter Prieto Duane Voy Sam Childress
13-3 | Horizontal Position at Q608 for MI Orbit Verification Before NuMI Extraction | I:HP608N I:HI608N | VME Ethrnt | 2 |  |  | 1 | MADC #44 | VME Crate Located in Rack MI60210 | Peter Prieto Duane Voy Sam Childress
13-4 | Vertical Position at Q609 for MI Orbit Verification Before NuMI Extraction | I:VP609N I:VI609N | VME Ethrnt | 2 |  |  | 1 | MADC #44 | VME Crate Located in Rack MI60210 | Peter Prieto Duane Voy Sam Childress
14 | Profile Monitors (5 Total) |  |  | Equipment Mostly in Rack MI60218. | [5 empty] | Sacha Kopp Gianni Tassotto Dan Schoo
14-1 | Profile Monitor Downstream of Q101 | E:PM101 (E:M101DS) | ARCNET VME Ethrnt |  |  |  | No |  |  | Sacha Kopp Al Franck
14-2 | Profile Monitor Upstream of Q105 | E:PM105 (E:M105DS) | ARCNET VME Ethrnt |  |  |  | No |  |  | Sacha Kopp Al Franck
14-3 | Profile Monitor Upstream of Q107 | E:PM107 (E:M107DS) | ARCNET VME Ethrnt |  |  |  | No |  |  | Sacha Kopp Al Franck
14-4 | Profile Monitor Upstream of Q108 | E:PM108 (E:M108DS) | ARCNET VME Ethrnt |  |  |  | No |  |  | Sacha Kopp Al Franck
14-5 | Reserved for Possible Future Profile Monitor PM111 | E:PM111 | ARCNET VME Ethrnt | [5 empty] | Cables Pulled for Motion Control But No Cables for Signals at this Time. | Sacha Kopp Al Franck
14-6 | Profile Monitor Downstream of Q112 | E:PM112 (E:M112DS) | ARCNET VME Ethrnt |  |  |  | No |  |  | Sacha Kopp Al Franck
14-7 | Clearing Voltage PS for PM101 | E:PM101V | .25 x 052 |  |  | 1 | No | CC $70 N7 A0 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Dan Schoo
14-8 | Clearing Voltage PS for PM105 | E:PM105V | .25 x 052 |  |  | 1 | No | CC $70 N7 A1 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Dan Schoo
14-9 | Clearing Voltage PS for PM107 | E:PM107V | .25 x 052 |  |  | 1 | No | CC $70 N7 A2 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Dan Schoo
14-10 | Clearing Voltage PS for PM108 | E:PM108V | .25 x 052 |  |  | 1 | No | CC $70 N7 A3 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Dan Schoo
14-11 | Clearing Voltage PS for Possible Future Profile Monitor PM111 | E:PM111V | .25 x 052 |  |  |  |  | CC $70 N8 A1 | Cable Pulled | Sacha Kopp Dan Schoo
14-12 | Clearing Voltage PS for PM112 | E:PM112V | .25 x 052 |  |  | 1 | No | CC $70 N8 A0 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Dan Schoo
15 | Loss Monitors (Chassis #1) | [7 empty] | Reg Loss Monitor Electronics Packages 12 Channels in One Chassis with HV Supply. Located in Rack MI60226 to Connect Outputs to MADC #44. | Gianni Tassotto Marv Olson
15-1 | Regular Loss Monitor HV Supply Output Chassis #1 | E:LMHV1O |  |  |  | 1 | 1A |  | Nominally Set at 2,000 Volts | Gianni Tassotto Marv Olson
15-2 | Regular Loss Monitor HV Supply Return Chassis #1 | E:LMHV1R |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-3 | Loss Monitor #1 at KM602A | I:LMNKMA |  |  |  | 1 | 1A |  | Log Amp with 5 Decades (Typical) | Gianni Tassotto Marv Olson
15-4 | Loss Monitor #2 at KM602B | I:LMNKMB |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-5 | Loss Monitor #3 at KM602C | I:LMNKMC |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-6 | Loss Monitor #4 at LAM60 | I:LML60 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-7 | Loss Monitor #5 at LAM61A | I:LML61A |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-8 | Loss Monitor #6 at LAM61B | I:LML61B |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-9 | Loss Monitor #7 at V100 | E:LMV100 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-10 | Loss Monitor #8 at Q101 | E:LMQ101 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-11 | Loss Monitor #9 at HV101-1 | E:LM1011 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-12 | Loss Monitor #10 at HV101-2 | E:LM1012 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-13 | Loss Monitor #11 at Q102 | E:LMQ102 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16 | Loss Monitors (Chassis #2) | [7 empty] | Reg Loss Monitor Electronics Packages 12 Channels in One Chassis with HV Supply. Located in Rack MI60226 to Connect Outputs to MADC #44. | Gianni Tassotto Marv Olson
16-1 | Regular Loss Monitor HV Supply Output Chassis #2 | E:LMHV2O |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-2 | Regular Loss Monitor HV Supply Return Chassis #2 | E:LMHV2R |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-3 | Loss Monitor #1 at HV101-3 | E:LM1013 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-4 | Loss Monitor #2 at HV101-4 | E:LM1014 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-5 | Loss Monitor #3 at HV101-5 | E:LM1015 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-6 | Loss Monitor #4 at Q103 | E:LMQ103 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-7 | Loss Monitor #5 at HV101-6 | E:LM1016 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-8 | Loss Monitor #6 at Q104 | E:LMQ104 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-9 | Loss Monitor #7 at HT104 | E:LMHT04 |  |  |  | 1 | 1A |  | Formerly E:LMH104 | Gianni Tassotto Marv Olson
16-10 | Loss Monitor #8 at Q105 | E:LMQ105 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-11 | Loss Monitor #9 at Q106 | E:LMQ106 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-12 | Loss Monitor #10 at Q107 | E:LMQ107 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
17 | Main Injector Beam Quality Loss Monitors (Chassis #6) | [8 empty] | Gianni Tassotto Marv Olson
17-1 | Main Injector Beam Quality Loss Monitor HV Supply Output Chassis #6 | I:LMHV6O |  |  |  | 1 | 1A | MADC #44 |  | Gianni Tassotto Marv Olson
17-2 | Main Injector Beam Quality Loss Monitor HV Supply Return Chassis #6 | I:LMHV6R |  |  |  | 1 | 1A | MADC #44 |  | Gianni Tassotto Marv Olson
17-3 | MI Beam Quality Loss Monitor at Q608 Area | I:LMQ608 |  |  |  | 1 | 1A | MADC #44 |  | Gianni Tassotto Marv Olson
17-4 | MI Beam Quality Loss Monitor at Q612 Area | I:LMQ612 |  |  |  | 1 | 1A | MADC #44 |  | Gianni Tassotto Marv Olson
18 | Other Instrumentation
18-1 | Beam Intensity Toroid #1 - Upstream | E:TOR101 E:TR101D | NIM Module and a 284 |  |  | 1 | 1A | MADC #44 CC $70 N15 | Requires a 479 Timing Channel (CC $70 N17 A(0)) for Sampling at the Right Time. This Timer Or'd with a 377 Timing Channel (CC $70 N16 A(6)) to Clear/Calibrate Without Beam. | Peter Prieto Greg Vogel Dallas H.
18-2 | Magnetic Flux Sensors by HV101 String | E:FLXHn - E:FLXVn | Custom |  |  | 8 | No | MADC #59 |  | G. Koizumi Dan Schoo
18-3 | Temperature Sensors by HV101 String | E:NTMP1 - E:NTEM9 | Custom |  |  | 9 | No | MADC #44 |  | G. Koizumi Dan Schoo
19 | Vacuum (MI System Additions) |  | ARCNET VME Ethrnt | [5 empty] | Existing CIA Crate Located Here is Sufficient | Leon Bartelson Jim Klen
19-1 | 40 L/sec Ion Pumps (Quantity 12) | I:IPxxxx |  |  |  |  | No |  | 4 for Each of Three Lambertsons | Leon Bartelson Jim Klen
19-2 | Pirani Gauges | I:PGxxxx |  |  |  |  | No |  | Proximate to Lambertsons | Leon Bartelson Jim Klen
20 | TCLK Timing Capability |  | 377 |  |  |  |  | CC $70 N16 | For Local Instrumentation | Al Franck Bob Ducar
21 | MIBS Timing Capability |  | 479 |  |  |  |  | CC $70 N17 | Thought Useful for Instrumentation | Greg Vogel Bob Ducar
22 | MADC Facility - Existing in Rack MI60219 | MADC #38 | 290 |  |  |  |  | CC $73 N23 | 14 Bit Resolution MADC Is Required Here and Is Already Installed | Ryan Hagler Rupe Crouch
23 | MADC Facility - Existing in Rack MI60226 | MADC #44 | 290 |  |  |  |  | CC $70 N23 |  | Ryan Hagler Rupe Crouch
24 | MADC Facility - Existing in Rack MI60205 | MADC #77 | 290 |  |  |  |  | CC $74 N21 | Dedicated to Trim Elements | Ryan Hagler Rupe Crouch
25 | NuMI Beam Permit |  | 200 |  |  |  |  | CC $73 N22 | Already Installed | Greg Vogel Bob Ducar
26 | NuMI Beam Permit |  | 200 |  |  |  |  | CC $70 N19 | Relocated From CC $73 N21. | Greg Vogel Bob Ducar
27 | Beam Permit Process Channel Interface and Controller |  | 204 | Connects to MADC #38 |  |  | 1D | CC $73 N21 | Output to Local 200 Beam Permit Module. 30 Power Supply Monitor Channels. | Al Franck Bob Ducar
28 | Beam Permit Process Channel Interface and Controller |  | 204 | Connects to MADC #44 |  |  | 1D | CC $70 N18 | Output to Local 200 Beam Permit Module. 24 Loss Monitor Channels. | Al Franck Bob Ducar
29 | Ethernet Connectivity | [7 empty] | Already Exists at this Location | Dan Stenman
30 | VME with Connection to Ethernet | [7 empty] | Already Exists at this Location | Dan Stenman
31 | ACNET Console X Terminal | [7 empty] | Already Exists at this Location | Dan Stenman
MI-62 Service Building "62SB" | [8 empty] | Basic Controls Infrastructure is Present. Four New Racks (MI62111-114) Have Been Installed in Controls/Kicker Room. These Will Support Vacuum (111 & 112) and Instrumentation (113 & 114).
1 | B2 Dipole String (6) | E:V108 | 468 | 7 ** |  |  | 3A 1D | CC $6C N1-2 | A Relocated Main Ring Power Supply Will Accommodate This Load. Located in Power Supply Room. | Steve Hays
2 | Quadrupole Power Supply (3Q120) | E:QF107 | 466 | 4 * |  |  | 2A | CC $6C N3 | 20 kW PEI In Power Supply Room | Steve Hays
3 | Quadrupole Power Supply (3Q120) | E:QD108 | 466 | 4 * |  |  | 2A | CC $6C N4 | 20 kW PEI In Power Supply Room | Steve Hays
4 | Quadrupole Power Supply (3Q120) | E:QF109 | 466 | 4 * |  |  | 2A | CC $6C N5 | 20 kW PEI In Power Supply Room | Steve Hays
5 | Quadrupole Power Supply (3Q60) | E:QD110 | 466 | 4 * |  |  | 2A | CC $6C N6 | 20 kW PEI In Power Supply Room. Not Planning to Ramp this Quad. | Steve Hays
6 | Quadrupole Power Supply (3Q120) | E:QD111 | 466 | 4 * |  |  | 2A | CC $6C N7 | 20 kW PEI In Power Supply Room | Steve Hays
7 | Quadrupole Power Supply (3Q120) | E:QF112 | 466 | 4 * |  |  | 2A | CC $6C N8 | 20 kW PEI In Power Supply Room | Steve Hays
* | MADC #79 Monitors for Q107 thru Q112 | Current Reference (F), Current Out, Current Error (E) and Voltage Out (V). First Two Analog Monitors Examined by Beam Permit.
** | MADC #79 Monitors for V108 | Current Reference (F), Current Out, Current Error (E), Unfiltered Voltage Out (U), Filtered Voltage Out (V), Plus Volts to Gnd (P), and Neg Volts to Gnd (N). First Three Monitors Examined by Beam Permit. "In Regulation" Digital Status Also to Beam Permit.
8 | Loss Monitors (Chassis #3) | [7 empty] | Reg Loss Monitor Electronics Packages 12 Channels in One Chassis with HV Supply. Located in Rack MI62106 for Proximity to MADC #79. | Gianni Tassotto Marv Olson
8-1 | Regular Loss Monitor HV Supply Output Chassis #3 | E:LMHV3O |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-2 | Regular Loss Monitor HV Supply Return Chassis #3 | E:LMHV3R |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-3 | Loss Monitor #1 at Q108 | E:LMQ108 |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-4 | Loss Monitor #2 at V108-1 | E:LM1081 |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-5 | Loss Monitor #3 at V108-2 | E:LM1082 |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-6 | Loss Monitor #4 at Q109 | E:LMQ109 |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-7 | Loss Monitor #5 at V108-3 | E:LM1083 |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-8 | Loss Monitor #6 at V108-4 | E:LM1084 |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-9 | Loss Monitor #7 at Q110 | E:LMQ110 |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-10 | Loss Monitor #8 at V108-5 | E:LM1085 |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-11 | Loss Monitor #9 at V108-6 | E:LM1086 |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-12 | Loss Monitor #10 at Q111 | E:LMQ111 |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-13 | Loss Monitor #11 at Q112 | E:LMQ112 |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
8-14 | Loss Monitor #12 at Beginning of Big (12") Beam Pipe Downstream of Q112 | E:LMBBBP |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto Marv Olson
9 | Total Loss Monitors (4 Total) | [7 empty] | These TLMs Are Likely to be Inputs to Beam Loss Budget Monitor (BLBM) Facility - Especially E:TLMCTU. Suggest Location of Electronics in Rack MI62114. | Gianni Tassotto
9-1 | Total Loss Monitor #1 for NuMI Stub and Peter's Porch | E:TLMNS |  |  |  | 1 | 1A | MADC #79 | Approximately 193 Feet Long. | Gianni Tassotto
9-2 | Total Loss Monitor #2 for Carrier Tunnel Upstream End | E:TLMCTU |  |  |  | 1 | 1A | MADC #79 | Approximately 220 Feet Long. | Gianni Tassotto
9-3 | Total Loss Monitor #3 for Carrier Tunnel Downstream End | E:TLMCTD |  |  |  | 1 | 1A | MADC #79 | Approximately 194 Feet Long. | Gianni Tassotto
9-4 | Total Loss Monitor #4 for Pre-Target Area | E:TLMPT |  |  |  | 1 | 1A | MADC #79 | Approximately 182 Feet Long. | Gianni Tassotto
9-5 | Total Loss Monitor High Voltage Power Supply Control | E:TLMHVS | 118 |  |  |  |  | CC $6C N9 |  | Gianni Tassotto Dan Schoo
9-6 | Total Loss Monitor High Voltage Out | E:TLMHVO |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto
9-7 | Total Loss Monitor High Voltage Return | E:TLMHVR |  |  |  | 1 | 1A | MADC #79 |  | Gianni Tassotto
10 | Temperature and Humidity Monitors | [7 empty] | One NIM Slot Will Be Required in the NIM Bin in Rack MI62106 | John Seraphin
10-1 | NuMI Stub Temperature | E:TTNSTB | NIM |  |  | 1 |  | MADC #67 |  | John Seraphin
10-2 | NuMI Stub Humidity | E:THNSTB | NIM |  |  | 1 |  | MADC #67 |  | John Seraphin
11 | Vacuum (All of NuMI Beamline) |  | ARCNET VME Ethrnt | [5 empty] | New CIA Crate Already Installed in Rack MI62112. Vacuum Equipment in Controls/Kicker Room Rack MI62111 and MI62112. | Leon Bartelson Jim Klen
11-A1 | Beam Valve | E:BV100 | CIA Crate |  |  |  | 1D |  | Between LAM61B and V100 | Leon & Jim
11-A2 | Beam Valve | E:BV112A | CIA Crate | [5 empty] | Upper Hobbit Upstream End | Leon & Jim
11-A3 | Beam Valve | E:BV112B | CIA Crate | [5 empty] | Upper Hobbit Downstream End | Leon & Jim
11-B1 | Pirani Gauge | E:PG103 | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-B2 | Pirani Gauge | E:PG110 | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-B3 | Pirani Gauge | E:PG112A | CIA Crate |  |  |  | No |  | Upper Hobbit Upstream End | Leon & Jim
11-B4 | Pirani Gauge | E:PG112B | CIA Crate |  |  |  | No |  | Upper Hobbit Downstream End | Leon & Jim
11-B5 | Pirani Gauge | E:PG115 | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-B6 | Pirani Gauge | E:PG121 | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-C1 | 400 L/sec Ion Pump | E:IP112A | CIA Crate |  |  |  | No |  | Upper Hobbit Upstream End | Leon & Jim
11-C2 | 400 L/sec Ion Pump | E:IP112B | CIA Crate |  |  |  | No |  | Upper Hobbit Upstream End | Leon & Jim
11-C3 | 400 L/sec Ion Pump | E:IP112C | CIA Crate |  |  |  | No |  | Upper Hobbit Downstream End | Leon & Jim
11-C4 | 400 L/sec Ion Pump | E:IP112D | CIA Crate |  |  |  | No |  | Upper Hobbit Downstream End | Leon & Jim
11-D1 | 40 L/sec Ion Pump | E:IP100 | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D2 | 40 L/sec Ion Pump | E:IP101A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D3 | 40 L/sec Ion Pump | E:IP101B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D4 | 40 L/sec Ion Pump | E:IP102 | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D5 | 40 L/sec Ion Pump | E:IP103A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D6 | 40 L/sec Ion Pump | E:IP103B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D7 | 40 L/sec Ion Pump | E:IP104 | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D8 | 40 L/sec Ion Pump | E:IP105A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D9 | 40 L/sec Ion Pump | E:IP105B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D10 | 40 L/sec Ion Pump | E:IP105C | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D11 | 40 L/sec Ion Pump | E:IP106A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D12 | 40 L/sec Ion Pump | E:IP106B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D13 | 40 L/sec Ion Pump | E:IP106C | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D14 | 40 L/sec Ion Pump | E:IP107A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D15 | 40 L/sec Ion Pump | E:IP107B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D16 | 40 L/sec Ion Pump | E:IP107C | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D17 | 40 L/sec Ion Pump | E:IP108A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D18 | 40 L/sec Ion Pump | E:IP108B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D19 | 40 L/sec Ion Pump | E:IP108C | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D20 | 40 L/sec Ion Pump | E:IP109A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D21 | 40 L/sec Ion Pump | E:IP109B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D22 | 40 L/sec Ion Pump | E:IP110A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D23 | 40 L/sec Ion Pump | E:IP110B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D24 | 40 L/sec Ion Pump | E:IP111 | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D25 | 40 L/sec Ion Pump | E:IP114A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D26 | 40 L/sec Ion Pump | E:IP114B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D27 | 40 L/sec Ion Pump | E:IP114C | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D28 | 40 L/sec Ion Pump | E:IP114D | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D29 | 40 L/sec Ion Pump | E:IP115A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D30 | 40 L/sec Ion Pump | E:IP115B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D31 | 40 L/sec Ion Pump | E:IP116A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D32 | 40 L/sec Ion Pump | E:IP116B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D33 | 40 L/sec Ion Pump | E:IP116C | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D34 | 40 L/sec Ion Pump | E:IP116D | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D35 | 40 L/sec Ion Pump | E:IP116E | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D36 | 40 L/sec Ion Pump | E:IP117 | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D37 | 40 L/sec Ion Pump | E:IP118A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D38 | 40 L/sec Ion Pump | E:IP118B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D39 | 40 L/sec Ion Pump | E:IP118C | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D40 | 40 L/sec Ion Pump | E:IP118D | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D41 | 40 L/sec Ion Pump | E:IP119A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D42 | 40 L/sec Ion Pump | E:IP119B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D43 | 40 L/sec Ion Pump | E:IP121A | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D44 | 40 L/sec Ion Pump | E:IP121B | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D45 | 40 L/sec Ion Pump | E:IP121C | CIA Crate |  |  |  | No |  |  | Leon & Jim
11-D46 | 40 L/sec Ion Pump | E:IP121D | CIA Crate |  |  |  | No |  |  | Leon & Jim
12 | MI-62 LCW and Pond Water Systems |  | PLC Ethernet | [5 empty] | PLC Hardware (Automation Direct) Located in Rack MI62109 | Puska & Doyle & Kasley
12-1 | Various NuMI LCW Control and Monitor Points | E:62Winn | PLC Ethernet |  |  |  | 1D |  | Detailed Separately | Puska & Doyle & Kasley
12-2 | Various Pond Water Control and Monitor Points | E:62Pinn | PLC Ethernet |  |  |  | No |  | Detailed Separately | Puska & Doyle & Kasley
13 | MIBS Timing Capability |  | 479 |  |  |  |  | CC $6A N4 | Likely Necessary for Instrumentation (?) | Greg Vogel Rupe Crouch
14 | MADC Facility - Existing in Rack MI62107 | MADC #79 | 290 |  |  |  |  | CC $6C N23 | 14 Bit Resolution MADC Is Required Here and is Now in Place. | Ryan Hagler Rupe Crouch
15 | NuMI Beam Permit |  | 200 |  |  |  |  | CC $6C N22 | Relocated From CC $6C | Greg Vogel Bob Ducar
16 | Beam Permit Process Channel Interface and Controller |  | 204 | Connects to MADC #79 |  |  | 1D | CC $6C N21 | Output to Local 200 Beam Permit Module. 15 Power Supply, 18 Loss Monitor and a Few Miscellaneous. Probably Need to Relocate Some Equipment in Rack to Fit. | Al Franck Bob Ducar
17 | Ethernet Connectivity | [7 empty] | Already Exists at this Location | Dan Stenman
18 | VME with Connection to Ethernet | [7 empty] | Already Exists at this Location | Dan Stenman
19 | ACNET Console X Terminal | [7 empty] | Already Exists at this Location | Dan Stenman
MI-65 Service Bldg Electronics Room "65SB" | [8 empty] | New Basic Controls Infrastructure is Required Here. Will Link to Existing Controls at MI-62. This Location Will Support Similar Infrastructure in the Target Hall Support Room Area ~120 Feet Below. Room for 9 Equipment Racks in the Electronics Room.
1 | B2 Dipole String (4) in Pre-Target Area | E:V118 | 468 | 9 ** |  |  | 3A 1D | CC $E4 N1-2 | Three Series 500 kW PEIs in Electrical Room With Output Filter. Ramped. | Steve Hays
1-1 | Local PLC for Extended Power Supply Status | [7 empty] | Status Supplied to Associated 468 Module | Steve Hays
2 | Quadrupole Power Supply (3Q120) | E:QD113 | 466 | 4 * |  |  | 2A | CC $E4 N3 | Smaller PEI in Electrical Room | Steve Hays
3 | Quadrupole Power Supply (3Q120) | E:QF114 | 466 | 4 * |  |  | 2A | CC $E4 N4 | Smaller PEI in Electrical Room | Steve Hays
4 | Quadrupole Power Supply (3Q60) | E:QF115 | 466 | 4 * |  |  | 2A | CC $E4 N5 | Smaller PEI in Electrical Room. Not Planning to Ramp this Quad. | Steve Hays
5 | Quadrupole Power Supply (3Q120) | E:QD116 | 466 | 4 * |  |  | 2A | CC $E4 N6 | Smaller PEI in Electrical Room | Steve Hays
6 | Quadrupole Power Supply (3Q120) | E:QF117 | 466 | 4 * |  |  | 2A | CC $E4 N7 | Smaller PEI in Electrical Room | Steve Hays
7 | Quadrupole Power Supply (3Q120) | E:QD118 | 466 | 4 * |  |  | 2A | CC $E4 N8 | Smaller PEI in Electrical Room | Steve Hays
8 | Quadrupole Power Supply (3Q60) | E:QF119 | 466 | 4 * |  |  | 2A | CC $E4 N9 | Smaller PEI in Electrical Room | Steve Hays
9 | Quadrupole Power Supply (3Q120) | E:QD120 | 466 | 4 * |  |  | 2A | CC $E4 N10 | Smaller PEI in Electrical Room | Steve Hays
10 | Quadrupole Power Supply (3Q120) | E:QF121 | 466 | 4 * |  |  | 2A | CC $E4 N11 | Smaller PEI in Electrical Room | Steve Hays
11 | Horizontal 200 Turn Trim Dipole | E:H117 | 466 | 4 * |  |  | 2A | CC $E4 N12 | Smaller PEI in Electrical Room | Steve Hays
* | MADC #85 Monitors for Q113 thru Q121 and H117 | Current Reference (F), Current Out, Current Error (E), and Voltage Out (V). First Two Analog Monitors Examined by Beam Permit.
** | MADC #85 Monitors for V118 | Current Reference (F), Current Out, Current Error (E), Plus Volts to Gnd (P), Neg Volts to Gnd (N), Filtered Voltage Out (V), and 3 x Unfiltered Voltage Out (AU, BU & CU). First Three Monitors Examined by Beam Permit. "In Regulation" Digital Status Also to Beam Permit.
12 | Trim Element Regulators (9) | [7 empty] | All Trim Elements Controlled from New Regulator System in Electronics Room | Leon Bartelson
12-1A | Trim Element Bulk Power Supply Controller - Current Output | E:CPS65 | 118 |  |  | 1 |  | CC $E5 N9 |  | Leon Bartelson
12-1B | Trim Element Bulk Power Supply Voltage Output | E:CPS65V |  |  |  | 1 | 1A | MADC #85 | Necessary to Wire Over to MADC #85 to Afford PCI Monitoring | Leon Bartelson
12-1C | Trim Element Bulk Power Supply RMS Current Output | E:CPS65I |  |  |  | 1 |  | MADC #86 |  | Leon Bartelson
12-2 | Vertical Trim Element #1 Located Downstream of Q113 | E:VT114 | .25 x 453 | 4 * |  |  | No | CC $E5 N1-2 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
12-3 | Horizontal Trim Element #2 Located Upstream of Q114 | E:HT114 | .25 x 453 | 4 * |  |  | No | CC $E5 N1-2 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
12-4 | Horizontal Trim Element #3 Located Downstream of Q115 | E:HT115 | .25 x 453 | 4 * |  |  | No | CC $E5 N1-2 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
12-5 | Vertical Trim Element #4 Located Downstream of Q116 | E:VT116 | .25 x 453 | 4 * |  |  | No | CC $E5 N1-2 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
12-6 | Horizontal Trim Element #5 Located Downstream of Q117 | E:HT117 | .25 x 453 | 4 * |  |  | No | CC $E5 N3-4 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
12-7 | Vertical Trim Element #6 Located Downstream of Q118 | E:VT118 | .25 x 453 | 4 * |  |  | No | CC $E5 N3-4 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
12-8 | Horizontal Trim Element #7 Located Upstream of Q119 | E:HT119 | .25 x 453 | 4 * |  |  | No | CC $E5 N3-4 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
12-9 | Horizontal Trim Element #8 Located Downstream of Q121 | E:HT121 | .25 x 453 | 4 * |  |  | No | CC $E5 N3-4 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
12-10 | Vertical Trim Element #9 Located Downstream of Q121 | E:VT121 | .25 x 453 | 4 * |  |  | No | CC $E5 N5-6 | Individual Regulators are 30 A. Plan to Ramp to Keep RMS Power Low. | Leon Bartelson
12-11 | Spare Channel |  | .25 x 453 |  |  |  |  | CC $E5 N5-6 |  | Leon Bartelson
12-12 | Spare Channel |  | .25 x 453 |  |  |  |  | CC $E5 N5-6 |  | Leon Bartelson
12-13 | Spare Channel |  | .25 x 453 |  |  |  |  | CC $E5 N5-6 |  | Leon Bartelson
* | MADC Monitors for Trim Elements | All MADC Monitors Wire Directly to Local MADC #86. Analog Monitors Include: Vref, Vout, I out, I rms. "Tracking" Status Bit Not Readily Available for Examination by Beam Permit. Installation of 204/PCI Not Viewed Favorably. Should Consider an ACNET Software Solution to Solving Beam Permit Problem.
13 | Beam Position Detectors (11) | [7 empty] | Using 3/8" Andrew Heliax LDF2RN-50 Cable | Peter Prieto Sam Childress
13-1 | Vertical BPM Upstream of Q113 | E:VP113 | VME Ethrnt |  |  |  | No |  | Four BPMs per VME Module | Peter Prieto Sam Childress
13-2 | Horizontal BPM Downstream of Q114 | E:HP114 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
13-3 | Horizontal BPM Upstream of Q115 | E:HP115 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
13-4 | Vertical BPM Upstream of Q116 | E:VP116 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
13-5 | Horizontal BPM Upstream of Q117 | E:HP117 | VME Ethrnt |  |  |  | No |  | Four BPMs per VME Module | Peter Prieto Sam Childress
13-6 | Vertical BPM Upstream of Q118 | E:VP118 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
13-7 | Horizontal BPM Downstream of Q119 | E:HP119 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
13-8 | Horizontal BPM Downstream of Q121 | E:HP121 | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
13-9 | Vertical BPM Downstream of Q121 | E:VP121 | VME Ethrnt |  |  |  | No |  | Four BPMs per VME Module | Peter Prieto Sam Childress
13-10 | Horizontal BPM Upstream of Target | E:HPTGT | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
13-11 | Vertical BPM Upstream of Target | E:VPTGT | VME Ethrnt |  |  |  | No |  |  | Peter Prieto Sam Childress
13-12 | Intensity Signal from Q121 BPM | E:HI121P | VME Ethrnt |  |  |  | Yes | MADC #85 | This is a Special Subset of BPM System Signals that Allows the Beam Permit System to Check Positions Immediately After an Extraction from the Main Injector. Duane Voy Assisted with Associated Implementation. | Peter Prieto Sam Childress
13-13 | Horizontal BPM Downstream of Q121 | E:HP121P | VME Ethrnt |  |  |  | Yes | MADC #85 |  | Peter Prieto Sam Childress
13-14 | Vertical BPM Downstream of Q121 | E:VP121P | VME Ethrnt |  |  |  | Yes | MADC #85 |  | Peter Prieto Sam Childress
13-15 | Horizontal BPM Upstream of Target | E:HPTGTP | VME Ethrnt |  |  |  | Yes | MADC #85 |  | Peter Prieto Sam Childress
13-16 | Vertical BPM Upstream of Target | E:VPTGTP | VME Ethrnt |  |  |  | Yes | MADC #85 |  | Peter Prieto Sam Childress
13-17 | MI-65 BPM Status / Heartbeat Expected Logic Low Before Extraction | E:65BPMB | VME Ethrnt |  |  | 1 | Yes | MADC #85 | These Channels Have a Common Source and Essentially Represent a Heartbeat from this BPM System. Provided by Duane Voy. | Peter Prieto Sam Childress
13-18 | MI-65 BPM Status / Heartbeat Expected Logic High After Extraction | E:65BPMA | VME Ethrnt |  |  | 1 | Yes | MADC #85 |  | Peter Prieto Sam Childress
14 | Profile Monitors (6 Total) | [8 empty] | Sacha Kopp Gianni Tassotto Dan Schoo
14-1 | Profile Monitor Downstream of Q114 | E:PM114 (E:M114DS) | ARCNET VME Ethrnt |  |  |  | No |  |  | Sacha Kopp Al Franck
14-2 | Profile Monitor Upstream of Q115 | E:PM115 (E:M115DS) | ARCNET VME Ethrnt |  |  |  | No |  |  | Sacha Kopp Al Franck
14-3 | Profile Monitor Upstream of Q117 | E:PM117 (E:M117DS) | ARCNET VME Ethrnt |  |  |  | No |  |  | Sacha Kopp Al Franck
14-4 | Profile Monitor Downstream of the VT118 Trim Element | E:PM118 (E:M118DS) | ARCNET VME Ethrnt | [5 empty] | This is a Fermilab Style Multiwire. Installed Early February 2005. | Sacha Kopp Al Franck
14-5 | Profile Monitor Downstream of Q121 | E:PM121 (E:M121DS) | ARCNET VME Ethrnt |  |  |  | No |  |  | Sacha Kopp Al Franck
14-6 | Profile Monitor Upstream of Target | E:PMTGT (E:MTGTDS) | ARCNET VME Ethrnt |  |  |  | No |  |  | Sacha Kopp Al Franck
14-7 | Clearing Voltage PS for PM114 | E:PM114V | .25 x 052 |  |  | 1 | No | CC $E5 N7 A0 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Dan Schoo
14-8 | Clearing Voltage PS for PM115 | E:PM115V | .25 x 052 |  |  | 1 | No | CC $E5 N7 A1 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Dan Schoo
14-9 | Clearing Voltage PS for PM117 | E:PM117V | .25 x 052 |  |  | 1 | No | CC $E5 N7 A2 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Dan Schoo
14-10 | Clearing Voltage PS for Possible Future Profile Monitor PM118 | E:PM118V | .25 x 052 |  |  |  |  | CC $E5 N8 A1 | Cable Pulled but Not Required for Fermilab Style | Sacha Kopp Dan Schoo
14-11 | Clearing Voltage PS for PM121 | E:PM121V | .25 x 052 |  |  | 1 | No | CC $E5 N7 A3 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Dan Schoo
14-12 | Clearing Voltage PS for PMTGT | E:PMTGTV | .25 x 052 |  |  | 1 | No | CC $E5 N8 A0 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Dan Schoo
15 | Temperature and Humidity Monitors | [7 empty] | 2 NIM Slots Will Be Required in the NIM Bin in Rack MI65108 | John Seraphin
15-1 | Upper Hobbit Temperature | E:TTUHOB | NIM |  |  | 1 |  | MADC #86 |  | John Seraphin
15-2 | Upper Hobbit Humidity | E:THUHOB | NIM |  |  | 1 |  | MADC #86 |  | John Seraphin
15-3 | Lower Hobbit Temperature | E:TTLHOB | NIM |  |  | 1 |  | MADC #86 |  | John Seraphin
15-4 | Lower Hobbit Humidity | E:THLHOB | NIM |  |  | 1 |  | MADC #86 |  | John Seraphin
15-5 | Pre-Target Temperature | E:TTPTGT | NIM |  |  | 1 |  | MADC #86 |  | John Seraphin
15-6 | Pre-Target Humidity | E:THPTGT | NIM |  |  | 1 |  | MADC #86 |  | John Seraphin
15-7 | MI-65 Electronics Room Temperature | E:ERT65E | NIM |  |  | 1 |  | MADC #86 |  | John Seraphin
15-8 | MI-65 Power Supply Room Temperature | E:ERT65P | NIM |  |  | 1 |  | MADC #86 |  | John Seraphin
15-9 | MI-65 Power Supply Room Humidity | E:ERH65P | NIM |  |  | 1 |  | MADC #86 |  | John Seraphin
15-10 | MI-65 Crane Bay Temperature | E:CBT65 | NIM |  |  | 1 |  | MADC #86 |  | John Seraphin
15-11 | MI-65 Crane Bay Humidity | E:CBH65 | NIM |  |  | 1 |  | MADC #86 |  | John Seraphin
16 | TCLK Event Monitor and Fanout |  | 178 |  |  |  |  | CC $E5 N20 | For Local Instrumentation & Diagnostics | Greg Vogel Bob Ducar
17 | TCLK Timing Capability |  | 377 |  |  |  |  | CC $E5 N22 | For Local Instrumentation | Al Franck Bob Ducar
18 | MIBS Timing Capability |  | 479 |  |  |  |  | CC $E5 N21 | For Local Instrumentation | Greg Vogel Bob Ducar
19 | MADC Facility - Located in Rack MI65103 | MADC #85 | 290 |  |  |  |  | CC $E4 N23 | 14 Bit Resolution Required Here for Power Supplies. | Ryan Hagler Rupe Crouch
20 | MADC Facility - Located in Rack MI65108 | MADC #86 | 290 |  |  |  |  | CC $E5 N23 | Dedicated to Trim Elements. 12 Bit Resolution Probably OK. | Ryan Hagler Rupe Crouch
21 | NuMI Beam Permit |  | 200 |  |  |  |  | CC $E4 N22 |  | Greg Vogel Bob Ducar
22 | Beam Permit Process Channel Interface and Controller |  | 204 | Connects to MADC #85 |  |  |  | CC $E4 N21 | Output to Local 200 Beam Permit Module. 27 Power Supply Channels Monitored. | Al Franck Bob Ducar
23 | Ethernet Connectivity | [7 empty] | Needed for Interface of Local Electronics and Console | Dan Stenman
24 | VME with Connection to Ethernet | [7 empty] | Needed for Interface of Profile Monitors | Dan Stenman Jimmy You
25 | ACNET Console X Terminal | [7 empty] | Necessary and Permanent | Dan Stenman
Target Hall Power Supply Support Room (Underground of MI-65 Service Building) "THSR" | [8 empty] | New Basic Controls Infrastructure is Required Here. Will Link to Existing Controls at MI-65 Above. All Controls Equipment Located in Power Supply Support Room.
1 | Horn Power Supply |  | IRM and CAMAC | [5 empty] | Two PEI 240KW and a Capacitor Bank. Much Control and Status for the Horn PS System Has Already Been Successfully Interfaced at MI-8 Via the IRM and Is Not Explicity Detailed Here. ~205,000 Amps to Horns. | Ken Bourkland Jim Biggs
1-1 | PEI-A Power Supply | E:NHSA | 468 |  |  |  | 1D | CC $E6 N1-2 | PS ON Digital Status to Beam Permit System. 2V Into 100 Ohms. | Ken Bourkland Jim Biggs
1-2 | PEI-B Power Supply | E:NHSB | 468 |  |  |  | 1D | CC $E6 N3-4 | PS ON Digital Status to Beam Permit System. 2V Into 100 Ohms. | Ken Bourkland Jim Biggs
1-3 | E:NHSA Output Waveform Reference | E:NHSAF | (468) |  |  | 1 | 1A | MADC #87 | Local Selector Switch Selects One of These Waveforms as the Input to the Slow Start Module. E:NHSAR Is Normally Selected. | Ken Bourkland Jim Biggs
1-4 | E:NHSB Output Waveform Reference | E:NHSBF | (468) |  |  | 1 | 1A | MADC #87
1-5 | Waveform Reference to PEI-A After Slow Start Module | E:NHSASF | Slow Start Kluge |  |  | 1 | 1A | MADC #87 | These Monitors Expected to Be Similar When Both Supplies Are Being Used and After the Slow Start. | Ken Bourkland Jim Biggs
1-6 | Waveform Reference to PEI-B After Slow Start Module | E:NHSBSF | Slow Start Kluge |  |  | 1 | 1A | MADC #87
1-7 | Current Output of PEI-A Power Supply to Capacitor Bank | E:NHSA | Mr. Biggs | 1 |  |  | 1A | MADC #87 |  | Ken Bourkland Jim Biggs
1-8 | Current Output of PEI-B Power Supply to Capacitor Bank | E:NHSB | Mr. Biggs | 1 |  |  | 1A | MADC #87 |  | Ken Bourkland Jim Biggs
1-9 | Horn Stripline Current | E:HLSI | Mr. Biggs |  |  | 1 | 1A | MADC #87 |  | Ken Bourkland Jim Biggs
1-10 | Peak Horn Stripline Current | E:HLSIP | Mr. Biggs |  |  | 1 | 1A | MADC #87 |  | Ken Bourkland Jim Biggs
1-11 | Power Supply Interlock (Permit) From "Local Controls" Electronics |  | Mr. Biggs |  |  |  | 1D |  |  | Ken Bourkland Jim Biggs
2 | Loss Monitors (Chassis #4) | [7 empty] | Reg Loss Monitor Electronics Packages 12 Channels in One Chassis with HV Supply | Gianni Tassotto Marv Olson
2-1 | Regular Loss Monitor HV Supply Output Chassis #4 | E:LMHV4O |  |  |  | 1 | 1A | MADC #87 |  | Gianni Tassotto Marv Olson
2-2 | Regular Loss Monitor HV Supply Return Chassis #4 | E:LMHV4R |  |  |  | 1 | 1A | MADC #87 |  | Gianni Tassotto Marv Olson
2-3 | Loss Monitor #1 at Q113 | E:LMQ113 |  |  |  | 1 | 1A | MADC #87 |  | Gianni Tassotto Marv Olson
2-4 | Loss Monitor #2 at Q114 | E:LMQ114 |  |  |  | 1 | 1A | MADC #87 |  | Gianni Tassotto Marv Olson
2-5 | Loss Monitor #3 at Q115 | E:LMQ115 |  |  |  | 1 | 1A | MADC #87 |  | Gianni Tassotto Marv Olson
2-6 | Loss Monitor #4 at Q116 | E:LMQ116 |  |  |  | 1 | 1A | MADC #87 |  | Gianni Tassotto Marv Olson
2-7 | Loss Monitor #5 at Q117 | E:LMQ117 |  |  |  | 1 | 1A | MADC #87 |  | Gianni Tassotto Marv Olson
2-8 | Loss Monitor #6 at H117 | E:LMH117 |  |  |  | 1 | 1A | MADC #87 |  | Gianni Tassotto Marv Olson
2-9 | Loss Monitor #7 at Q118 | E:LMQ118 |  |  |  | 1 | 1A | MADC #87 |  | Gianni Tassotto Marv Olson
2-10 | Loss Monitor #8 at V118-1 | E:LM1181 |  |  |  | 1 | 1A | MADC #87 |  | Gianni Tassotto Marv Olson
2-11 | Loss Monitor #9 at V118-2 | E:LM1182 |  |  |  | 1 | 1A | MADC #87 |  | Gianni Tassotto Marv Olson
2-12 | Loss Monitor #10 at Q119 | E:LMQ119 |  |  |  | 1 | 1A | MADC #87 |  | Gianni Tassotto Marv Olson
3 | Loss Monitors (Chassis #5) | [7 empty] | Reg Loss Monitor Electronics Packages 12 Channels in One Chassis with HV Supply | Gianni Tassotto Marv Olson
3-1 | Regular Loss Monitor HV Supply Output Chassis #5 | E:LMHV5O |  |  |  | 1 | 1A | MADC #88 |  | Gianni Tassotto Marv Olson
3-2 | Regular Loss Monitor HV Supply Return Chassis #5 | E:LMHV5R |  |  |  | 1 | 1A | MADC #88 |  | Gianni Tassotto Marv Olson
3-3 | Loss Monitor #1 at V118-3 | E:LM1183 |  |  |  | 1 | 1A | MADC #88 |  | Gianni Tassotto Marv Olson
3-4 | Loss Monitor #2 at V118-4 | E:LM1184 |  |  |  | 1 | 1A | MADC #88 |  | Gianni Tassotto Marv Olson
3-5 | Loss Monitor #3 at Q120 | E:LMQ120 |  |  |  | 1 | 1A | MADC #88 |  | Gianni Tassotto Marv Olson
3-6 | Loss Monitor #4 at Q121 | E:LMQ121 |  |  |  | 1 | 1A | MADC #88 |  | Gianni Tassotto Marv Olson
3-6 | Loss Monitor #5 Before TORTGT Toroid | E:LMTGTT |  |  |  | 1 | 1A | MADC #88 |  | Gianni Tassotto Marv Olson
3-6 | Loss Monitor #6 at Target Shield Wall | E:LMTSW |  |  |  | 1 | 1A | MADC #88 |  | Gianni Tassotto Marv Olson
3-7 | Interlocked Scarecrow Located in Lower Hobbit Just Downstream of Hobbit Door | G:RD1224 | [6 empty] | Connected to NuMI RSS and ES&H Rad Mux System | Mike Gerardi Dale White
4 | Temperature and Humidity Monitors | [7 empty] | 1 NIM Slot Will Be Required in the NIM Bin in Rack THSR104 | John Seraphin
4-1 | Power Supply Support Rm Temperature | E:TTPSSR | NIM |  |  | 1 |  | MADC #88 |  | John Seraphin
4-2 | Power Supply Support Room Humidity | E:THPSSR | NIM |  |  | 1 |  | MADC #88 |  | John Seraphin
4-3 | RAW Room Temperature | E:TTRAWR | NIM |  |  | 1 |  | MADC #88 |  | John Seraphin
4-4 | Target Hall Temperature | E:TTTGTH | NIM |  |  | 1 |  | MADC #88 |  | John Seraphin
4-5 | Target Hall Humidty | E:THTGTH | NIM |  |  | 1 |  | MADC #88 |  | John Seraphin
4-6 | Temp Mon at QD113 | E:TQD113 | Custom by Schoo |  |  | 1 |  | MADC #88 |  | Gordon Koizumi Dan Schoo
4-7 | Temp Mon at QF114 | E:TQF114 | Custom by Schoo |  |  | 1 |  | MADC #88 |  | Gordon Koizumi Dan Schoo
4-8 | Temp Mon at QF117 | E:TQF117 | Custom by Schoo |  |  | 1 |  | MADC #88 |  | Gordon Koizumi Dan Schoo
4-9 | Temp Mon at H117 | E:TH117 | Custom by Schoo |  |  | 1 |  | MADC #88 |  | Gordon Koizumi Dan Schoo
4-10 | Temp Mon at QD118 | E:TQD118 | Custom by Schoo |  |  | 1 |  | MADC #88 |  | Gordon Koizumi Dan Schoo
4-11 | Temp Mon at QD120 | E:TQD120 | Custom by Schoo |  |  | 1 |  | MADC #88 |  | Gordon Koizumi Dan Schoo
4-12 | Temp Mon at QF121 | E:TQF121 | Custom by Schoo |  |  | 1 |  | MADC #88 |  | Gordon Koizumi Dan Schoo
4-13 | Temp Mon at TGT BPM Stnd | E:TTGTBS | Custom by Schoo |  |  | 1 |  | MADC #88 |  | Gordon Koizumi Dan Schoo
5 | Primary Beam Monitoring | [7 empty] | BPM Electronics Independent of Beamline BPM Systems | Jim Hylen Rich Talaga
5-1 | Beam Intensity Toroid #2 - Downstream | E:TORTGT E:TRTGTD | NIM Module and a 284 |  |  | 1 |  | MADC #87 CC $E6 N13 | Requires a 479 Timing Channel (CC $E6 N14 A(0)) for Sampling at the Right Time. This Timer Or'd with a 377 Timing Channel (CC $E6 N17 A(7)) to Clear/Calibrate Without Beam. | Peter Prieto Greg Vogel Dallas H.
6 | Baffle and Target Instrumentation | [7 empty] | May Use Some Automation Direct PLC Hardware, But Largely Independent | Jim Hylen Rich Talaga
6-1 | Baffle Thermocouples | E:BAFT1 E:BAFT2 | Custom | 2 |  |  | 2A | MADC #87 |  | Jim Hylen Rich Talaga
6-2 | Target Thermocouples (Actually Support Tube) | E:TGTT1 E:TGTT2 | Custom | 2 |  |  |  | MADC #87 |  | Jim Hylen Rich Talaga
6-3 | Target Budal Monitor for X | E:HFVSL E:HFVSH | Custom | 2 |  |  | No | MADC #87 |  | Jim Hylen Rich Talaga
6-4 | Target Budal Monitor for Y | E:VFHSL E:VFHSH | Custom | 2 |  |  | No | MADC #87 |  | Jim Hylen Rich Talaga
6-5 | Target to Ground Impedance | E:TGTGZ | Custom | 1 |  |  | No | MADC #87 |  | Jim Hylen Rich Talaga
6-6 | Target Vacuum Pirani Gauge | E:PGTGT | Custom | 1 |  |  | No | MADC #87 |  | Jim Hylen Rich Talaga
6-7 | Target/Baffle Carrier Temperatures | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 2 Channels | Hylen Talaga Stefanik
6-8 | Target Helium Pressure | E:BTHP01 | PLC Ethernet |  |  |  | Yes |  |  | Jim Hylen Rich Talaga
6-9 | Target Helium Supply Bottle Pressure | E:BTHP02 | PLC Ethernet |  |  |  | No |  |  | Jim Hylen Rich Talaga
6-10 | Target RAW Expansion Tank Helium Flow | E:TRETHF | Transducer |  |  | 1 | No | MADC #87 | Installed 10-Aug-05 | Jim Hylen Hiep Le
7 | Horn and Horn Stripline Iinstrumentation | [7 empty] | Anticipate Using Automation Direct PLC Hardware for Thermocouples | Jim Hylen Rich Talaga
7-1 | Horn 1 Alignment Loss Monitor | E:H1ALM |  | 1 |  |  | No | MADC #88 | Separate from Loss Monitor Chassis #4 & #5 | Jim Hylen Rich Talaga
7-2 | Horn 1 Alignment LM High Voltage | E:H1ALV |  |  |  | 1 | No | MADC #88 | HV Power Supply at Top of Rack THSR105 (May Need a Second HV Supply) | Jim Hylen Rich Talaga
7-3 | Horn 2 Alignment Loss Monitor | E:H2ALM |  | 1 |  |  | No | MADC #88 | Separate from Loss Monitor Chassis #4 & #5 | Jim Hylen Rich Talaga
7-4 | Horn 2 Alignment LM High Voltage | E:H2ALV |  |  |  | 1 | No | MADC #88 | HV Power Supply at Top of Rack THSR105 (May Need a Second HV Supply) | Jim Hylen Rich Talaga
7-5 | Horn Stripline Quadrant A Current | E:HSQAI | (Mr. Biggs) | 1 |  |  | No | MADC #88 |  | Jim Hylen Rich Talaga
7-6 | Horn Stripline Quadrant B Current | E:HSQBI | (Mr. Biggs) | 1 |  |  | No | MADC #88 |  | Jim Hylen Rich Talaga
7-7 | Horn Stripline Quadrant C Current | E:HSQCI | (Mr. Biggs) | 1 |  |  | No | MADC #88 |  | Jim Hylen Rich Talaga
7-8 | Horn Stripline Quadrant D Current | E:HSQDI | (Mr. Biggs) | 1 |  |  | No | MADC #88 |  | Jim Hylen Rich Talaga
7-9 | Peak Horn Stripline Quadrant A Current | E:HSQAIP | Custom | 1 |  |  | No | MADC #88 | Sample and Hold Output | Jim Hylen Rich Talaga
7-10 | Peak Horn Stripline Quadrant B Current | E:HSQBIP | Custom | 1 |  |  | No | MADC #88 | Sample and Hold Output | Jim Hylen Rich Talaga
7-11 | Peak Horn Stripline Quadrant C Current | E:HSQCIP | Custom | 1 |  |  | No | MADC #88 | Sample and Hold Output | Jim Hylen Rich Talaga
7-12 | Peak Horn Stripline Quadrant D Current | E:HSQDIP | Custom | 1 |  |  | No | MADC #88 | Sample and Hold Output | Jim Hylen Rich Talaga
7-13 | Per Pulse Integral of Horn Stripline Quadrant A Current | E:HSQAII | Custom | 1 |  |  | No | MADC #87 |  | Jim Hylen Rich Talaga
7-14 | Per Pulse Integral of Horn Stripline Quadrant B Current | E:HSQBII | Custom | 1 |  |  | No | MADC #87 |  | Jim Hylen Rich Talaga
7-15 | Per Pulse Integral of Horn Stripline Quadrant C Current | E:HSQCII | Custom | 1 |  |  | No | MADC #87 |  | Jim Hylen Rich Talaga
7-16 | Per Pulse Integral of Horn Stripline Quadrant D Current | E:HSQDII | Custom | 1 |  |  | No | MADC #87 |  | Jim Hylen Rich Talaga
7-17 | Horn Stripline Current at Arrival of Beam | E:HSLIB | Custom | 1 |  |  | No | MADC #87 | Sample and Hold Output Triggered by a 479 Beam Sync Timing Module Channel | Jim Hylen Rich Talaga
7-18 | Arrival of Beam wrt Clock | E:NOCLU1 | Custom | 1 |  |  | No | MADC #87 |  | Jim Hylen Rich Talaga
7-19 | Horn BDOT Zero wrt Clock | E:NOCLU2 | Custom | 1 |  |  | No | MADC #87 |  | Jim Hylen Rich Talaga
7-20 | Delta Arrival of Beam wrto Horn BDOT Zero | E:NOCLU3 | Custom | 1 |  |  | No | MADC #87 |  | Jim Hylen Rich Talaga
7-21 | Horn 1 Magnetic Field Monitors B-Dot Coils | E:H1FLXL - E:H1INTR | Custom | 9 |  |  | No | MADC #88 | Associated Sample & Hold? | Jim Hylen Rich Talaga
7-22 | Horn 2 Magnetic Field Monitors B-Dot Coils | E:H2FLXL - E:H2INTR | Custom | 9 |  |  | No | MADC #88 | Associated Sample & Hold? | Jim Hylen Rich Talaga
7-23 | Horn 1 Module Support Thermocouples | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 2 Channels | Jim Hylen Rich Talaga
7-24 | Horn 2 Module Support Thermocouples | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 2 Channels | Jim Hylen Rich Talaga
7-25 | Horn 1 Carriage (Hanger) Thermocouples | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 2 Channels | Jim Hylen Rich Talaga
7-26 | Horn 1 Body (Clamp) Thermocouples | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 6 Channels | Jim Hylen Rich Talaga
7-27 | Horn 2 Body (Clamp) Thermocouples | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 6 Channels | Jim Hylen Rich Talaga
8 | Target and Baffle RAW System |  | PLC Ethernet |  |  |  | 1D |  | Anticipate Using Automation Direct PLC Hardware | Puska & Doyle & Kasley
8-1 | Various Control and Monitor Points | E:TBRinn | PLC Ethrnt | [5 empty] | Detailed Separately | Puska & Doyle & Kasley
9 | Horn 1 RAW System |  | PLC Ethernet |  |  |  | 1D |  | Anticipate Using Automation Direct PLC Hardware | Puska & Doyle & Kasley
9-1 | Various Control and Monitor Points | E:H1Rinn | PLC Ethrnt | [5 empty] | Detailed Separately | Puska & Doyle & Kasley
10 | Horn 2 RAW System |  | PLC Ethernet |  |  |  | 1D |  | Anticipate Using Automation Direct PLC Hardware | Puska & Doyle & Kasley
10-1 | Various Control and Monitor Points | E:H2Rinn | PLC Ethrnt | [5 empty] | Detailed Separately | Puska & Doyle & Kasley
11 | Decay Pipe Cooling RAW System - Upstream End |  | PLC Ethernet |  |  |  | 1D |  | Anticipate Using Automation Direct PLC Hardware | Puska & Doyle & Kasley
11-1 | Various Control and Monitor Points | E:DURinn | PLC Ethrnt | [5 empty] | Detailed Separately | Puska & Doyle & Kasley
12 | Target Pile Air Cooling System |  | PLC Ethernet | [5 empty] | Anticipate Using Automation Direct PLC Hardware. Primary Components Include a Chiller, Reheater, Fan and Filters. Various Monitor Points of Temperature, Pressure and Humidity. | Andy Stefanik Jim Hylen
12-1 | Various Control and Monitor Points | E:TPCinn | PLC Ethrnt | [5 empty] | Detailed Separately | Andy Stefanik
12-2 | Fan Differential Pressure | E:TPCFDP | Custom | 1 |  |  | 1A | MADC #87 | Electronics Independent of PLC | Jim Hylen Rich Talaga
12-3 | Target Pile Air Supply Temperature | E:TPCAST | Custom | 1 |  |  | 1A | MADC #87 | Electronics Independent of PLC | Jim Hylen Rich Talaga
13 | Target Positioning System |  | ARCNET VME Ethrnt |  |  |  | No |  | 5 Motors and Similar to AP0 | Al Legan Kris Anderson
14 | Positioning System for Horn #1 |  | ARCNET VME Ethrnt |  |  |  | No |  | 4 Motors and Similar to AP0 | Al Legan Kris Anderson
15 | Total Loss Monitor Gas Flow | (E:TLMGF) | Custom |  |  |  | 1D |  | From Gas Bottles in Power Supply Support Room | Dan Schoo
16 | TCLK Event Monitor and Fanout |  | 178 |  |  |  |  | CC $E6 N15 | For Local Instrumentation & Dignostics | Greg Vogel Bob Ducar
17 | TCLK Timing Capability | Initial E:THSRT0/F | 2 x 377 |  |  |  |  | CC $E6 N17 CC $E6 N16 | Horn Timing and Also for Local Instrumentation | Ken Bourkland Al Franck
18 | MIBS Timing Capability (Ref $74) |  | 479 |  |  |  |  | CC $E6 N14 | Horn Timing and Also for Local Instrumentation | Ken Bourkland Vogel/Ducar
19 | MADC Facility - Located in Rack THSR103 | MADC #87 | 290 |  |  |  |  | CC $E6 N23 | 14 Bit Resolution Required Here | Ryan Hagler Rupe Crouch
20 | MADC Facility - Located in Rack THSR104 | MADC #88 | 290 |  |  |  |  | CC $E6 N22 | 14 Bit Resolution Required Here | Ryan Hagler Rupe Crouch
21 | NuMI Beam Permit |  | 200 |  |  |  |  | CC $E6 N20 | BP Input Panel Located in Rack THSR103 | Greg Vogel Bob Ducar
22 | NuMI Beam Permit |  | 200 |  |  |  |  | CC $E6 N21 | BP Input Panel Located in Rack THSR104 | Greg Vogel Bob Ducar
23 | Beam Permit Process Channel Interface and Controller |  | 204 | Connects to MADC #87 |  |  | 1D | CC $E6 N19 | Output to Local 200 Beam Permit Module. | Al Franck Bob Ducar
24 | Beam Permit Process Channel Interface and Controller |  | 204 | Connects to MADC #88 |  |  | 1D | CC $E6 N18 | Output to Local 200 Beam Permit Module. | Al Franck Bob Ducar
25 | Ethernet Connectivity | [7 empty] | Needed for Interface of Local Electronics and Console | Dan Stenman Jimmy You
26 | VME with Connection to Ethernet | [7 empty] | Needed for Interface of Motion Control | Dan Stenman
27 | ACNET Console X Terminal | [7 empty] | Thought to Reside Here Permanently. Definitely Necessary During Commissioning. | Dan Stenman
MINOS Service Building (West of Lederman Science Center) "MSB" | [8 empty] | Little Controls Infrastructure is Required Here in Mechanical Areas. Main Purpose is to Provide Repeater Stations for Necessary Signals Linking Controls Infrastructure. Basic Control and Monitoring Anticipated, But Nothing Especially Complex.
1 | TCLK Event Monitor and Fanout |  | 178 |  |  |  |  | CC $E7 N20 | Not Thought Necessary for Equipment, But Useful for Diagnostics. | Greg Vogel Bob Ducar
2 | Digital In - Digital Out Facility |  | 184 |  |  |  |  | CC $E7 N1 | Potential for Control and Monitor of Local Systems | Greg Vogel Bob Ducar
3 | MADC Facility - Located in Rack MSB101 | MADC #1 | 290 |  |  |  |  | CC $E7 N23 | 12 Bit Resolution Adequate Here. Expected to Monitor Critical Sump Pump Functions. | Ryan Hagler Rupe Crouch
4 | NuMI Beam Permit Origin Module |  | 201 |  |  |  |  | CC $E7 N21 | Most Distant Location for the Extraction Kicker. Close the Loop With TCLK $A6. | Greg Vogel Bob Ducar
5 | NuMI Beam Permit |  | 200 |  |  |  | None | CC $E7 N22 | Useful for Diagnostics if Checking Return of Permit Signal from Absorber Area. | Greg Vogel Bob Ducar
6 | Ethernet Connectivity | [7 empty] | Thought Necessary Because of Distances Involved | Dan Stenman
MINOS Near Detector Hall (350 Feet Underground of MINOS Svc Bldg) "MND" | [8 empty] | New Controls Infrastructure Required Here Linked by Fiber to Above MINOS Building. Link from here to Absorber Access Tunnel. Fiber Connectivity to Feynman Supported on Controls Singlemode Fibers.
1 | Detector Magnet Power Supply | E:NDMAG | 218 |  | 2 | 1 | No | CC $E8 N1 | 150 kW PEI 150-5 with a Reversing Switch. Expected to Run DC. | Leon Beverly Walt Jaskierny
2 | MINOS LCW System |  | PLC Ethernet |  |  |  | No |  | Includes Analysis Magnet and Its Power Supply and Detector Electronics Rack Cooling. Also Controlling Heat Exchangers Using Clean and Cold Sump Water. | Puska & Doyle & Kasley
2-1 | Various Control and Monitor Points | E:MNWinn | PLC Ethrnt | [5 empty] | Detailed Separately | Puska & Doyle & Kasley
3 | Area Temperature & Humidity Sensors | [5 empty] | No |  | Likely to be Instrumented Thru Above Local PLC | Cat James
4 | TCLK Event Monitor and Fanout |  | 178 |  |  |  |  | CC $E8 N19 | Diagnostics and Other Potential Utility | Greg Vogel Bob Ducar
5 | TCLK Timing Capability |  | 377 |  |  |  |  | CC $E8 N21 | Diagnostics and Other Potential Utility | Al Franck Bob Ducar
6 | MIBS Timing Capability (Ref $74) |  | 479 |  |  |  |  | CC $E8 N20 | Need Main Injector 53 MHz for MINOS Experiment Clocking | Cat James Vogel/Ducar
7 | Digital In - Digital Out Facility |  | 184 |  |  |  |  | CC $E8 N2 | Potential for Control and Monitor of Local Systems in Lieu of Local PLC | Greg Vogel Bob Ducar
8 | MADC Facility - Located in Rack MND101 | MADC #2 | 290 |  |  |  |  | CC $E8 N23 | 12 Bit Resolution Should be OK Here | Ryan Hagler Rupe Crouch
9 | NuMI Beam Permit |  | 200 |  |  |  | None | CC $E8 N22 | Status of Permit Loop and Diagnostics Afforded. No Inputs Planned Here. | Greg Vogel Bob Ducar
10 | Ethernet Connectivity | [8 empty] | Dan Stenman
Absorber Access Tunnel (Near Absorber at End of Decay Pipe) "AAT" | [8 empty] | New Controls Infrastructure Required Here Linked by Fiber to MINOS Near Detector - About 900 Feet Away.
1 | Hadron Monitor Instrumentation | E:HADM | ARCNET VME Ethrnt |  |  |  | No |  | Detectors Installed Between Decay Pipe End and Absorber. Using SWIC Scanner Hardware for Readout. | Debbie Harris Sacha Kopp
1-1 | High Voltage Supply #1 for Hadron Monitor | E:HMHV1 | .25 x 052 |  |  | 1 | No | CC $E9 N1 A0 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
1-2 | High Voltage Supply #2 for Hadron Monitor | E:HMHV2 | .25 x 052 |  |  | 1 | No | CC $E9 N1 A1 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
1-3 | High Voltage Supply #3 for Hadron Monitor | E:HMHV3 | .25 x 052 |  |  | 1 | No | CC $E9 N1 A2 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
1-4 | High Voltage Supply #4 for Hadron Monitor | E:HMHV4 | .25 x 052 |  |  | 1 | No | CC $E9 N1 A3 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
1-5 | High Voltage Supply #5 for Hadron Monitor | E:HMHV5 | .25 x 052 |  |  | 1 | No | CC $E9 N2 A0 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
1-6 | High Voltage Supply #6 for Hadron Monitor | E:HMHV6 | .25 x 052 |  |  | 1 | No | CC $E9 N2 A1 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
1-7 | High Voltage Supply #7 for Hadron Monitor | E:HMHV7 | .25 x 052 |  |  | 1 | No | CC $E9 N2 A2 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
2 | Muon Monitor Instrumentation for Alcove 1 | E:MMA1 | ARCNET VME Ethrnt |  |  |  | No |  | Detectors Installed at Muon Alcove 1. Using SWIC Scanner Hardware for Readout. Gas System is Fully Manual. | Debbie Harris Sacha Kopp
2-1 | High Voltage Supply #1 for Muon Monitor in Alcove 1 | E:MM1HV1 | .25 x 052 |  |  | 1 | No | CC $E9 N3 A0 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
2-2 | High Voltage Supply #2 for Muon Monitor in Alcove 1 | E:MM1HV2 | .25 x 052 |  |  | 1 | No | CC $E9 N3 A1 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
2-3 | High Voltage Supply #3 for Muon Monitor in Alcove 1 | E:MM1HV3 | .25 x 052 |  |  | 1 | No | CC $E9 N3 A2 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
3 | Muon Monitor Instrumentation for Alcove 2 | E:MMA2 | ARCNET VME Ethrnt |  |  |  | No |  | Detectors Installed at Muon Alcove 2. Using SWIC Scanner Hardware for Readout. Gas System is Fully Manual. | Debbie Harris Sacha Kopp
3-1 | High Voltage Supply #1 for Muon Monitor in Alcove 2 | E:MM2HV1 | .25 x 052 |  |  | 1 | No | CC $E9 N4 A0 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
3-2 | High Voltage Supply #2 for Muon Monitor in Alcove 2 | E:MM2HV2 | .25 x 052 |  |  | 1 | No | CC $E9 N4 A1 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
3-3 | High Voltage Supply #3 for Muon Monitor in Alcove 2 | E:MM2HV3 | .25 x 052 |  |  | 1 | No | CC $E9 N4 A2 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
4 | Muon Monitor Instrumentation for Alcove 3 | E:MMA3 | ARCNET VME Ethrnt |  |  |  | No |  | Detectors Installed at Muon Alcove 3. Using SWIC Scanner Hardware for Readout. Gas System is Fully Manual. | Debbie Harris Sacha Kopp
4-1 | High Voltage Supply #1 for Muon Monitor in Alcove 3 | E:MM3HV1 | .25 x 052 |  |  | 1 | No | CC $E9 N5 A0 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
4-2 | High Voltage Supply #2 for Muon Monitor in Alcove 3 | E:MM3HV2 | .25 x 052 |  |  | 1 | No | CC $E9 N5 A1 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
4-3 | High Voltage Supply #3 for Muon Monitor in Alcove 3 | E:MM3HV3 | .25 x 052 |  |  | 1 | No | CC $E9 N5 A2 | PS is Half of PREP NIM Module ES-7125. 052 Provides Reference and Reset. | Sacha Kopp Greg Vogel
5 | Hadron & Muon Monitor Gas System | [8 empty] | Sacha Kopp
5-1 | Hadron Monitor Gas Pressures at AAT101 Rack and Detector and Overall Gas Flow | E:HMGPR E:HMGPD E:HMGF |  |  |  | 3 |  | MADC #3 | Kopp Providing Transducers | Sacha Kopp
5-2 | Alcove 1 Muon Monitor Gas Pressures at AAT101 Rack and Detector and Overall Gas Flow | E:MM1GPR E:MM1GPD E:MM!GF |  |  |  | 3 |  | MADC #3 | Kopp Providing Transducers | Sacha Kopp
5-3 | Alcove 2 Muon Monitor Gas Pressures at AAT101 Rack and Detector and Overall Gas Flow | E:MM2GPR E:MM2GPD E:MM2GF |  |  |  | 3 |  | MADC #3 | Kopp Providing Transducers | Sacha Kopp
5-4 | Alcove 3 Muon Monitor Gas Pressures at AAT101 Rack and Detector and Overall Gas Flow | E:MM3GPR E:MM3GPD E:MM3GF |  |  |  | 3 |  | MADC #3 | Kopp Providing Transducers | Sacha Kopp
5-5 | Miscellaneous Gas System Monitors | E:MGO2I E:MGSP E:HMMRCI |  |  |  | 3 |  | MADC #3 | Kopp Providing Transducers | Sacha Kopp
6 | Temperature and Humidity Monitors | [7 empty] | 2 NIM Slots Will Be Required in the NIM Bin in Rack AAT102 | John Seraphin
6-1 | Hadron Monitor Area Temperature | E:TTHADM | NIM |  |  | 1 |  | MADC #3 |  | John Seraphin
6-2 | Muon Alcove 1 Temperature | E:TTMA1 | NIM |  |  | 1 |  | MADC #3 |  | John Seraphin
6-3 | Muon Alcove 2 Temperature | E:TTMA2 | NIM |  |  | 1 |  | MADC #3 |  | John Seraphin
6-4 | Muon Alcove 3 Temperature | E:TTMA3 | NIM |  |  | 1 |  | MADC #3 |  | John Seraphin
6-5 | Upper Absorber Access Tunnel Temp | E:TTAATU | NIM |  |  | 1 |  | MADC #3 |  | John Seraphin
6-6 | Upper AAT Humidity | E:THAATU | NIM |  |  | 1 |  | MADC #3 |  | John Seraphin
6-7 | Lower AAT Temperature | E:TTAATL | NIM |  |  | 1 |  | MADC #3 |  | John Seraphin
6-8 | Lower AAT Humidity | E:THAATL | NIM |  |  | 1 |  | MADC #3 |  | John Seraphin
6-9 | Hadron Monitor RTD | E:HMRTD | ? |  |  | 1 |  | MADC #3 |  | Sacha Kopp
6-10 | Muon Monitor at Alcove 1 RTD | E:MM1RTD | ? |  |  | 1 |  | MADC #3 |  | Sacha Kopp
6-11 | Muon Monitor at Alcove 2 RTD | E:MM2RTD | ? |  |  | 1 |  | MADC #3 |  | Sacha Kopp
6-12 | Muon Monitor at Alcove 3 RTD | E:MM3RTD | ? |  |  | 1 |  | MADC #3 |  | Sacha Kopp
7 | Absorber Instrumentation | [5 empty] | 1D |  | Anticipate Using Automation Direct PLC Hardware. Mostly Thermocouples and Humidity Sensors. | Dixon Bogert Ernie Villegas
7-1 | Various Control and Monitor Points | E:ABSinn | PLC Ethrnt | [5 empty] | Mostly Thermocouples. Detailed Separately. | Dixon Bogert Ernie Villegas Paul Kasley
8 | Decay Pipe Vacuum System | [5 empty] | 1D |  | Anticipate Using Automation Direct PLC Hardware. Controls Also at Upstream End. | Dave Pushka
8-1 | Various Control and Monitor Points | E:DPVinn | PLC Ethrnt | [5 empty] | Detailed Separately. Expecting Two 20 HP Pumps at a Maximum. | Dave Pushka
9 | Absorber Cooling RAW System | [5 empty] | 1D |  | Anticipate Using Automation Direct PLC Hardware | Puska & Doyle & Kasley
9-1 | Various Control and Monitor Points | E:ABRinn | PLC Ethrnt | [5 empty] | Detailed Separately. Expecting Two 3 HP Pumps at a Maximum. | Puska & Doyle & Kasley
10 | Intermediate Water Cooling for Absorber RAW System | [5 empty] | No |  | Anticipate Using Automation Direct PLC Hardware | Puska & Doyle & Kasley
10-1 | Various Control and Monitor Points | E:ABIinn | PLC Ethrnt | [5 empty] | Detailed Separately. Expecting Two 5 HP Pumps. | Puska & Doyle & Kasley
11 | Decay Pipe Cooling RAW System - Downstream End | [5 empty] | 1D |  | Anticipate Using Automation Direct PLC Hardware | Puska & Doyle & Kasley
11-1 | Various Control and Monitor Points | E:DDRinn | PLC Ethrnt | [5 empty] | Detailed Separately. Expecting Two 7.5 HP Pumps. | Puska & Doyle & Kasley
12 | TCLK Event Monitor and Fanout |  | 178 |  |  |  |  | CC $E9 N19 | Needs Not Specific at this Time But Useful for Diagnostics. | Greg Vogel Bob Ducar
13 | TCLK Timing Capability |  | 377 |  |  |  |  | CC $E9 N21 | Needs Not Specific at this Time But Useful for Diagnostics. | Al Franck Bob Ducar
14 | MIBS Timing Capability (Ref $74) |  | 479 |  |  |  |  | CC $E9 N20 | Thought Necessary for Hadron and Muon Monitor Instrumentation. | Debbie Harris Sacha Kopp
15 | MADC Facility - Located in Rack AAT103 | MADC #3 | 290 |  |  |  |  | CC $E9 N23 | 12 or 14 Bit Resolution | Ryan Hagler Rupe Crouch
16 | NuMI Beam Permit |  | 200 |  |  |  |  | CC $E9 N22 |  | Greg Vogel Bob Ducar
17 | Ethernet Connectivity | [8 empty] | Dan Stenman
18 | VME with Connection to Ethernet | [7 empty] | For Hadron & Muon Monitors | Dan Stenman Jimmy You
19 | ACNET Console X Terminal | [7 empty] | May Not Reside Here Permanently But Thought Convenient During Commissioning | Dan Stenman
General Ordering of System / Device: Power Supplies, Trim Supplies, Instrumentation, Vacuum, Water, Special, Timing, Digital I/O, MADC, Beam Permit, Ethernet, VME, Console

## Timer Cards
NuMI TIMING CHANNEL INFORMATION | [6 empty] | 2005-02-24
Location | Module Type | Crate | Slot | Channel | Name | Description | Likely Reference
Accelerator Cross Gallery
MAC Room | 377 | SWYD $07 | N14 | 2 | T:NMICST | NuMI Cycle Sample Time (Generates $A4) | $A5
MI-60 South
MI-60 South Control Room | 377 | 94 | N3 | 2 | I:MINX | Initiate NuMI Beam Extraction (Generates MIBS $74) | $A5
MI-60 South Control Room | 377 | 90 | N12 | 6 | I:BNKGST | BNKG Permit Sample Time | $A5
MI-60 South | 377 | 63 | N2 | 0 | I:63SDC0
Equip Room |  |  |  | 1 | I:63SDC1
|  |  |  | 2 | I:LMNUMR
|  |  |  | 3 | I:LMNUMH
|  |  |  | 4 | I:LMP1R1
|  |  |  | 5 | I:LMP1H1
|  |  |  | 6 | I:LMP1R2
|  |  |  | 7 | I:LMP1H2
MI-60 South | 377 | 63 | N3 | 0 | I:T714T0
Equip Room |  |  |  | 1 | I:T714T1
|  |  |  | 2 | I:T714T2
|  |  |  | 3 | I:T714T3
|  |  |  | 4 | I:T714T4
|  |  |  | 5 | I:T714T5
|  |  |  | 6 | I:T714T6
|  |  |  | 7 | I:T714T7
MI-60 South | 377 | 63 | N19 | 0 | I:K6NUCD | K6N Kicker Unclamp Dly | $A5
Equip Room |  |  |  | 1 | I:K6NST1 | K6N Spare TCLK Dly Ch1 | $A5
|  |  |  | 2 | I:K6NST2 | K6N Spare TCLK Dly Ch2 | $A5
|  |  |  | 3 | I:K6NST3 | K6N Spare TCLK Dly Ch3 | $A5
|  |  |  | 4 | I:K6NST4 | K6N Spare TCLK Dly Ch4 | $A5
|  |  |  | 5 | I:K6NST5 | K6N Spare TCLK Dly Ch5 | $A5
|  |  |  | 6 | I:K6NST6 | K6N Spare TCLK Dly Ch6 | $A5
|  |  |  | 7 | I:K6NST7 | K6N Spare TCLK Dly Ch7 | $A5
MI-60 South | 479 | 63 | N20 | 0 | I:K6NKD0 | $74 NuMI Kicker Dly 0 (Fires the Kicker) | 74
Equip Room |  |  |  | 1 | I:K6NKD1 | $74 NuMI Kicker Dly 1 | 74
|  |  |  | 2 | I:K6NKD2 | $74 NuMI Kicker Dly 2 | 74
|  |  |  | 3 | I:K6NKD3 | $79 NuMI Kicker Test Dly | 79
MI-60 North
MI-60 North | 377 | 71 | N2 | 0 | I:TC30DA
North Gallery |  |  |  | 1 | I:TC30DB
|  |  |  | 2 | I:RFSST1
|  |  |  | 3 | I:RFSST2
|  |  |  | 4 | I:QXRSGN
|  |  |  | 5 | C71SD5
|  |  |  | 6 | C71SD6
|  |  |  | 7 | C71SD7
MI-60 North | 377 | 72 | N17 | 0 | I:MW720D
North Gallery |  |  |  | 1 | I:MW721D
|  |  |  | 2 | I:MW722D
|  |  |  | 3 | I:MW723D
|  |  |  | 4 | I:MW724D
|  |  |  | 5 | I:MW725D
|  |  |  | 6 | I:MW726D
|  |  |  | 7 | I:MW727D
MI-60 North | 377 | 72 | N19 | 0 | I:FFCCDD
North Gallery |  |  |  | 1 | I:FFCCON
|  |  |  | 2 | I:FFCCOF
|  |  |  | 3 | I:FFPBON
|  |  |  | 4 | I:FFPBOF
|  |  |  | 5 | I:FFSPD5
|  |  |  | 6 | I:FFSPD6
|  |  |  | 7 | I:FFSPD7
MI-60 North | 377 | 73 | N1 | 0 | I:T914T0
North Gallery |  |  |  | 1 | I:T914T1
|  |  |  | 2 | I:LMA1R1
|  |  |  | 3 | I:LMA1H1
|  |  |  | 4 | I:LMA1R2
|  |  |  | 5 | I:LMA1H2
6
7
MI-60 North | 377 | 70 | N16 | 0 | E:NLMC1R | NuMI Loss Mon #1 Reset | $A5
North Gallery |  |  |  | 1 | E:NLMC1H | NuMI Loss Mon #1 Hold | $A5
|  |  |  | 2 | E:NLMC2R | NuMI Loss Mon #2 Reset | $A5
|  |  |  | 3 | E:NLMC2H | NuMI Loss Mon #2 Hold | $A5
|  |  |  | 4 | I:NLMC6R | MI Loss Mon #6 Reset | $A5
|  |  |  | 5 | I:NLMC6H | MI Loss Mon #6 Hold | $A5
|  |  |  | 6 | E:TC101D | Clear Time for E:TR101D | $A5 $00
|  |  |  | 7 | E:C70ST7 | Spare TCLK Timer 7 | $A5
MI-60 North | 479 | 70 | N17 | 0 | E:TS101D | Sample Time for E:TR101D | MIBS $74
North Gallery |  |  |  | 1 | E:NRWMT | NuMI Restv Wall Mon Trig | MIBS $74
|  |  |  | 2 | E:70BSD2 | Beam Sync Trig at $70 N17 | MIBS $74
|  |  |  | 3 | E:70BSD3 | Beam Sync Trig at $70 N17 | MIBS $74
MI-62
MI-62 | 377 | $6A | N2 | 0 | I:K6AUCD
Cntrl/Kicker Rm |  |  |  | 1 | I:K6ARTD
|  |  |  | 2 | I:K62GD2
|  |  |  | 3 | I:K62GD3
|  |  |  | 4 | I:K6BUCD
|  |  |  | 5 | I:K6BRTD
6
7
MI-62 | 479 | $6A | N3 | 0 | I:K6AKD0
Cntrl/Kicker Rm |  |  |  | 1 | I:K6AKD1
|  |  |  | 2 | I:K6BKD0
|  |  |  | 3 | I:K6BKD1
MI-62 | 479 | $6A | N4 | 0 | E:6ABSD0 | Beam Sync Trig at $6A N4 | MIBS $74
Cntrl/Kicker Rm |  |  |  | 1 | E:6ABSD1 | Beam Sync Trig at $6A N4 | MIBS $74
|  |  |  | 2 | E:6ABSD2 | Beam Sync Trig at $6A N4 | MIBS $74
|  |  |  | 3 | E:6ABSD3 | Beam Sync Trig at $6A N4 | MIBS $74
MI-62 | 377 | $6B | N1 | 0 | I:T902T0
Cntrl/Kicker Rm |  |  |  | 1 | I:T902T1
|  |  |  | 2 | E:NLMC3R | NuMI Loss Mon #3 Reset | $A5
|  |  |  | 3 | E:NLMC3H | NuMI Loss Mon #3 Hold | $A5
|  |  |  | 4 | E:NTLMR | NuMI Total Loss Mon Reset | $A5
|  |  |  | 5 | E:NTLMH | NuMI Total Loss Mon Hold | $A5
6
|  |  |  | 7 | E:V108E7
MI-65
MI-65 | 479 | $E5 | N21 | 0 | E:E5BSD0 | Beam Sync Trig at $E5 N21 | MIBS $74
Electronics Room |  |  |  | 1 | E:E5BSD1 | Beam Sync Trig at $E5 N21 | MIBS $74
|  |  |  | 2 | E:E5BSD2 | Beam Sync Trig at $E5 N21 | MIBS $74
|  |  |  | 3 | E:E5BSD3 | Beam Sync Trig at $E5 N21 | MIBS $74
MI-65 | 377 | $E5 | N22 | 0 | E:MI65D0 | Spare TCLK Timer 0 | $A5
Electronics Room |  |  |  | 1 | E:MI65D1 | Spare TCLK Timer 1 | $A5
|  |  |  | 2 | E:MI65D2 | Spare TCLK Timer 2 | $A5
|  |  |  | 3 | E:MI65D3 | Spare TCLK Timer 3 | $A5
|  |  |  | 4 | E:MI65D4 | Spare TCLK Timer 4 | $A5
|  |  |  | 5 | E:MI65D5 | Spare TCLK Timer 5 | $A5
|  |  |  | 6 | E:MI65D6 | Spare TCLK Timer 6 | $A5
|  |  |  | 7 | E:MI65D7 | Spare TCLK Timer 7 | $A5
MI-65 Underground
Power Supply Support Room | 479 | $E6 | N14 | 0 | E:TSTGTD | Sample Time for E:TRTGTD | MIBS $74
|  |  |  | 1 | E:E6BSD1 | Beam Sync Trig at $E6 N14 | MIBS $74
|  |  |  | 2 | E:E6BSD2 | Beam Sync Trig at $E6 N14 | MIBS $74
|  |  |  | 3 | E:E6BSD3 | Beam Sync Trig at $E6 N14 | MIBS $74
Power Supply Support Room | 377 | $E6 | N16 | 0 | E:NHTD0 | NuMI Horn Time Delay 0 | $A5
|  |  |  | 1 | E:NHTD1 | NuMI Horn Time Delay 1 | $A5
|  |  |  | 2 | E:NHTD2 | NuMI Horn Time Delay 2 | $A5
|  |  |  | 3 | E:NHTD3 | NuMI Horn Time Delay 3 | $A5
|  |  |  | 4 | E:HSLBDT | Horn StrL/Bdot Mod Track | $A5
|  |  |  | 5 | E:HSLBDP | Horn StrL/Bdot Mod Peak | $A5
|  |  |  | 6 | E:HSLBDH | Horn StrL/Bdot Mod Hold | $A5
|  |  |  | 7 | E:NHTD7 | NuMI Horn Time Delay 7 | $A5
Power Supply Support Room | 377 | $E6 | N17 | 0 | E:NLMC4R | NuMI Loss Mon #4 Reset | $A5
|  |  |  | 1 | E:NLMC4H | NuMI Loss Mon #4 Hold | $A5
|  |  |  | 2 | E:NLMC5R | NuMI Loss Mon #5 Reset | $A5
|  |  |  | 3 | E:NLMC5H | NuMI Loss Mon #5 Hold | $A5
|  |  |  | 4 | E:HBLMBR | Horn AlgnBLM /Budal Reset | $A5
|  |  |  | 5 | E:HTIMMS | Horn Timing Module Stop | $A5
|  |  |  | 6 | E:HBLMBH | Horn Algn BLM/Budal Hold | $A5
|  |  |  | 7 | E:TCTGTD | Clear Time for E:TRTGTD | $A5 $00
MINOS Underground - North
Near Detector Hall | 479 | $E8 | N20 | 0 | E:E8BSD0 | Beam Sync Trig at $E8 N20 | MIBS $74
|  |  |  | 1 | E:E8BSD1 | Beam Sync Trig at $E8 N20 | MIBS $74
|  |  |  | 2 | E:E8BSD2 | Beam Sync Trig at $E8 N20 | MIBS $74
|  |  |  | 3 | E:E8BSD3 | Beam Sync Trig at $E8 N20 | MIBS $74
Near Detector Hall | 377 | $E8 | N21 | 0 | E:MNDT0 | Spare TCLK Timer 0 | $A5
|  |  |  | 1 | E:MNDT1 | Spare TCLK Timer 1 | $A5
|  |  |  | 2 | E:MNDT2 | Spare TCLK Timer 2 | $A5
|  |  |  | 3 | E:MNDT3 | Spare TCLK Timer 3 | $A5
|  |  |  | 4 | E:MNDT4 | Spare TCLK Timer 4 | $A5
|  |  |  | 5 | E:MNDT5 | Spare TCLK Timer 5 | $A5
|  |  |  | 6 | E:MNDT6 | Spare TCLK Timer 6 | $A5
|  |  |  | 7 | E:MNDT7 | Spare TCLK Timer 7 | $A5
MINOS Underground - South
Absorber | 479 | $E9 | N20 | 0 | E:E9BSD0 | Beam Sync Trig at $E9 N20 | MIBS $74
|  |  |  | 1 | E:E9BSD1 | Beam Sync Trig at $E9 N20 | MIBS $74
|  |  |  | 2 | E:E9BSD2 | Beam Sync Trig at $E9 N20 | MIBS $74
|  |  |  | 3 | E:E9BSD3 | Beam Sync Trig at $E9 N20 | MIBS $74
Absorber | 377 | $E9 | N21 | 0 | E:HMMPST | Had/M Mon Pre-Spill Trig | $A5
|  |  |  | 1 | E:HMMST | Had/M Mon Spill Trig | $A5 or $A9
|  |  |  | 2 | E:AATT2 | Spare TCLK Timer 2 | $A5
|  |  |  | 3 | E:AATT3 | Spare TCLK Timer 3 | $A5
|  |  |  | 4 | E:AATT4 | Spare TCLK Timer 4 | $A5
|  |  |  | 5 | E:AATT5 | Spare TCLK Timer 5 | $A5
|  |  |  | 6 | E:AATT6 | Spare TCLK Timer 6 | $A5
|  |  |  | 7 | E:AATT7 | Spare TCLK Timer 7 | $A5
Available for NuMI Assignment | [5 empty] | Specifically Assigned and Used by NuMI

## GOLDEN FILE of NBPS Inputs
247 | The GOLDEN FILE of NuMI BEAM PERMIT SYSTEM INPUTS | [5 empty] | Sample Time Key: Cont = SAT1 = Continuous at 5 Hz BE = SAT2 = $25 Before Extraction AE = SAT3 = 6 msec After Extraction (TD0) JBE = SAT4 = Just Before Extraction (Various TD1s) BJBE = SAT5 = Beam Cycle Just Before Extraction (TD2) | [5 empty] | 2005-08-10
10:00
Ref # | Item | ACNET Name | 200 | PCI | MADC -CHAN | Sample Time | Requirement for Permit | Anticipated Nominal | Anticipated Low Trip | Anticipated High Trip | Programmed Low Trip | Programmed High Trip | Full Scale Value at MADC
NOTE | This Color Indicates Input Has Been Masked.
60S | "60S" C204 for MADC #65 at CC $63 N21. SAT1 SAT2 SAT3 SAT4 Required Here. SAT4 Should Finish Just Before MIBS $74.
60S-1 | Extraction Kicker PS Charging Waveform Reference | I:KPS6NF |  | X | 65-5 | BE SAT2 | Charging Waveform Refererence Nominal | 50.001 kVolts | Nom - 5% | Nom + 5% | 47.5 | 52.5 | 60 kVolts
60S-2 | P-Bar Production Beam Present in NuMI Kicker Gap | I:BNKG |  | X | 65-6 | JBE SAT4 | No P-Bar Production Beam Should Be Present Before NuMI Extraction | 4 Volts | NA | 1.5 Volts | NA | 1.5 Volts | NA
60S-3 | Extraction Kicker PS Charging Waveform Buffered Reference | I:KPS6NE |  | X | 65-12 | BE SAT2 | Charging Waveform Buffered Refererence Nominal | 50.001 kVolts | Nom - 5% | Nom + 5% | 47.5 | 52.5 | 60 kVolts
60S-4 | Extraction Kicker PS Available Voltage | I:KPS6N |  | X | 65-13 | BE SAT2 | Nominal Voltage | 50.001 kVolts | Nom - 5% | Nom + 5% | 47.5 | 52.5 | 60 kVolts
60S-5 | Extraction Kicker PS Sampled Current | I:KPS6NI |  | X | 65-14 | AE SAT3 | Current Nominal | 4,912 Amps | Nom - 2% | Nom + 2% | 4940 | 5120 | 8,000 Amps
60S-6 | Kicker Flourinert Cooling System Temperature Reference | I:K6FTR |  | X | 65-15 | Cont SAT1 | Temperature Reference Nominal | 100 F | 60 F | 120 F | 60 F | 120 F | 130 F
60S-7 | Kicker Flourinert Cooling System Temperature Error | I:K6FTE |  | X | 65-16 | Cont SAT1 | Difference Between Actual and Set Point Nominal | 0 F | -5 F | +5 F | -5 F | +5 F | 70 F
60S-8 | Kicker Flourinert Cooling System Filter/Return Temp | I:K6FT2 |  | X | 65-18 | Cont SAT1 | Filter/Return Temperature Nominal | 100 F | 60 F | 120 F | 60 F | 120 F | 216 F
60S | "60S" Local 200 Module Inputs Near Top of Rack MI60124. 200 Module at CC $63 N22.
60S-9 | PCI Permit from MADC #65 |  | X |  | 200-1 | Now | All Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
60S-10 | NuMI Radiation Safety System |  | X |  | 200-2 | Now | CDC Permit | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
60S-11 | MI-52 P-Bar Production Batch Kicker System | Related to I:KPS5S | X |  | 200-3 | Now | Kicker Power Supply Status OK | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
60S-12 | NuMI Extraction Kicker Power Supply | Related to I:KPS6N | X |  | 200-4 | Now | Kicker Power Supply Status OK | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
60S-13 | No Beam in NuMI Kicker Gap | Related to I:BNKG | X |  | 200-5 | Now | No P-Bar Production Beam Should Be Present ~0.5 msec Before NuMI Extraction at I:BNKGST | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
60A | "60A" C204 for MADC #44 at CC $70 N18. SAT1 SAT3 SAT4 SAT5 Required Here.
60A-1 | MI Horiz Intensity | I:HI606N |  | X | 44-0 | BJBE SAT5 | Enough Intensity to Give Valid BPM Values | Beam Intensity Should be Greater than 1.0xE12/PP and Between Limits to Set the Internal Beam Present Flag |  |  | 5000 | 65000 | CNTS
60A-2 | Main Inj Loss Monitor Near Q612 for MI Beam Quality | I:LMQ612 |  | X | 44-1 | BJBE SAT5 | Acceptable Loss | Nominal TBD Alberto's Call | NA | TBD | NA | 0.8 Volts | Volts
60A-3 | Trim Element PS Bulk Voltage Out | I:CPS6NV |  | X | 44-2 | Cont SAT1 | Voltage Nominal | 175 Volts | 150 Volts | 190 Volts | 150 Volts | 190 Volts | 200 Volts
60A-4 | Loss Monitor Chassis #1 High Voltage Out | E:LMHV1O |  | X | 44-3 | Cont SAT1 | High Voltage Present | 2,000 Volts | 1,500 Volts | 2,500 Volts | 1,500 Volts | 2,500 Volts | 3,000 Volts
60A-5 | Loss Monitor Chassis #1 High Voltage Return | E:LMHV1R |  | X | 44-4 | Cont SAT1 | High Voltage Present | 2,000 Volts | 1,500 Volts | 2,500 Volts | 1,500 Volts | 2,500 Volts | 3,000 Volts
60A-6 | Loss Mon at KM602A | I:LMNKMA |  | X | 44-5 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-7 | Loss Mon at KM602B | I:LMNKMB |  | X | 44-6 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-8 | Loss Mon at KM602C | I:LMNKMC |  | X | 44-7 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-9 | Loss Mon at LAM60 | I:LML60 |  | X | 44-8 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-10 | Loss Mon at LAM61A | I:LML61A |  | X | 44-9 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-11 | Loss Mon at LAM61B | I:LML61B |  | X | 44-10 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-12 | Loss Mon at V100 | E:LMV100 |  | X | 44-11 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-13 | Loss Mon at Q101 | E:LMQ101 |  | X | 44-12 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-14 | Loss Mon at HV101-1 | E:LM1011 |  | X | 44-13 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-15 | Loss Mon at HV101-2 | E:LM1012 |  | X | 44-14 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-16 | Loss Mon at Q102 | E:LMQ102 |  | X | 44-15 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-17 | Loss Monitor Chassis #2 High Voltage Out | E:LMHV2O |  | X | 44-16 | Cont SAT1 | High Voltage Present | 2,000 Volts | 1,500 Volts | 2,500 Volts | 1,500 Volts | 2,500 Volts | 3,000 Volts
60A-18 | Loss Monitor Chassis #2 High Voltage Return | E:LMHV2R |  | X | 44-17 | Cont SAT1 | High Voltage Present | 2,000 Volts | 1,500 Volts | 2,500 Volts | 1,500 Volts | 2,500 Volts | 3,000 Volts
60A-19 | Loss Mon at HV101-3 | E:LM1013 |  | X | 44-18 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-20 | Loss Mon at HV101-4 | E:LM1014 |  | X | 44-19 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-21 | Loss Mon at HV101-5 | E:LM1015 |  | X | 44-20 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-22 | Loss Mon at Q103 | E:LMQ103 |  | X | 44-21 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-23 | Loss Mon at HV101-6 | E:LM1016 |  | X | 44-22 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-24 | Loss Mon at Q104 | E:LMQ104 |  | X | 44-23 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-25 | Loss Mon at HT104 | E:LMHT04 |  | X | 44-24 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-26 | Loss Mon at Q105 | E:LMQ105 |  | X | 44-25 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-27 | Loss Mon at Q106 | E:LMQ106 |  | X | 44-26 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-28 | Loss Mon at Q107 | E:LMQ107 |  | X | 44-27 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
60A-29 | MIQ Loss Monitor Chassis #6 High Voltage Out | I:LMHV6O |  | X | 44-28 | Cont SAT1 | High Voltage Present | 2,000 Volts | 1,500 Volts | 2,500 Volts | 1,500 Volts | 2,500 Volts | 3,000 Volts
60A-30 | MIQ Loss Monitor Chassis #6 High Voltage Return | I:LMHV6R |  | X | 44-29 | Cont SAT1 | High Voltage Present | 2,000 Volts | 1,500 Volts | 2,500 Volts | 1,500 Volts | 2,500 Volts | 3,000 Volts
60A-31 | Main Inj Loss Monitor Near Q608 for MI Beam Quality | I:LMQ608 |  | X | 44-46 | BJBE SAT5 | Acceptable Loss | Nominal TBD Alberto's Call | NA | TBD | NA | 1.8 Volts | Volts
60A-32 | Upstream Beam Intensity Toroid | E:TOR101 |  | X | 44-47 | AE SAT3 | Below Maximum | Maximum Set by NuMI Run Coordinator | NA | 23 E12 | NA | 23 E12 | 58.19 E12 ppp
60A-33 | Main Injector Horizontal Beam Position for Orbit Verification | I:HP606N |  | X | 44-54 | BJBE SAT5 | Nominal Position Before Extraction | + 0.5 mm But Intensity Sensitive | Nom -1.5mm | Nom +1.5mm | -1 mm | +2 mm | mm (+/- 5V Signal)
60A-34 | Main Injector Vertical Beam Position for Orbit Verification | I:VP607N |  | X | 44-55 | BJBE SAT5 | Nominal Position Before Extraction | + 4.25 mm | Nom -1.5mm | Nom +1.5mm | +2.75 mm | +5.75 mm | mm (+/- 5V Signal)
60A-35 | Main Injector Horizontal Beam Position for Orbit Verification | I:HP608N |  | X | 44-56 | BJBE SAT5 | Nominal Position Before Extraction | - 21.2 mm | Nom -1.5mm | Nom +1.5mm | - 22.7 mm | - 19.7 mm | mm (+/- 5V Signal)
60A-36 | Main Injector Vertical Beam Position for Orbit Verification | I:VP609N |  | X | 44-57 | BJBE SAT5 | Nominal Position Before Extraction | 0.0 mm | Nom -1.5mm | Nom +1.5mm | - 1.5 mm | +1.5 mm | mm (+/- 5V Signal)
60A-37 | Main Injector Intensity at V607 BPM | I:VI607N |  | X | 44-60 | JBE SAT4 | Below Some Maximum Where the Target is Safe | Above 2 E13 | NA | Presently Equivalent to 2.35 E13 | NA | 19250 | 67,100 CNTS 5V = 4 E13
60A | "60A" Local 200 Module Inputs Near Top of Rack MI60227. 200 Module at CC $70 N19.
60A-38 | PCI Permit from MADC #44 |  | X |  | 200-1 | Now | All Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
60B | "60B" C204 for MADC #38 at CC $73 N21. Only SAT2 Required Here.
60B-1 | LAM60 PS Reference | I:LAM60F |  | X | 38-0 | BE SAT2 | Current Reference Nominal | 915.01 Amps | Nom - 5% | Nom + 5% | 869.3 | 960.8 | 1,000 Amps
60B-2 | LAM60 PS Current | I:LAM60 |  | X | 38-1 | BE SAT2 | Current Nominal | 915.01 Amps | Nom - 0.5% | Nom + 0.5% | 910.43 | 919.59 | 1,000 Amps
60B-3 | LAM60 PS I Error | I:LAM60E |  | X | 38-2 | BE SAT2 | Current Error Nominal | 0 Amps | -2 Amps | + 2 Amps | -2 | 2 | 20 Amps
60B-4 | LAM61 PS Reference | I:LAM61F |  | X | 38-5 | BE SAT2 | Current Reference Nominal | 1,967 Amps | Nom - 5% | Nom + 5% | 1868.65 | 2065.35 | 2,500 Amps
60B-5 | LAM61 PS Current | I:LAM61 |  | X | 38-6 | BE SAT2 | Current Nominal | 1,967 Amps | Nom - 0.5% | Nom + 0.5% | 1957.17 | 1976.84 | 2,500 Amps
60B-6 | LAM61 PS I Error | I:LAM61E |  | X | 38-7 | BE SAT2 | Current Error Nominal | 0 Amps | -2 Amps | + 2 Amps | -2 | 2 | 25 Amps
60B-7 | V100 PS Reference | E:V100F |  | X | 38-11 | BE SAT2 | Current Reference Nominal | 2,806 Amps | Nom - 5% | Nom + 5% | 2665.7 | 2946.3 | 5,000 Amps
60B-8 | V100 PS Current | E:V100 |  | X | 38-12 | BE SAT2 | Current Nominal | 2,806 Amps | Nom - 0.5% | Nom + 0.5% | 2791.97 | 2820.03 | 5,000 Amps
60B-9 | V100 PS I Error | E:V100E |  | X | 38-13 | BE SAT2 | Current Error Nominal | 0 Amps | -2 Amps | + 2 Amps | -2 | 2 | 50 Amps
60B-10 | HV101 "B" PS Reference | E:HV01BF |  | X | 38-17 | BE SAT2 | Current Reference Nominal | TBD or 1,602.5 Amps | Nom - 5% | Nom + 5% | 1522.38 | 1682.63 | 1,750 Amps
60B-11 | HV101 PS Current | E:HV101 |  | X | 38-19 | BE SAT2 | Current Nominal | 1,602.5 Amps | Nom - 1.4% | Nom + 0.5% | 1580 | 1610.51 | 1,750 Amps
60B-12 | HV101 PS I Error | E:HV101E |  | X | 38-20 | BE SAT2 | Current Error Nominal | 0 Amps | -2 Amps | + 2 Amps | -2 | 2 | 20 Amps
60B-13 | QD101 PS Reference | E:QD101F |  | X | 38-27 | BE SAT2 | Current Reference Nominal | 56.25 Amps | Nom - 5% | Nom + 5% | 53.44 | 59.06 | 100 Amps
60B-14 | QD101 PS Current | E:QD101 |  | X | 38-28 | BE SAT2 | Current Nominal | 56.25 Amps | Nom - 2% | Nom + 2% | 55.13 | 57.38 | 100 Amps
60B-15 | QF102 PS Reference | E:QF102F |  | X | 38-31 | BE SAT2 | Current Reference Nominal | 64.63 Amps | Nom - 5% | Nom + 5% | 61.4 | 67.86 | 100 Amps
60B-16 | QF102 PS Current | E:QF102 |  | X | 38-32 | BE SAT2 | Current Nominal | 64.63 Amps | Nom - 2% | Nom + 2% | 63.34 | 65.92 | 100 Amps
60B-17 | QD103 PS Reference | E:QD103F |  | X | 38-35 | BE SAT2 | Current Reference Nominal | 63.57 Amps | Nom - 5% | Nom + 5% | 60.39 | 66.75 | 100 Amps
60B-18 | QD103 PS Current | E:QD103 |  | X | 38-36 | BE SAT2 | Current Nominal | 63.57 Amps | Nom - 2% | Nom + 2% | 62.3 | 64.84 | 100 Amps
60B-19 | QF104 PS Reference | E:QF104F |  | X | 38-39 | BE SAT2 | Current Reference Nominal | 21.85 Amps | Nom - 5% | Nom + 5% | 20.76 | 22.94 | 100 Amps
60B-20 | QF104 PS Current | E:QF104 |  | X | 38-40 | BE SAT2 | Current Nominal | 21.85 Amps | Nom - 2% | Nom + 2% | 21.41 | 22.29 | 100 Amps
60B-21 | QF105 PS Reference | E:QF105F |  | X | 38-43 | BE SAT2 | Current Reference Nominal | 60.04 Amps | Nom - 5% | Nom + 5% | 57.04 | 63.04 | 100 Amps
60B-22 | QF105 PS Current | E:QF105 |  | X | 38-44 | BE SAT2 | Current Nominal | 60.04 Amps | Nom - 2% | Nom + 2% | 58.84 | 61.24 | 100 Amps
60B-23 | QD106 PS Reference | E:QD106F |  | X | 38-47 | BE SAT2 | Current Reference Nominal | 60.04 Amps | Nom - 5% | Nom + 5% | 57.04 | 63.04 | 100 Amps
60B-24 | QD106 PS Current | E:QD106 |  | X | 38-48 | BE SAT2 | Current Nominal | 60.04 Amps | Nom - 2% | Nom + 2% | 58.84 | 61.24 | 100 Amps
60B | "60B" Local 200 Module Inputs Near Top of Rack MI60219. 200 Module at CC $73 N22.
60B-25 | PCI Permit from MADC #38 |  | X |  | 200-1 | Now | All Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
60B-26 | LAM60 Power Supply | Related to I:LAM60 | X |  | 200-2 | Now | In Regulation | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
60B-27 | LAM61 Power Supply | Related to I:LAM61 | X |  | 200-3 | Now | In Regulation | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
60B-28 | V100 Power Supply | Related to E:V100 | X |  | 200-4 | Now | In Regulation | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
60B-29 | HV101 Power Supply | Related to E:HV101 | X |  | 200-5 | Now | In Regulation | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
62A | "62A" C204 for MADC #79 at CC $6C N21. SAT1 SAT2 SAT3 Required Here.
62A-1 | Loss Monitor Chassis #3 High Voltage Out | E:LMHV3O |  | X | 79-0 | Cont SAT1 | High Voltage Present | 2,000 Volts | 1,500 Volts | 2,500 Volts | 1,500 Volts | 2,500 Volts | 3,000 Volts
62A-2 | Loss Monitor Chassis #3 High Voltage Return | E:LMHV3R |  | X | 79-1 | Cont SAT1 | High Voltage Present | 2,000 Volts | 1,500 Volts | 2,500 Volts | 1,500 Volts | 2,500 Volts | 3,000 Volts
62A-3 | Loss Mon at Q108 | E:LMQ108 |  | X | 79-2 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
62A-4 | Loss Mon at V108-1 | E:LM1081 |  | X | 79-3 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
62A-5 | Loss Mon at V108-2 | E:LM1082 |  | X | 79-4 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
62A-6 | Loss Mon at Q109 | E:LMQ109 |  | X | 79-5 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
62A-7 | Loss Mon at V108-3 | E:LM1083 |  | X | 79-6 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
62A-8 | Loss Mon at V108-4 | E:LM1084 |  | X | 79-7 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
62A-9 | Loss Mon at Q110 | E:LMQ110 |  | X | 79-8 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
62A-10 | Loss Mon at V108-5 | E:LM1085 |  | X | 79-9 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
62A-11 | Loss Mon at V108-6 | E:LM1086 |  | X | 79-10 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
62A-12 | Loss Mon at Q111 | E:LMQ111 |  | X | 79-11 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
62A-13 | Loss Mon at Q112 | E:LMQ112 |  | X | 79-12 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
62A-14 | NuMI Stub Total LM | E:TLMNS |  | X | 79-13 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 10 Rad/Sec | NA | 10 Rad/Sec | 1746 Rad/Sec
62A-15 | Upper Hobbit Total LM | E:TLMCTU |  | X | 79-14 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 10 Rad/Sec | NA | 30 Rad/Sec | 1746 Rad/Sec
62A-16 | Lower Hobbit Total LM | E:TLMCTD |  | X | 79-15 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 10 Rad/Sec | NA | 30 Rad/Sec | 1746 Rad/Sec
62A-17 | Pre-Target Total LM | E:TLMPT |  | X | 79-16 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 10 Rad/Sec | NA | 10 Rad/Sec | 1746 Rad/Sec
62A-18 | Total Loss Monitors High Voltage Out | E:TLMHVO |  | X | 79-17 | Cont SAT1 | High Voltage Present | 800 Volts | 700 Volts | 900 Volts | 700 Volts | 900 Volts | 3,000 Volts
62A-19 | Total Loss Monitors High Voltage Return | E:TLMHVR |  | X | 79-18 | Cont SAT1 | High Voltage Present | 800 Volts | 700 Volts | 900 Volts | 700 Volts | 900 Volts | 3,000 Volts
62A-20 | Loss Mon at Beginning of Big Beam Pipe | E:LMBBBP |  | X | 79-19 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
62A-21 | V108 PS Reference | E:V108F |  | X | 79-32 | BE SAT2 | Current Reference Nominal | 4,406.1 Amps | Nom - 5% | Nom + 5% | 4185.8 | 4626.41 | 5,000 Amps
62A-22 | V108 PS Current | E:V108 |  | X | 79-33 | BE SAT2 | Current Nominal | 4,406.1 Amps | Nom - 1.5% | Nom + 1.5% | 4340.01 | 4472.19 | 5,000 Amps
62A-23 | V108 PS I Error | E:V108E |  | X | 79-34 | BE SAT2 | Current Error Nominal | 0 Amps | -2 Amps | + 2 Amps | -3 | 3 | 50 Amps
62A-24 | QF107 PS Reference | E:QF107F |  | X | 79-39 | BE SAT2 | Current Reference Nominal | 60.04 Amps | Nom - 5% | Nom + 5% | 57.04 | 63.04 | 100 Amps
62A-25 | QF107 PS Current | E:QF107 |  | X | 79-40 | BE SAT2 | Current Nominal | 60.04 Amps | Nom - 2% | Nom + 2% | 58.84 | 61.24 | 100 Amps
62A-26 | QD108 PS Reference | E:QD108F |  | X | 79-43 | BE SAT2 | Current Reference Nominal | 60.04 Amps | Nom - 5% | Nom + 5% | 57.04 | 63.04 | 100 Amps
62A-27 | QD108 PS Current | E:QD108 |  | X | 79-44 | BE SAT2 | Current Nominal | 60.04 Amps | Nom - 2% | Nom + 2% | 58.84 | 61.24 | 100 Amps
62A-28 | QF109 PS Reference | E:QF109F |  | X | 79-47 | BE SAT2 | Current Reference Nominal | 60.04 Amps | Nom - 5% | Nom + 5% | 57.04 | 63.04 | 100 Amps
62A-29 | QF109 PS Current | E:QF109 |  | X | 79-48 | BE SAT2 | Current Nominal | 60.04 Amps | Nom - 2% | Nom + 2% | 58.84 | 61.24 | 100 Amps
62A-30 | QD110 PS Reference | E:QD110F |  | X | 79-51 | BE SAT2 | Current Reference Nominal | 25.62 Amps | Nom - 5% | Nom + 5% | 24.34 | 26.9 | 100 Amps
62A-31 | QD110 PS Current | E:QD110 |  | X | 79-52 | BE SAT2 | Current Nominal | 25.62 Amps | Nom - 2% | Nom + 2% | 25.11 | 26.13 | 100 Amps
62A-32 | QD111 PS Reference | E:QD111F |  | X | 79-55 | BE SAT2 | Current Reference Nominal | 78.08 Amps | Nom - 5% | Nom + 5% | 77.55 | 85.71 | 100 Amps
62A-33 | QD111 PS Current | E:QD111 |  | X | 79-56 | BE SAT2 | Current Nominal | 78.08 Amps | Nom - 2% | Nom + 2% | 76.52 | 79.64 | 100 Amps
62A-34 | QF112 PS Reference | E:QF112F |  | X | 79-59 | BE SAT2 | Current Reference Nominal | 81.63 Amps | Nom - 5% | Nom + 5% | 80 | 83.26 | 100 Amps
62A-35 | QF112 PS Current | E:QF112 |  | X | 79-60 | BE SAT2 | Current Nominal | 81.63 Amps | Nom - 2% | Nom + 2% | 80 | 83.26 | 100 Amps
62A | "62A" Local 200 Module Inputs Near Top of Rack MI62107. 200 Module at CC $6C N22.
62A-36 | PCI Permit from MADC #79 |  | X |  | 200-1 | Now | All Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
62A-37 | V108 Power Supply |  | X |  | 200-2 | Now | In Regulation | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
62A-38 | Sector Isolation Valves | E:BV100 E:BV112A E:BV112B | X |  | 200-3 | Now | All Fully Open | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
62A-39 | MI-62 LCW and Pond Water Systems | Related to E:62Winn and E:62Pinn | X |  | 200-4 | Now | All Below Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
62A-40 | LCW Temperature | E:62WTnn | PLC |  |  | Cont | 97.5 F | 90 F | NA | 105 F | NA |  | NA
62A-41 | LCW Expansion Tank Level | E:62WLnn | PLC |  |  | Cont | Above 10 Inches | 18 Inches | 10 Inches | NA |  | NA | NA
62A-42 | LCW Pump Motors (2) ON/OFF Status | E:62WEnn | PLC |  |  | Cont | One Pump Enabled to Run | One ON and One OFF | NA | NA | NA | NA | NA
62A-43 | LCW Pump Motors (2) Current | E:62WInn | PLC |  |  | Cont | Enabled Motor Current Nominal | FLA | 75% FLA | 125% FLA |  |  | NA
62A-44 | Pond Pump Motors (2) ON/OFF Status | E:62PEnn | PLC |  |  | Cont | One Pump Enabled to Run | One ON and One OFF | NA | NA | NA | NA | NA
62A-45 | Pond Pump Motors (2) Current | E:62PInn | PLC |  |  | Cont | Enabled Motor Current Nominal | FLA | 75% FLA | 125% FLA |  |  | NA
62A-46 | Pressure Differential Across Pond Pumps at PV-9 | E:62PPnn | PLC |  |  | Cont | Above Minimum | 10 PSIG | 2 PSIG | NA |  | NA | NA
62A-47 | LCW System Resistivity | E:62WA08 | PLC |  |  | Cont | Above Minimum | 3 to 5 MOhm-cm | 1 MOhm-cm | NA | 1 MOhm-cm | NA | NA
62A-48 | LCW PLC Heartbeat |  | X |  | 200-5 | Now | Thump Thump | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
65A | "65A" C204 for MADC #85 at CC $E4 N21. SAT1 SAT2 and SAT6 Required Here.
65A-1 | Intensity from H121 BPM | E:HI121P |  | X | 85-0 | AE SAT6 | Enough Intensity to Give Valid BPM Values | Beam Intensity Should be Greater than 1.0xE12/PP and Between Limits to Set the Internal Beam Present Flag |  |  | 5000 | 65000 | CNTS
65A-2 | V118 PS Current | E:V118 |  | X | 85-3 | BE SAT2 | Current Nominal | 4,125.1 Amps | Nom - 0.5% | Nom + 0.5% | 4104.47 | 4145.73 | 5,000 Amps
65A-3 | V118 PS I Error | E:V118E |  | X | 85-4 | BE SAT2 | Current Error Nominal | 0 Amps | -2 Amps | + 2 Amps | -2 | 2 | 5 Amps
65A-4 | V118 PS Reference | E:V118F |  | X | 85-9 | BE SAT2 | Current Reference Nominal | 4,173.15 Amps | Nom - 5% | Nom + 5% | 3918.85 | 4331.36 | 5,000 Amps
65A-5 | QD113 PS Reference | E:QD113F |  | X | 85-11 | BE SAT2 | Current Reference Nominal | 81.63 Amps | Nom - 5% | Nom + 5% | 77.55 | 85.71 | 100 Amps
65A-6 | QD113 PS Current | E:QD113 |  | X | 85-12 | BE SAT2 | Current Nominal | 81.63 Amps | Nom - 2% | Nom + 2% | 80 | 83.26 | 100 Amps
65A-7 | QF114 PS Reference | E:QF114F |  | X | 85-15 | BE SAT2 | Current Reference Nominal | 78.08 Amps | Nom - 5% | Nom + 5% | 74.18 | 81.98 | 100 Amps
65A-8 | QF114 PS Current | E:QF114 |  | X | 85-16 | BE SAT2 | Current Nominal | 78.08 Amps | Nom - 2% | Nom + 2% | 76.52 | 79.64 | 100 Amps
65A-9 | QF115 PS Reference | E:QF115F |  | X | 85-19 | BE SAT2 | Current Reference Nominal | 25.62 Amps | Nom - 5% | Nom + 5% | 24.34 | 26.9 | 100 Amps
65A-10 | QF115 PS Current | E:QF115 |  | X | 85-20 | BE SAT2 | Current Nominal | 25.62 Amps | Nom - 2% | Nom + 2% | 25.11 | 26.13 | 100 Amps
65A-11 | QD116 PS Reference | E:QD116F |  | X | 85-23 | BE SAT2 | Current Reference Nominal | 63.97 Amps | Nom - 5% | Nom + 5% | 60.77 | 67.17 | 100 Amps
65A-12 | QD116 PS Current | E:QD116 |  | X | 85-24 | BE SAT2 | Current Nominal | 63.97 Amps | Nom - 2% | Nom + 2% | 62.69 | 65.25 | 100 Amps
65A-13 | QF117 PS Reference | E:QF117F |  | X | 85-27 | BE SAT2 | Current Reference Nominal | 55.02 Amps | Nom - 5% | Nom + 5% | 52.27 | 57.77 | 100 Amps
65A-14 | QF117 PS Current | E:QF117 |  | X | 85-28 | BE SAT2 | Current Nominal | 55.02 Amps | Nom - 2% | Nom + 2% | 53.92 | 56.12 | 100 Amps
65A-15 | QD118 PS Reference | E:QD118F |  | X | 85-31 | BE SAT2 | Current Reference Nominal | 51.69 Amps | Nom - 5% | Nom + 5% | 49.11 | 54.27 | 100 Amps
65A-16 | QD118 PS Current | E:QD118 |  | X | 85-32 | BE SAT2 | Current Nominal | 51.69 Amps | Nom - 2% | Nom + 2% | 50.66 | 52.72 | 100 Amps
65A-17 | QF119 PS Reference | E:QF119F |  | X | 85-35 | BE SAT2 | Current Reference Nominal | 35.34 Amps | Nom - 5% | Nom + 5% | 32.3 | 37.11 | 100 Amps
65A-18 | QF119 PS Current | E:QF119 |  | X | 85-36 | BE SAT2 | Current Nominal | 35.34 Amps | Nom - 2% | Nom + 2% | 34.63 | 36.05 | 100 Amps
65A-19 | QD120 PS Reference | E:QD120F |  | X | 85-39 | BE SAT2 | Current Reference Nominal | 68.17 Amps | Nom - 5% | Nom + 5% | 64.76 | 71.58 | 100 Amps
65A-20 | QD120 PS Current | E:QD120 |  | X | 85-40 | BE SAT2 | Current Nominal | 68.17 Amps | Nom - 2% | Nom + 2% | 66.81 | 69.53 | 100 Amps
65A-21 | QF121 PS Reference | E:QF121F |  | X | 85-43 | BE SAT2 | Current Reference Nominal | 60.38 Amps | Nom - 5% | Nom + 5% | 57.36 | 63.4 | 100 Amps
65A-22 | QF121 PS Current | E:QF121 |  | X | 85-44 | BE SAT2 | Current Nominal | 60.38 Amps | Nom - 2% | Nom + 2% | 59.17 | 61.59 | 100 Amps
65A-23 | H117 PS Reference | E:H117F |  | X | 85-47 | BE SAT2 | Current Reference Nominal | 50 Amps | Nom - 5% | Nom + 5% | 47.5 | 52.5 | 100 Amps
65A-24 | H117 PS Current | E:H117 |  | X | 85-48 | BE SAT2 | Current Nominal | 50 Amps | Nom - 2% | Nom + 2% | 49 | 51 | 100 Amps
65A-25 | Beam Position from H121 | E:HP121P |  | X | 85-52 | AE SAT6 | Nominal Position +/- 1.5 mm | -1.2 mm | -2.7 mm | +0.3 mm | -2.7 mm | +0.3 mm | 60 mm
65A-26 | Beam Position from V121 | E:VP121P |  | X | 85-53 | AE SAT6 | Nominal Position +/- 1.5 mm | 1.0 mm | -0.5 mm | +2.5 mm | -0.5 mm | +2.5 mm | 60 mm
65A-27 | Beam Position from HTGT | E:HPTGTP |  | X | 85-54 | AE SAT6 | Nominal Position +/- 1.5 mm | -1.2 mm | -2.7 mm | +0.3 mm | -2.7 mm | +0.3 mm | 60 mm
65A-28 | Beam Position from VTGT | E:VPTGTP |  | X | 85-55 | AE SAT6 | Nominal Position +/- 1.5 mm | 1.0 mm | -0.5 mm | +2.5 mm | -0.5 mm | +2.5 mm | 60 mm
65A-29 | Trim Element PS Bulk Voltage Out | E:CPS65V |  | X | 85-56 | Cont SAT1 | Voltage Nominal | 175 Volts | 150 Volts | 190 Volts | 150 Volts | 190 Volts | 200 Volts
65A-30 | MI-65 BPM Functional Status / Heartbeat | E:65BPMB |  | X | 85-57 | BE SAT2 | Logic Low at Start of Flattop | 0 Volts | NA | 2 Volts | NA | 2 Volts | 10 Volts
65A-31 | MI-65 BPM Functional Status / Heartbeat | E:65BPMA |  | X | 85-58 | AE SAT6 | Logic High After Extraction | 5 Volts | 2 Volts | NA | 2 Volts | NA | 10 Volts
65A | "65A" Local 200 Module Inputs Near Top of Rack MI65103. 200 Module at CC $E4 N22.
65A-32 | PCI Permit from MADC #85 |  | X |  | 200-1 | Now | All Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
65A-33 | V118 Power Supply | Related to E:V118 | X |  | 200-2 | Now | In Regulation | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
THA | "THA" C204 for MADC #87 at CC $E6 N19. SAT1 SAT2 SAT3 SAT4 Required Here. SAT4 Timing Presently Conditional.
THA-1 | Horn Stripline Current | E:HSLI |  | X | 87-0 | JBE SAT4 | Before Extraction Nominal | 200,000 Amps | Nom - 2% | Nom + 2% | More Study Needed |  | ??? Amps
THA-2 | Horn Power Supply A Reference | E:NHSAF |  | X | 87-1 | BE SAT2 | Reference Nominal | 614 Volts Observed | Nom - 5% | Nom + 5% | 550 | 700 | 1,000 Volts
THA-3 | Horn Power Supply B Reference | E:NHSBF |  | X | 87-2 | BE SAT2 | Reference Nominal | Spare |  |  | Not in Active Service |  | 1,000 Volts
THA-4 | Horn Power Supply A Slowed Reference | E:NHSASF |  | X | 87-3 | BE SAT2 | Slow Start Reference Nominal | 604.5 Volts Observed | Nom - 5% | Nom + 5% | 550 | 700 | 1,000 Volts
THA-5 | Horn Power Supply B Slowed Reference | E:NHSBSF |  | X | 87-4 | BE SAT2 | Slow Start Reference Nominal | Spare |  |  | Not in Active Service |  | 1,000 Volts
THA-6 | Peak Horn Stripline Current | E:HSLIP |  | X | 87-5 | AE SAT3 | Peak Nominal | 200,000 Amps | Nom - 2% | Nom + 2% | More Study Needed |  | ??? Amps
THA-7 | Loss Monitor Chassis #4 High Voltage Out | E:LMHV4O |  | X | 87-6 | Cont SAT1 | High Voltage Present | 2,000 Volts | 1,500 Volts | 2,500 Volts | 1,500 Volts | 2,500 Volts | 3,000 Volts
THA-8 | Loss Monitor Chassis #4 High Voltage Return | E:LMHV4R |  | X | 87-7 | Cont SAT1 | High Voltage Present | 2,000 Volts | 1,500 Volts | 2,500 Volts | 1,500 Volts | 2,500 Volts | 3,000 Volts
THA-9 | Loss Mon at Q113 | E:LMQ113 |  | X | 87-8 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 20 Rad/Sec | 1746 Rad/Sec
THA-10 | Loss Mon at Q114 | E:LMQ114 |  | X | 87-9 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THA-11 | Loss Mon at Q115 | E:LMQ115 |  | X | 87-10 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THA-12 | Loss Mon at Q116 | E:LMQ116 |  | X | 87-11 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THA-13 | Loss Mon at Q117 | E:LMQ117 |  | X | 87-12 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THA-14 | Loss Mon at H117 | E:LMH117 |  | X | 87-13 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THA-15 | Loss Mon at Q118 | E:LMQ118 |  | X | 87-14 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THA-16 | Loss Mon at V118-1 | E:LM1181 |  | X | 87-15 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THA-17 | Loss Mon at V118-2 | E:LM1182 |  | X | 87-16 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THA-18 | Loss Mon at Q119 | E:LMQ119 |  | X | 87-17 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THA-19 | Baffle Temperature 1 | E:BAFT1 |  | X | 87-34 | Cont SAT1 | Below Extreme | 18 C | NA | 76 C | NA | 60 | Degrees C
THA-20 | Baffle Temperature 2 | E:BAFT2 |  | X | 87-35 | Cont SAT1 | Below Extreme | 18 C | NA | 76 C | NA | 60 | Degrees C
THA-21 | Targt Pile Fan Differential Pressure | E:TPCFDP |  | X | 87-45 | Cont SAT1 | Between Extremes | 6.4 Inches H2O | 4 Inches H2O | 15 Inches H2O | 4 Inches H2O | 15 Inches H2O | 25 Inches H2O
THA-22 | Targt Pile Air Supply Temperature | E:TPCAST |  | X | 87-46 | Cont SAT1 | Between Extremes | 18 C | 12 C | 26 C | 12 C | 26 C | 100 C
THA-23 | Target Helium Gas Flow - Rough | E:TGTHFR |  | X | 87-52 | Cont SAT1 | Below Nominal | Zero | NA | 0.5 | NA | 1.4 | 6 Liter/Minute
THA-24 | Arrival of Beam wrt Clock | E:NOCLU1 |  | X | 87-61 | AE | Between Extremes |  |  |  | Not Available
THA-25 | Horn BDOT Zero wrt Clock | E:NOCLU2 |  | X | 87-62 | AE | Between Extremes |  |  |  | Not Available
THA-26 | Beam Arvl - BDOT Zero | E:NOCLU3 |  | X | 87-63 | AE | Between Extremes |  |  |  | Not Available
THA | "THA" Local 200 Module Inputs Near Top of Rack THSR103. 200 Module at CC $E6 N20.
THA-27 | PCI Permit from MADC #87 |  | X |  | 200-1 | Now | All Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
THA-28 | THSR PLC Heartbeat |  | X |  | 200-2 | Now | Thump Thump | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
THA-29 | Horn Power Supply A | Related to E:NHSA | X |  | 200-3 | Now | Power Supply Ready (Rectifiers On) | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
THA-30 | Horn Power Supply B | Related to E:NHSB | X |  | 200-4 | Now | Power Supply Ready (Rectifiers On) | 2 V+ into 100 Ohm | NA | NA | Not in Active Service |  | NA
THA-31 | Target Hall (South) Air Damper Closed |  | X |  | 200-6 | Now | Air Damper Closed (by DDC Operation) | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
THB | "THB" C204 for MADC #88 at CC $E6 N18. SAT1 SAT3 Required Here.
THB-1 | Loss Monitor Chassis #5 High Voltage Out | E:LMHV5O |  | X | 88-0 | Cont SAT1 | High Voltage Present | 2,000 Volts | 1,500 Volts | 2,500 Volts | 1,500 Volts | 2,500 Volts | 3,000 Volts
THB-2 | Loss Monitor Chassis #5 High Voltage Return | E:LMHV5R |  | X | 88-1 | Cont SAT1 | High Voltage Present | 2,000 Volts | 1,500 Volts | 2,500 Volts | 1,500 Volts | 2,500 Volts | 3,000 Volts
THB-3 | Loss Mon at V118-3 | E:LM1183 |  | X | 88-2 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THB-4 | Loss Mon at V118-4 | E:LM1184 |  | X | 88-3 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THB-5 | Loss Mon at Q120 | E:LMQ120 |  | X | 88-4 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THB-6 | Loss Mon at Q121 | E:LMQ121 |  | X | 88-5 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THB-7 | Loss Mon Before TORTGT Toroid | E:LMTGTT |  | X | 88-8 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 50 Rad/Sec | 1746 Rad/Sec
THB-8 | Loss Mon at Target Shield Wall | E:LMTSW |  | X | 88-9 | AE SAT3 | Acceptable Loss | Nominal TBD | NA | 5 Rad/Sec | NA | 5 Rad/Sec | 1746 Rad/Sec
THB | "THB" Local 200 Module Inputs Near Top of Rack THSR104. 200 Module at CC $E6 N21.
THB-9 | PCI Permit from MADC #88 |  | X |  | 200-1 | Now | All Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
THB-10 | Target and Baffle RAW Skid | Related to E:TBRinn | X |  | 200-2 | Now | All Below Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
THB-11 | Discharge Minus Suction Pressure | E:TBRPnn | PLC |  |  | Cont | Within Extremes | TBD | 5 PSIG | 75 PSIG |  |  | NA
THB-12 | Supply Temperature | E:TBRTnn | PLC |  |  | Cont | Below Extreme | 95 F | NA | 130 F | NA |  | NA
THB-13 | Expansion Tank Level | E:TBRLnn | PLC |  |  | Cont | Above 10 Inches | 18 Inches | 10 Inches | NA |  | NA | NA
THB-14 | Pump Motors (2) ON/OFF Status | E:TBREnn | PLC |  |  | Cont | One Pump Enabled to Run | One ON and One OFF | NA | NA | NA | NA | NA
THB-15 | Pump Motors (2) Current | E:TBRInn | PLC |  |  | Cont | Enabled Motor Current Nominal | FLA | 75% FLA | 125% FLA |  |  | NA
THB-16 | Target Helium Pressure | E:BTHP01 | PLC |  |  | Cont | Positive Helium Pressure to Keep Water Out | >21 PSIG | 21 PSIG | NA |  | NA | NA
THB-17 | Horn 1 RAW Skid | Related to E:H1Rinn | X |  | 200-3 | Now | All Below Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
THB-18 | Discharge Minus Suction Pressure | E:H1RPnn | PLC |  |  | Cont | Within Extremes | 40 PSIG | 5 PSIG | 75 PSIG |  |  | NA
THB-19 | Supply Temperature | E:H1RTnn | PLC |  |  | Cont | Below Extreme | 70 F | NA | 90 F | NA |  | NA
THB-20 | Expansion Tank Level | E:H1RLnn | PLC |  |  | Cont | Above 10 Inches | 24 Inches | 10 Inches | NA |  | NA | NA
THB-21 | Pump Motors (2) ON/OFF Status | E:H1REnn | PLC |  |  | Cont | One Pump Enabled to Run | One ON and One OFF | NA | NA | NA | NA | NA
THB-22 | Pump Motors (2) Current | E:H1RInn | PLC |  |  | Cont | Enabled Motor Current Nominal | FLA | 75% FLA | 125% FLA |  |  | NA
THB-23 | Horn 2 RAW Skid | Related to E:H2Rinn | X | PLC | 200-4 | Now | All Below Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
THB-24 | Discharge Minus Suction Pressure | E:H2RPnn | PLC |  |  | Cont | Within Extremes | 40 PSIG | 5 PSIG | 75 PSIG |  |  | NA
THB-25 | Supply Temperature | E:H2RTnn | PLC |  |  | Cont | Below Extreme | 70 F | NA | 90 F | NA |  | NA
THB-26 | Expansion Tank Level | E:H2RLnn | PLC |  |  | Cont | Above 10 Inches | 24 Inches | 10 Inches | NA |  | NA | NA
THB-27 | Pump Motors (2) ON/OFF Status | E:H2REnn | PLC |  |  | Cont | One Pump Enabled to Run | One ON and One OFF | NA | NA | NA | NA | NA
THB-28 | Pump Motors (2) Current | E:H2RInn | PLC |  |  | Cont | Enabled Motor Current Nominal | FLA | 75% FLA | 125% FLA |  |  | NA
THB-29 | Decay Pipe Cooling RAW Skid Upstream End | Related to E:DURinn | X |  | 200-5 | Now | All Below Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
THB-30 | Discharge Minus Suction Pressure | E:DURPnn | PLC |  |  | Cont | Within Extremes | TBD | 5 PSIG | 75 PSIG |  |  | NA
THB-31 | Temperature | E:DURTnn | PLC |  |  | Cont | Below Extreme | 70 F | NA | 105 F | NA |  | NA
THB-32 | Expansion Tank Level | E:DURLnn | PLC |  |  | Cont | Above 10 Inches | 24 Inches | 10 Inches | NA |  | NA | NA
THB-33 | Pump Motors (2) ON/OFF Status | E:DUREnn | PLC |  |  | Cont | One Pump Enabled to Run | One ON and One OFF | NA | NA | NA | NA | NA
THB-34 | Pump Motors (2) Current | E:DURInn | PLC |  |  | Cont | Enabled Motor Current Nominal | FLA | 75% FLA | 125% FLA |  |  | NA
THB-35 | Total Loss Monitor Gas Flow | (E:TLMGF) | X |  | 200-6 | Now | Gas Flowing | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
THB-36 | Target & Baffle RAW Flow | (E:TBR...) | X |  | 200-7 | Now | RAW Flowing | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
MSB | "MSB" Local 200 Module Inputs Near Top of Rack MSB101. 200 Module at CC $E7 N22.
No Permits are Connected at this Location. All Inputs Jumpered to Current Source.
MND | "MND" Local 200 Module Inputs Near Top of Rack MND101. 200 Module at CC $E8 N22.
No Permits are Connected at this Location. All Inputs Jumpered to Current Source.
AAT | "AAT" Local 200 Module Inputs Near Top of Rack AAT103. 200 Module at CC $E9 N22.
AAT-1 | Absorber Cooling RAW Skid | Related to E:ABRinn | X | PLC | 200-1 | Now | All Below Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
AAT-2 | Discharge Minus Suction Pressure | E:ABRPnn | PLC |  |  | Cont | Within Extremes | 20 PSIG | 5 PSIG | 50 PSIG |  |  | NA
AAT-3 | Supply Temperature | E:ABRTnn | PLC |  |  | Cont | Below Extreme | 100 F | NA | 110 F | NA |  | NA
AAT-4 | Expansion Tank Level | E:ABRLnn | PLC |  |  | Cont | Above 10 Inches | 18 Inches | 10 Inches | NA |  | NA | NA
AAT-5 | Pump Motors (2) ON/OFF Status | E:ABREnn | PLC |  |  | Cont | One Pump Enabled to Run | One ON and One OFF | NA | NA | NA | NA | NA
AAT-6 | Pump Motors (2) Current | E:ABRInn | PLC |  |  | Cont | Enabled Motor Current Nominal | FLA | 75% FLA | 125% FLA |  |  | NA
AAT-7 | Absorber Intermediate Cooling System | Related to E:ABIinn | X |  | 200-2 | Now | All Below Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
AAT-8 | Expansion Tank Level | E:ABILnn | PLC |  |  | Cont | Above 10 Inches | 18 Inches | 10 Inches | NA |  | NA | NA
AAT-9 | Pump Motors (2) ON/OFF Status | E:ABIEnn | PLC |  |  | Cont | One Pump Enabled to Run | One ON and One OFF | NA | NA | NA | NA | NA
AAT-10 | Pump Motors (2) Current | E:ABIInn | PLC |  |  | Cont | Enabled Motor Current Nominal | FLA | 75% FLA | 125% FLA |  |  | NA
AAT-11 | Decay Pipe Cooling RAW Skid - Downstream End | Related to E:DDRinn | X |  | 200-3 | Now | All Below Monitored Inputs Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
AAT-12 | Discharge Minus Suction Pressure | E:DDRPnn | PLC |  |  | Cont | Within Extremes | 120 PSIG | 50 PSIG | 150 PSIG | Now Set to 40 PSIG |  | NA
AAT-13 | Temperature | E:DDRTnn | PLC |  |  | Cont | Below Extreme | 70 F | NA | 105 F | NA |  | NA
AAT-14 | Pump Motors (2) ON/OFF Status | E:DDREnn | PLC |  |  | Cont | One Pump Enabled to Run | One ON and One OFF | NA | NA | NA | NA | NA
AAT-15 | Pump Motors (2) Current | E:DDRInn | PLC |  |  | Cont | Enabled Motor Current Nominal | FLA | 75% FLA | 125% FLA |  |  | NA
AAT-16 | Absorber Instrumentation | Related to E:ABSinn | X |  | 200-4 | Now | System Nominal | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
AAT-17 | Various Absorber Thermocouples | E:ABSTnn | PLC |  |  | Cont | Each of the Four Thermocouples Must be Below Extreme | 140 F | NA | 150 F | NA |  | NA
AAT-18 | AAT PLC Heartbeat |  | X |  | 200-5 | Now | Thump Thump | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
AAT-19 | MINOS AAT Elephant Door Air Damper Closed |  | X |  | 200-6 | Now | Air Damper Closed (by DDC Operation) | 2 V+ into 100 Ohm | NA | NA | NA | NA | NA
NuMI SAT Assignments |  |  | Location Used |  |  | SAT RESET | TCLK Event Sequence | Sample | Time Delay | Comment
SAT1 = Continuous |  |  | 60S 60A 62A 65A THA THB |  |  | $A5 | $0F $0F $0F $0F | Direct | NA | 5 Hz Rate Synchronized to $A5
SAT2 = Before Extraction |  |  | 60S 60B 62A 65A THA |  |  | 26 | $A5 $25 | Direct | NA | Sample at Beginning of Flattop
SAT3 = After Extraction |  |  | 60S 60A 62A THA THB |  |  | $A5 | $A9 | TD0 | 6 msec | Happens Only if MIBS $74 is Issued
SAT4 = Just Before NuMI Extraction but After P-Bar Extraction |  |  | 60S |  |  | 26 | $A5 $25 | TD1 | 48.9 msec | At 60S, Mainly Checking I:BNKG Just After P-Bar Beam is Out. The Setting for TD1 is Quite Critical Here. Just Missed the Kicker Fire when at 49 msec.
SAT4 = Just Before NuMI Extraction During a NuMI Only Cycle |  |  | 60A |  |  | 80 | $A5 $25 | TD1 | 40 msec | At 60A, Mainly Checking I:VI607N Against a Maximum So the Target is Not Hit with Too Much Beam.
SAT4 = Just Before Extraction |  |  | THA |  |  | 26 | $A5 $25 | TD1 | 40 msec | Expect Time Delay to be Adjusted Here
SAT5 = Beam Cycle Just Before NuMI Extraction but After P-Bar Extraction |  |  | 60A |  |  | 26 | $A5 $25 | TD2 | 48.3 msec | Mainly Checking MI Loss Monitors and Position of MI Beam Before Extraction for Orbit Verifier Function.
SAT6 = Beam Cycle After Extraction |  |  | 65A |  |  | $A5 | $19 $25 $A9 | TD3 | 100 msec | Some Extra Time Needed for BPM Electronics to Compute Intensity and Positions After a Shot.
Infrastructure Requirements for NuMI Beam Permit | [8 empty] | Current Important Timing Information
INFR-1 | MINOS Service Building Fiber Optic Repeater and CAMAC Crate $E7 | [5 empty] | Equipment Operational |  | Event |  | Time | Scale
INFR-2 | Absorber Access Tunel Fiber Optic Repeater and CAMAC Crate $E9 | [5 empty] | Equipment Operational |  | $A5 |  | 0 | sec
INFR-3 | Near Detector Hall Fiber Optic Repeater and CAMAC Crate $E8 | [5 empty] | Equipment Operational |  | 25 |  | 1.1909 | sec
INFR-4 | MI-12 Service Building Fiber Optic Repeater | [5 empty] | Equipment Operational |  | MIBS $79 (TCLK $81) |  | 1.239 | sec
INFR-5 | MI-62 Service Building Fiber Optic Repeater and CAMAC Crate $6C | [5 empty] | Equipment Operational |  | MIBS $74 (TCLK $A9) |  | 1.2401 | sec
INFR-6 | Target Hall Support Room Fiber Optic Repeater and CAMAC Crate $E6 | [5 empty] | Equipment Operational |  | P-Bar Kicker Delay |  | 24.8742 | MI Rev
INFR-7 | MI-65 Service Building Fiber Optic Repeater and CAMAC Crate $E4 | [5 empty] | Equipment Operational |  | NuMI Kicker Delay |  | 19.9031 | MI Rev
INFR-8 | MI-60 SB North Fiber Optic Repeater and CAMAC Crates $70 and $73 | [5 empty] | Equipment Operational |  | NuMI Kicker Delay |  | Approx 200 | micro sec
INFR-9 | MI-60 SB South Fiber Optic Repeater and CAMAC Crate $63 | [5 empty] | Equipment Operational |  | $25 to MIBS $79 |  | 48.096 | milli sec
INFR-10 | Cross Gallery MAC Room Repeater | [5 empty] | Equipment Operational |  | $25 to MIBS $74 |  | 49.15 | milli sec
[9 empty] | MIBS $79 to MIBS $74 |  | 1.052 | milli sec

## NuMI 200 Module Inputs
NuMI BEAM PERMIT SYSTEM - 200 MODULE INPUTS
2005-08-09
ORDER of CONNECTION of NuMI BEAM PERMIT SIGNAL
BP Signal Starts at MINOS SB ($E6) - To AAT ($E8) - To MINOS Detector Hall ($E7) - To MINOS SB ($E6) - To MI-62 SB ($6C) - To THSR ($E6) - To MI-65 SB ($E4) - To MI-60 North ($70 and $73) - To MI-60 South ($63)
"60S" at MI-60 South Equipment Room
Ref # | 200 Module Location | 200 Module Input # | Input Description (Top of Rack MI60124) (28 Characters Max)
60S-9 | CC $63 N22 | 1 | "60S" C204 / PCI Permit from MADC 65
60S-10 |  | 2 | NuMI CDC Permit (Safety Sys)
60S-11 |  | 3 | I:KPS5S Kicker Status OK
60S-12 |  | 4 | I:KPS6N Kicker Status OK
60S-13 |  | 5 | No Beam in NuMI Kicker Gap
|  | 6 thru 8 | Spare Inputs (Jumpered to Current Source)
"60A" at MI-60 North Equipment Gallery
Ref # | 200 Module Location | 200 Module Input # | Input Description (Top of Rack MI60227)
60A-38 | CC $70 N19 | 1 | "60A" C204 / PCI Permit from MADC 44
|  | 2 thru 8 | Spare Inputs (Jumpered to Current Source)
"60B" at MI-60 North Equipment Gallery
Ref # | 200 Module Location | 200 Module Input # | Input Description (Top of Rack MI60219)
60B-25 | CC $73 N22 | 1 | "60B" C204 / PCI Permit from MADC 38
60B-26 |  | 2 | I:LAM60 PS in Regulation
60B-27 |  | 3 | I:LAM61 PS in Regulation
60B-28 |  | 4 | E:V100 PS in Regulation
60B-29 |  | 5 | E:HV101 PS in Regulation
|  | 6 thru 8 | Spare Inputs (Jumpered to Current Source)
"62A" at MI-62 Service Building Controls / Kicker Room
Ref # | 200 Module Location | 200 Module Input # | Input Description (Top of Rack MI62107)
62A-36 | CC $6C N22 | 1 | "62A" C204 / PCI Permit from MADC 79
62A-37 |  | 2 | E:V108 PS in Regulation
62A-38 |  | 3 | NuMI Vacuum Valves Open (E:BV100 E:BV112A E:BV112B)
62A-39 |  | 4 | NuMI LCW Cooling OK E:MNWPLC
62A-48 |  | 5 | NuMI LCW PLC Alive
|  | 6 thru 8 | Spare Inputs (Jumpered to Current Source)
"65A" at MI-65 Service Building Electronics Room
Ref # | 200 Module Location | 200 Module Input # | Input Description (Top of Rack MI65103)
65A-32 | CC $E4 N22 | 1 | "65A" C204 / PCI Permit from MADC 85
65A-33 |  | 2 | E:V118 PS in Regulation
|  | 3 thru 8 | Spare Inputs (Jumpered to Current Source)
"THA" at Target Hall Power Supply Support Room Underground of MI-65 Service Building
Ref # | 200 Module Location | 200 Module Input # | Input Description (Top of Rack THSR103)
THA-27 | CC $E6 N20 | 1 | "THA" C204 / PCI Permit from MADC 87
THA-28 |  | 2 | Target Hall PLC Alive
THA-29 |  | 3 | E:NHSA Horn PS Rectifiers On
THA-30 |  | 4 | E:NHSB Horn PS Rectifiers On
|  | 5 | Spare Input (Jumpered to Current Source)
THA-31 |  | 6 | Targt Hall Air Damper Closed
|  | 7 and 8 | Spare Inputs (Jumpered to Current Source)
"THB" at Target Hall Power Supply Support Room Underground of MI-65 Service Building
Ref # | 200 Module Location | 200 Module Input # | Input Description (Top of Rack THSR104)
THB-9 | CC $E6 N21 | 1 | "THB" C204 / PCI Permit from MADC 88
THB-10 |  | 2 | Target & Baffle RAW Skid OK (Includes Target Helium Pressure E:BTHP01)
THB-17 |  | 3 | Horn 1 RAW Skid OK
THB-23 |  | 4 | Horn 2 RAW Skid OK
THB-29 |  | 5 | Decay Pipe US RAW Skid OK
THB-35 |  | 6 | Total Loss Mon Gas Flow OK
THB-36 |  | 7 | Target & Baffle RAW Flow OK
|  | 8 | Spare Input (Jumpered to Current Source)
"MSB" at MINOS Service Building Northwest Mechanical/Electrical Area
Ref # | 200 Module Location | 200 Module Input # | Input Description (Top of Rack MSB101)
MSB | CC $E7 N22 | 1 thru 8 | Spare Inputs (Jumpered to Current Source)
"MND" at MINOS Near Detector Hall Underground of MINOS Service Building
Ref # | 200 Module Location | 200 Module Input # | Input Description (Top of Rack MND101)
MND | CC $E8 N22 | 1 thru 8 | Spare Inputs (Jumpered to Current Source)
"AAT" at Absorber Access Tunnel Upstream End Underground of MINOS Service Building
Ref # | 200 Module Location | 200 Module Input # | Input Description (Top of Rack AAT103)
AAT-1 | CC $E9 N22 | 1 | Absorber RAW Skid OK
AAT-7 |  | 2 | Absorber Interm Cooling OK
AAT-11 |  | 3 | Decay Pipe DS RAW Skid OK
AAT-16 |  | 4 | Absorber Temperature OK
AAT-18 |  | 5 | Absorber PLC Alive
AAT-19 |  | 6 | AAT Air Damper Closed
|  | 7 and 8 | Spare Inputs (Jumpered to Current Source)

## Hardware Requirements
SUMMARY OF CONTROLS HARDWIRE REQUIREMENTS
Hardware Type and Location | 052 | 118 | 178 | 184 | 200 | 201 | 204 & PCI | 217 | 218 | 284 | 290 | 333 | 377 | 453 | 466 | 468 | 479 | 12 Bit MADC | 14 Bit MADC | SWIC SCANNER | PLC | CAMAC CRATE and TSCC | NIM BIN | VME | NEW ACNET CONSOLE | NEW & USED EQUIP RACKS
60S |  |  |  |  | 1 |  | 1 | 1 |  | 1 |  | 2 | 1 |  | 1 |  | 1
60N | 2 |  |  |  | 2 |  | 2 |  |  | 1 |  |  | 1 | 3 | 7 | 4 | 1 |  |  | 5 | 1 |  |  | 1
62SB |  |  |  |  | 1 |  | 1 | [7 empty] | 6 | 1 | 1 |  |  |  | 1 |  |  |  |  | 4 Used
65SB | 2 | 1 | 1 |  | 1 |  | 1 |  |  |  | 2 |  | 1 | 3 | 10 | 1 | 1 | 1 | 1 | 5 | 1 | 2 | 1 | 2 | 1 | 9 New
THSR |  |  | 1 |  | 2 |  | 2 |  |  | 1 | 2 |  | 2 |  |  | 2 | 1 |  | 2 |  | 1 | 1 | 1 | 1 | 1 | 9 New
MSB |  |  | 1 | 1 | 1 | 1 |  |  |  |  | 1 | [6 empty] | 1 |  |  |  | 1 |  |  |  | 2 Used
MND |  |  | 1 | 1 | 1 |  |  |  | 1 |  | 1 |  | 1 |  |  |  | 1 | 1 |  |  | 1 | 1 |  |  |  | 2 New
AAT | 5 |  | 1 |  | 1 | [5 empty] | 1 |  | 1 |  |  |  | 1 | 1 or 0 | 0 or 1 | 4 | 1 | 1 | 2 | 1 | 1 | 6 Used
Total Required | 9 | 1 | 5 | 2 | 10 | 1 | 7 | 1 | 1 | 3 | 7 | 2 | 7 | 6 | 24 | 8 | 7 | 4 or 3 | 3 or 4 | 14 | 6 | 6 | 4 | 5 | 3 | 20 New 12 Used
FIRUS by Legan & Flores, L.L.P., P.C.
CATV by Jackson & Cunneen, L.L.P., P.C.
Target and Horn Motion Control by Legan & Flores, L.L.P., P.C.
The 216 Module Accepts 24 Volt Status. The 217 Module Accepts 5 Volt Status.
The 466 Module Requires a Special I/O Paddle Board for 24 Volt Status
MADC Utility is 14 Bit Resolution Unless Otherwise Noted
TWINAX CONVENTION Cable End: Pin is Plus, Socket is Minus. Analog Entry Box Bulkhead: Socket is Plus, Pin is Minus.

## Desired MI Crate Space
NuMI Module Installations in Existing Main Injector CAMAC Crates
Crate $63 at MI-60 South |  |  |  | Crate $70 at MI-60 North |  |  |  | Crate $73 at MI-60 North
Slot | Module | Name | Notes | Slot | Module | Name | Notes | Slot | Module | Name | Notes
1 | 284 |  | If Needed | 1 | 453 |  |  | 1 | 377
2 | 377 |  |  | 2 |  |  |  | 2 | 468 | I:LAM60 | Lambertson
3 | 377 |  |  | 3 | 453 |  |  | 3
4 |  |  |  | 4 |  |  |  | 4 | 468 | I:LAM61 | Lambertson (2)
5 | 166 | I:MDAT60 |  | 5 | 453 |  |  | 5
6 | 166 | I:MDAT61 |  | 6 |  |  |  | 6 | 468 | E:V100 | C Magnet
7 | 466 | I:KPS6N | Extraction Kicker | 7 | 052 | E:PM101V+ | Clearing Voltage | 7
8 | 217 | I: | Fluorinert Set Pt | 8 | 052 | E:PM112V | Clearing Voltage | 8 | 468 | E:HV101 | EPB String of 6
9 |  |  |  | 9 |  |  |  | 9
10 |  |  |  | 10 |  |  |  | 10 | 466 | E:QD101
11 |  |  |  | 11 |  |  |  | 11 | 466 | E:QF102
12 |  |  |  | 12 |  |  |  | 12 | 466 | E:QD103
13 |  |  |  | 13 |  |  |  | 13 | 466 | E:QF104
14 |  |  |  | 14 |  |  |  | 14 | 466 | E:QF105
15 |  |  |  | 15 | 284 | E:TR101D | Upstream Beam Int | 15 | 466 | E:QD106
16 |  |  |  | 16 | 377 |  | TCLK Timing | 16 | 466 | Spare | Formerly E:H104
17 | 333 |  | Event Scaler | 17 | 479 |  | MIBS Timing | 17
18 | 119 |  |  | 18 | 204 | NuMI BPS | PCI to MADC #44 | 18
19 | 377 |  | If Needed | 19 | 200 | NuMI BPS |  | 19 | 218
20 | 479 |  | MIBS Timing | 20 | 200 | MI BPS |  | 20 | 178
21 | 204 | NuMI BPS | PCI to MADC #65 | 21 | 200 | Recyl BPS |  | 21 | 204 | NuMI BPS | PCI to MADC #38
22 | 200 | NuMI BPS |  | 22 |  |  |  | 22 | 200 | NuMI BPS
23 | 290 | MADC #65 | 14 Bit MADC | 23 | 290 | MADC #44 | 12 Bit MADC | 23 | 290 | MADC #38 | 14 Bit MADC
24 | TSCC | ADR $63 | Main Injector FE | 24 | TSCC | ADR $70 | Main Injector FE | 24 | TSCC | ADR $73 | Main Injector FE
25 |  |  |  | 25 |  |  |  | 25
Crate $74 at MI-60 North |  |  |  | Crate $6A at MI-62 |  |  |  | Crate $6C at MI-62
Slot | Module | Name | Notes | Slot | Module | Name | Notes | Slot | Module | Name | Notes
1 | 453 |  |  | 1 |  |  |  | 1 | 468 | E:V108 | 6 B2 Dipoles
2 |  |  |  | 2 | 377 |  |  | 2
3 | 453 |  |  | 3 | 479 |  |  | 3 | 466 | E:QF107
4 |  |  |  | 4 | 479 |  | MIBS Timing | 4 | 466 | E:QD108
5 | 453 |  |  | 5 |  |  |  | 5 | 466 | E:QF109
6 |  |  |  | 6 |  |  |  | 6 | 466 | E:QD110
7 | 453 |  |  | 7 |  |  |  | 7 | 466 | E:QD111
8 |  |  |  | 8 |  |  |  | 8 | 466 | E:QF112
9 |  |  |  | 9 | 119 |  |  | 9 | 119 | E:TLMHVS
10 |  |  |  | 10 | 119 |  |  | 10
11 | 118 |  |  | 11 | 119 |  |  | 11
12 | 453 |  | Trim Elements Installed | 12 |  |  |  | 12
13 |  |  |  | 13 |  |  |  | 13
14 | 453 |  | Trim Elements Installed | 14 |  |  |  | 14
15 |  |  |  | 15 |  |  |  | 15
16 | 453 |  | Trim Elements Installed | 16 | 183 |  |  | 16
17 |  |  |  | 17 |  |  |  | 17
18 | 453 |  |  | 18 |  |  |  | 18
19 |  |  |  | 19 |  |  |  | 19
20 |  |  |  | 20 | 200 | MI BPS |  | 20
21 | 290 | MADC #77 | 14 Bit MADC | 21 |  |  |  | 21 | 204 | NuMI BPS | PCI to MADC #79
22 | 290 | MADC #70 | 14 Bit MADC | 22 |  |  |  | 22 | 200 | NuMI BPS
23 | 290 | MADC #61 | 14 Bit MADC | 23 | 290 | MADC #66 | 14 Bit MADC | 23 | 290 | MADC #79 | 14 Bit MADC
24 | TSCC | ADR $74 | Main Injector FE | 24 | TSCC | ADR $6A | Main Injector FE | 24 | TSCC | ADR $6C | Main Injector FE
25 |  |  |  | 25 |  |  |  | 25
| Shaded Box Denotes NuMI Equipment |  |  |  | Shaded Slot Number Indicates That the Desired NuMI Module is Installed

## New Crate Space
NuMI Module Installations in New CAMAC Crates
Crate $E4 at MI-65 SB Electronics Room |  |  |  | Crate $E5 at MI-65 SB Electronics Room |  |  |  | Crate $E6 at Target Hall Support Room
Slot | Module | Name | Notes | Slot | Module | Name | Notes | Slot | Module | Name | Notes
1 | 468 | E:V118 | Controls Three 500 kW PEIs | 1 | 453 | E:VT114 + 3 More | Trim Elements | 1 | 468 | E:NHSA | NuMI Horn PS
2 |  |  |  | 2 |  |  |  | 2
3 | 466 | E:QD113 |  | 3 | 453 | E:HT117 + 3 More | Trim Elements | 3 | 468 | E:NHSB | NuMI Horn PS
4 | 466 | E:QF114 |  | 4 |  |  |  | 4
5 | 466 | E:QF115 |  | 5 | 453 | E:VT121 + 3 Spare | Trim Elements | 5 | Kluge | Slow Start | By Bourkland and Biggs
6 | 466 | E:QD116 |  | 6 |  |  |  | 6
7 | 466 | E:QF117 |  | 7 | 052 | E:PM114V+ | Clearing Voltage | 7
8 | 466 | E:QD118 |  | 8 | 052 | E:PMTGTV | Clearing Voltage | 8
9 | 466 | E:QF119 |  | 9 | 118 | E:CPS65 | Trim Element PS | 9
10 | 466 | E:QD120 |  | 10 |  |  |  | 10
11 | 466 | E:QF121 |  | 11 |  |  |  | 11
12 | 466 | E:H117 | 200 Turn Trim | 12 |  |  |  | 12
13 |  |  |  | 13 |  |  |  | 13 | 284 | E:TRTGTD | Downstrm Beam Int
14 |  |  |  | 14 |  |  |  | 14 | 479 |  | MIBS Timing
15 |  |  |  | 15 |  |  |  | 15 | 178 |  | TCLK Events
16 |  |  |  | 16 |  |  |  | 16 | 377 | E:THSRT8/F | TCLK Timing
17 |  |  |  | 17 |  |  |  | 17 | 377 | E:THSRT0/7 | TCLK Timing
18 |  |  |  | 18 |  |  |  | 18 | 204 | NuMI BPS | PCI to MADC #88
19 |  |  |  | 19 |  |  |  | 19 | 204 | NuMI BPS | PCI to MADC #87
20 |  |  |  | 20 | 178 |  | TCLK Events | 20 | 200 | NuMI BPS
21 | 204 | NuMI BPS | PCI to MADC #85 | 21 | 479 |  | MIBS Timing | 21 | 200 | NuMI BPS
22 | 200 | NuMI BPS |  | 22 | 377 |  | TCLK Timing | 22 | 290 | MADC #88 | 14 Bit MADC
23 | 290 | MADC #85 | 14 Bit MADC | 23 | 290 | MADC #86 | 12 Bit MADC | 23 | 290 | MADC #87 | 14 Bit MADC
24 | TSCC | ADR $E4 | Main Injector FE | 24 | TSCC | ADR $E5 | Main Injector FE | 24 | TSCC | ADR $E6 | Main Injector FE
25 |  |  |  | 25 |  |  |  | 25
Crate $E7 at MINOS SB Mechanical Room |  |  |  | Crate $E8 at MINOS Near Detector Hall |  |  |  | Crate $E9 at Absorber Access Tunnel
Slot | Module | Name | Notes | Slot | Module | Name | Notes | Slot | Module | Name | Notes
1 | 184 |  | Needed for Sumps | 1 | 218 |  | Analysis Magnet | 1 | 052 | E:HMHV1+ | Hadron Mon HV
2 |  |  |  | 2 | 184 |  | If Needed | 2 | 052 | E:HMHV5+ | Hadron Mon HV
3 |  |  |  | 3 |  |  |  | 3 | 052 | E:MM1HV1+ | Muon Mon 1 HV
4 |  |  |  | 4 |  |  |  | 4 | 052 | E:MM2HV1+ | Muon Mon 2 HV
5 |  |  |  | 5 |  |  |  | 5 | 052 | E:MM3HV1+ | Muon Mon 3 HV
6 |  |  |  | 6 |  |  |  | 6
7 |  |  |  | 7 |  |  |  | 7
8 |  |  |  | 8 |  |  |  | 8
9 |  |  |  | 9 |  |  |  | 9
10 |  |  |  | 10 |  |  |  | 10
11 |  |  |  | 11 |  |  |  | 11
12 |  |  |  | 12 |  |  |  | 12
13 |  |  |  | 13 |  |  |  | 13
14 |  |  |  | 14 |  |  |  | 14
15 |  |  |  | 15 |  |  |  | 15
16 |  |  |  | 16 |  |  |  | 16
17 |  |  |  | 17 |  |  |  | 17
18 |  |  |  | 18 |  |  |  | 18
19 |  |  |  | 19 | 178 |  | TCLK Events | 19 | 178 |  | TCLK Events
20 | 178 |  | TCLK Events | 20 | 479 |  | MIBS Timing | 20 | 479 |  | MIBS Timing
21 | 201 | NuMI BPS | Origin Module | 21 | 377 |  | TCLK Timing | 21 | 377 |  | TCLK Timing
22 | 200 | NuMI BPS | No Inputs | 22 | 200 | NuMI BPS | No Inputs | 22 | 200 | NuMI BPS
23 | 290 | MADC #89 | 12 Bit MADC | 23 | 290 | MADC #90 | 12 Bit MADC | 23 | 290 | MADC #91 | 12 or 14 Bit MADC
24 | TSCC | ADR $E7 | Main Injector FE | 24 | TSCC | ADR $E8 | Main Injector FE | 24 | TSCC | ADR $E9 | Main Injector FE
25 |  |  |  | 25 |  |  |  | 25
| All Installed Equipment Relates to NuMI |  |  |  | Shaded Slot Number Indicates That the Desired NuMI Module is Installed

## Temperature & Humidity Monitors
Temperature and Humidity Monitors for the NuMI Project
Type | ACNET Name | Description (24 Char) | Monitor Location | Electronics Location | Cable | MADC | Chan
Temperature | E:TTNSTB | MI NuMI Stub Temp | NuMI Stub | MI-62 MI62106 | OA 0130 | 67 | 6
Humidity | E:THNSTB | MI NuMI Stub Humidity | NuMI Stub | MI-62 MI62106 | OA 0131 | 67 | 7
Temperature | E:TTUHOB | NuMI Upper Hobbit Temp | Mid Point of Upper Hobbit | MI-65 MI65108 | OA 0196 | 86 | 55
Humidity | E:THUHOB | NuMI Upper Hobbit Humid | Mid Point of Upper Hobbit | MI-65 MI65108 | OA 0197 | 86 | 56
Temperature | E:TTLHOB | NuMI Lower Hobbit Temp | Mid Point of Lower Hobbit | MI-65 MI65108 | OA 0198 | 86 | 57
Humidity | E:THLHOB | NuMI Lower Hobbit Humid | Mid Point of Lower Hobbit | MI-65 MI65108 | OA 0199 | 86 | 58
Temperature | E:TTPTGT | NuMI Pre-Tgt Temp | Mid Point of Pre-Target | MI-65 MI65108 | OA 0200 | 86 | 59
Humidity | E:THPTGT | NuMI Pre-Tgt Humidity | Mid Point of Pre-Target | MI-65 MI65108 | OA 0201 | 86 | 60
Temperature | E:ERT65E | MI65 Elec Rm Temp | MI-65 Electronics Room | MI-65 MI65108 | OA 0137 | 86 | 61
Temperature | E:ERT65P | MI65 PS Rm Temp | MI-65 Electrical (PS) Room | MI-65 MI65108 | OA 0138 | 86 | 62
Humidity | E:ERH65P | MI65 PS Rm Humidity | MI-65 Electrical Room | MI-65 MI65108 | OA 0139 | 86 | 63
Temperature | E:CBT65 | MI65 Crane Bay Temp | MI-65 Crane Bay North Wall | MI-65 MI65108 | OA 0294 | 86 | 53
Humidity | E:CBH65 | MI65 Crane Bay Humidity | MI-65 Crane Bay North Wall | MI-65 MI65108 | OA 0295 | 86 | 54
Temperature | E:TTPSSR | NuMI PS Sprt Rm Temp | Power Supply Support Room | PS Sprt Rm THSR104 | OA 0134 | 88 | 27
Humidity | E:THPSSR | NuMI PS Sprt Rm Humid | Power Supply Support Room | PS Sprt Rm THSR104 | OA 0135 | 88 | 28
Temperature | E:TTRAWR | NuMI RAW Room Temp | RAW Support Room | PS Sprt Rm THSR104 | OA 0136 | 88 | 29
Temperature | E:TTTGTH | NuMI Target Hall Temp | Mid West Wall of Target Hall | PS Sprt Rm THSR104 | OA 0132 | 88 | 30
Humidity | E:THTGTH | NuMI Target Hall Humidty | Mid West Wall of Target Hall | PS Sprt Rm THSR104 | OA 0133 | 88 | 31
Temperature | E:TTHADM | NuMI Hadron Mon Temp | South Absorber Hall | Upper AAT AAT102 | OA 0140 | 91 | 24
Temperature | E:TTMA1 | NuMI Muon Alcove 1 Temp | North Absorber Hall | Upper AAT AAT102 | OA 0141 | 91 | 25
Temperature | E:TTMA2 | NuMI Muon Alcove 2 Temp | Muon Alcove 2 | Upper AAT AAT102 | OA 0234 | 91 | 26
Temperature | E:TTMA3 | NuMI Muon Alcove 3 Temp | Muon Alcove 3 | Upper AAT AAT102 | OA 0235 | 91 | 27
Temperature | E:TTAATU | NuMI Upper AAT Temp | South End of AAT by Racks | Upper AAT AAT102 | OA 0236 | 91 | 28
Humidity | E:THAATU | NuMI Upper AAT Humidity | South End of AAT by Racks | Upper AAT AAT102 | OA 0237 | 91 | 29
Temperature | E:TTAATL | NuMI Lower AAT Temp | North End of AAT | Upper AAT AAT102 | OA 0238 | 91 | 30
Humidity | E:THAATL | NuMI Lower AAT Humidity | North End of AAT | Upper AAT AAT102 | OA 0239 | 91 | 31
Summary: 9 NIM Modules 15 Temperature Sensors 9 Humidity Sensors

## General PLC Conventions
NuMI PLC Systems
Summary of Instrumentation and Control Signals
Guidelines for ACNET Database Names and Device Descriptions
General Name | System Description | Instrumentation Types
E:62W i nn | MI-62 LCW System | Character i = | Description
E:62P i nn | Pond Water Cooling for MI-62 LCW System (PV-9) | A | Alarm
E:BTHinn | Baffle, Target and Horn Instrumentation | E | Enable
E:TBR i nn | Target & Baffle RAW System | F | Flow
E:H1R i nn | Horn 1 RAW System | H | Humidity
E:H2R i nn | Horn 2 RAW System | I | Current
E:DUR i nn | Decay Pipe Cooling RAW System - Upstream | L | Liquid Level
E:TPCinn | Target Pile Air Cooling System | P | Pressure
E:ABSinn | Absorber Instrumentation | R | Resistivity
E:DPVinn | Decay Pipe Vacuum System | S | Motor or Actuator
E:ABR i nn | Absorber Cooling RAW System | T | Temperature
E:ABI i nn | Intermediate Water Cooling for Absorber RAW System | V | Valve
E:DDR i nn | Decay Pipe Cooling RAW System - Downstream | W | Three Way Control Valve
E:MNW i nn | MINOS LCW System | X | Position
|  | Characters nn = | Description
|  | 01 thru 99 Max | Number for a Given Type