## Model
[16 empty] | PRESSURE | TEMP | DENSITY | SFTC | 1/f(T)
HXTU Temperature profile within pressurized He II, Yuenian Huang, 2/16/00 | [15 empty] | [bar] | [K] | [g/cm3] | [W3/cm5-g] | [W3/cm5-K]
(All dimensions are in cm, except listed.) | [15 empty] | 1.45 | 1.8 | 0.148 | 1.155 | 1155
[16 empty] | 1.45 | 1.81 | 0.148 | 1.21 | 1210
[6 empty] | Top | 753.3132 | cm | [7 empty] | 1.45 | 1.82 | 0.148 | 1.263 | 1263
[6 empty] | Bottom | 753.3386 | cm | [7 empty] | 1.45 | 1.83 | 0.148 | 1.316 | 1316
[16 empty] | 1.45 | 1.84 | 0.148 | 1.367 | 1367
|  | 331.7875 | [6 empty] | 421.5257 | [6 empty] | 1.45 | 1.85 | 0.148 | 1.415 | 1415
[16 empty] | 1.45 | 1.86 | 0.148 | 1.462 | 1462
|  | 60.9981 | [7 empty] | 57.6453 | [5 empty] | 1.45 | 1.87 | 0.1481 | 1.505 | 1505
[16 empty] | 1.45 | 1.88 | 0.1481 | 1.544 | 1544
[16 empty] | 1.45 | 1.89 | 0.1481 | 1.579 | 1579
[16 empty] | 1.45 | 1.9 | 0.1481 | 1.608 | 1608
10.3124 | 28.575 |  | 317.5 | [5 empty] | 383.4384 |  |  | 13.4874 | 16.0274 | 17.145 |  | 1.45 | 1.91 | 0.1481 | 1.632 | 1632
[16 empty] | 1.45 | 1.92 | 0.1481 | 1.65 | 1650
[16 empty] | 1.45 | 1.93 | 0.1482 | 1.66 | 1660
[16 empty] | 1.45 | 1.94 | 0.1482 | 1.662 | 1662
[16 empty] | 1.45 | 1.95 | 0.1482 | 1.656 | 1656
[16 empty] | 1.45 | 1.96 | 0.1482 | 1.641 | 1641
[16 empty] | 1.45 | 1.97 | 0.1482 | 1.617 | 1617
[16 empty] | 1.45 | 1.98 | 0.1483 | 1.582 | 1582
[16 empty] | 1.45 | 1.99 | 0.1483 | 1.522 | 1522
[16 empty] | 1.45 | 2 | 0.1483 | 1.441 | 1441
6.5214
4.1275
16.0274 | 17.145 |  | 39.7256 | 12.7 | 269.2146 |  |  |  | 365.4806 | 12.7 | 6.858 | 13.4874 | 16.0274 | 8.5725
|  | 330.2127 | [6 empty] | 423.1259
Thermometer
Heater

## Calculation
Equation |  |  | q is constant |  |  | q is proportional to x
1/f(T) | [W^3/cm^5-K] | 1200
Left side |  | Module 1 | Module 2&3 | Module 4 | Right side |  | Module 1 | Module 2&3 | Module 4
Q | [W] | 50 | 50 | 50 | Q | [W] | 50 | 50 | 50
ID_1 | [cm] | 13.4493 | 13.4493 | 13.4493 | ID_1 | [cm] | 13.4493 | 13.4493 | 13.4493
A1 | [cm^2] | 142.0657 | 142.0657 | 142.0657 | A1 | [cm^2] | 142.0657 | 142.0657 | 142.0657
Heater | [cm^2] | 8.5403 | 8.5403 | 8.5403 | Heater | [cm^2] | 8.5403 | 8.5403 | 8.5403
x-section A | [cm^2] | 133.5254 | 133.5254 | 133.5254 | x-section A | [cm^2] | 133.5254 | 133.5254 | 133.5254
q1 | [W/cm^2] | 0.18723 | 0.18723 | 0.18723 | q1 | [W/cm^2] | 0.18723 | 0.18723 | 0.18723
L1 | [cm] | 269.2146 | 269.2146 | 269.2146 | L1 | [cm] | 365.4806 | 365.4806 | 365.4806
DT1 | [mK] | 0.36812 | 0.36812 | 0.36812 | DT1 | [mK] | 0.49975 | 0.49975 | 0.49975
ID_2 | [cm] | 8.2804 | 8.2804 | 8.2804 | ID_2 | [cm] | 8.2804 | 8.2804 | 8.2804
A2 | [cm^2] | 53.8508 | 53.8508 | 53.8508 | A2 | [cm^2] | 53.8508 | 53.8508 | 53.8508
q2 | [W/cm^2] | 0.46425 | 0.46425 | 0.46425 | q2 | [W/cm^2] | 0.46425 | 0.46425 | 0.46425
L2 | [cm] | 60.9981 | 60.9981 | 60.9981 | L2 | [cm] | 57.6453 | 57.6453 | 57.6453
DT2 | [mK] | 5.086 | 5.086 | 5.086 | DT2 | [mK] | 4.8065 | 4.8065 | 4.8065
ID_3 | [cm] | 8.2804 | 8.2804 | 8.2804 | ID_3 | [cm] | 8.2804 | 8.2804 | 8.2804
A3 | [cm^2] | 53.8508 | 53.8508 | 53.8508 | A3 | [cm^2] | 53.8508 | 53.8508 | 53.8508
q3 | [W/cm^2] | 0.46425 | 0.92849 | 0.92849 | q3 | [W/cm^2] | 0.92849 | 0.92849 | 0.46425
L3 | [cm] | 10.6489 | 10.6489 | 10.6489 | L3 | [cm] | 10.6489 | 10.6489 | 10.6489
DT3 | [mK] | 0.88791 | 7.1033 | 7.1033 | DT3 | [mK] | 7.1033 | 7.1033 | 0.88791
ID_4 | [cm] | 16.1468 | 16.1468 | 16.1468 | ID_4 | [cm] | 16.1468 | 16.1468 | 16.1468
OD (corru) | [cm] | 9.7536 | 9.7536 | 9.7536 | OD (corru) | [cm] | 9.7536 | 9.7536 | 9.7536
A4 | [cm^2] | 130.0508 | 130.0508 | 130.0508 | A4 | [cm^2] | 130.0508 | 130.0508 | 130.0508
q4 | [W/cm^2] | 0.19223 | 0.19223 | 0.19223 | q4 | [W/cm^2] | 0.19223 | 0.19223 | 0.19223
L4 | [cm] | 331.7875 | 331.7875 | 331.7875 | L4 | [cm] | 421.5257 | 421.5257 | 421.5257
DT4 | [mK] | 0.49102 | 0.49102 | 0.49102 | DT4 | [mK] | 0.62383 | 0.62383 | 0.62383
Total DT left |  | 6.8331 | 13.0484 | 13.0484 | Total DT right |  | 13.0333 | 13.0333 | 6.8179
Saturated helium side pressure drop and temperature difference.
Total heater's power Q, Total length L, Vapor velocity at HX exit V, Total pressure drop DP and Temperature drop DT
|  | Module 1 | Module 2&3 | Module 4
Q | [W] | 200 | 200 | 200
L | [m] | 7.5 | 7.5 | 7.5
V | [m/s] | 3.87 | 3.87 | 3.87
DP | [Pa] | 40.7 | 40.7 | 40.7
DT | [mK] | 6.7833 | 6.7833 | 6.7833
Q_section | [W] | 50 | 50 | 50
DT_section | [mK] | 1.6958 | 1.6958 | 1.6958

## Temperature profile
Calculated temperature at each location, Y. Huang
INPUT DATA
[5 empty] | Q in each module |  |  | 50 | [W] |  |  |  | This value is imported from previous sheet
[5 empty] | L |  |  | 750 | [cm]
[5 empty] | q=Q/L |  |  | 0.066667 | [W/cm]
[5 empty] | Liquid fraction |  |  | 87%
[5 empty] | Mass flow rate |  |  | 10.0037 | [g/s]
[5 empty] | Wetted fraction |  |  | 25% | [-] |  |  |  | You can change the wetted fraction of the corrugated pipe
[5 empty] | SSHX Length |  |  | 10 | [cm]
[5 empty] | Wetted fraction |  |  | 100% | [-]
[5 empty] | Q_SSHX |  |  | 2.6667 | [W]
[5 empty] | T_bath |  |  | 1.764 | [K] |  |  |  | This value is calculated by Tom Peterson
[5 empty] | DT of DP |  |  | 6.8 | [mK] |  |  |  | Caused by vapor pressure drop
[5 empty] | 1/T_bath^3 |  |  | 0.18218 | [K^-3]
[5 empty] | Thermal resistance |  |  | 10.01 | [mK/W]
[5 empty] | DT |  |  | 26.6933 | [mK]
Nominal case
Point 5 |  | 1.764 |  |  | 1.7649 |  |  | 1.7657 |  |  | 1.7666 |  |  | 1.7674 |  |  | 1.7683 |  |  | 1.7691 |  |  | 1.77 |  |  | 1.7708 | Point 4
|  |  | DT4 |  | 1.7915 | 0.62383 |  | 1.7922 |  |  | 1.7932 | 0.62383 |  | 1.7939 |  |  | 1.7949 | 0.62383 |  | 1.7956 |  |  | 1.7966 | 0.62383 |  | 1.7973 |  | #REF!
|  | 1.792 | 0.49102 |  | 1.7915 | DT4 |  | 1.7937 | 0.49102 |  | 1.7932 |  |  | 1.7954 | 0.49102 |  | 1.7949 |  |  | 1.7971 | 0.49102 |  | 1.7966
| DT3 | 0.88791 |  |  |  |  | DT3 | 7.1033 | [5 empty] | 7.1033 | [5 empty] | 7.1033 | [5 empty] | 0.88791
|  | 1.7929 | 5.086 | 0.36812 | 1.7984 |  |  | 1.8008 | 5.086 | 0.36812 | 1.8063 |  |  | 1.8025 | 5.086 | 0.36812 | 1.808 |  |  | 1.8042 | 5.086 | 0.36812 | 1.8097
[5 empty] | 1.8046 | 0.49975 | 4.8065 | 1.7993 |  |  | 1.8063 | 0.49975 | 4.8065 | 1.801 |  |  | 1.808 | 0.49975 | 4.8065 | 1.8027 |  |  | 1.8035 | 0.49975 | 4.8065 | 1.7982
|  |  | DT2 | DT1 |  | DT1 | DT2
|  |  |  | Module 1 | [5 empty] | Module 2 | [5 empty] | Module 3 | [5 empty] | Module 4