November  21, 1997

Contract  # TW-0928

SPECIAL SPECIFICATION

SECTION 02810-S

UNDERGROUND IRRIGATION SYSTEM

PART 1 - GENERAL	Page

1.01	Description of Work	2

1.02	References	2

1.03	Quality Assurance	2

1.04	Submittal	3

1.05	Delivery, Storage, and Handling	3

1.06	Job Conditions	.....................................................................................3

1.07	Warranty	............................................................................................4

1.08	Maintenance	.........................................................................................4

PART 2 - PRODUCTS

2.01	Acceptable Manufacturers	........................................................................5

2.02	Materials	............................................................................................5

PART 3 - EXECUTION

3.01	System Design	.....................................................................................8

3.02	Examination	........................................................................................8

3.03	Preparation	.........................................................................................8

3.04	Installation	..........................................................................................9

3.05	Field Quality Control	.............................................................................12

3.06	Backfilling	.........................................................................................12

3.07	Coverage and Adjustment	......................................................................13

SPECIAL SPECIFICATION

SECTION 02810

UNDERGROUND IRRIGATION SYSTEM

PART 1 - GENERAL

1.01	DESCRIPTION OF WORK

A.	Extent of underground irrigation system is shown on drawings and schedules.

B.	Related Sections:  The following sections contain requirements that relate to this Section.

1.	Plant materials, topsoil, and landscape work are specified in Division 2 Section, "Trees, Shrubs, and Ground Covers".

2.	Water distribution is specified in Division 2 Section, "Exterior Water Distribution" except as noted herein.

3.	Excavation and filling required for irrigation system installation are specified in Division 2 Section, "Earthwork".

4.	Electrical service for the automatic control system is specified in Division 16 sections.

1.02	REFERENCES

A.	The following publications are referenced in this Section:

1.	American Society of Testing and Material (ASTM):  various tests and specifications as indicated.

2.	National Electric Code.

3.	Uniform Plumbing Code.

4.	National Sanitation Foundation.

1.03	QUALITY ASSURANCE

A.	Installer Qualifications:  Licensed landscaping contracting firm with not less than 5 years experience in the type and scale of work required in this Section.

B.	Manufacturer Qualifications:  Provide underground irrigation system as a complete unit produced by acceptable manufacturers, including heads, valves, piping circuits, controls, and accessories.

1.04	SUBMITTALS

A.	Material Product Data Sheets:  Submit material product data sheets for valve boxes, backflow preventers, manual valves, automatic valves, heads, nozzles, bubblers, and automatic drain valves.

B.	Operation and Maintenance Manual:  Submit an Operation and Maintenance Manual for the irrigation system prior to final acceptance.  Include a table of contents of material and copies of material product data sheets.  Cross out irrelevant information.  Include exploded drawings of equipment components where available, source of materials, copies of contractor and material vendor business cards, copy of controller manual and diagrams, and a schedule of suggested watering times by month for each station for the first year of operation.  Provide materials in three-hole punched format, ready for insertion into a three-ring binder.  Review operation and maintenance with the SDR and staff prior to final acceptance.  Type or clearly print written information.

C.	Record Drawings:  On a SDR-furnished print of the irrigation plan, clearly mark the exact arrangement of the system, including the arrangement and sizes of all valves and main lines, intermittent pressure lines, splices, control wires, and lines under paved surfaces.  Locate features of the irrigation system using a system of specific measurements from easily identified, permanent features such as buildings, roads, and walks.  As work progresses, note on the plans in red pencil any variations in work noted.  Maintain and store record drawings on-site at all times.  No inspections will be conducted or approvals granted if record drawings are not on-site or current.  Provide record drawings to the SDR for approval prior to final acceptance.

D.	Controller Diagrams:  Prepare a waterproof, color-coded diagram for each controller keying station of the controller to valve zones.  Mount diagram inside the automatic controller door.  Provide one copy of each diagram in the Operation and Maintenance Manual.

E.	Submit all of the above in accordance with Provisions of section 1300, “Descriptive Submittals”.

1.05	DELIVERY, STORAGE, AND HANDLING

A.	Delivery and Storage:  Coordinate delivery and on-site storage location with the SDR.  Do not store PVC pipes in direct sunlight.

B.	Product Handling:  Follow manufacturer's recommended procedures for loading, unloading, stacking, transporting and handling materials and equipment.

1.06	JOB CONDITIONS

A.	Existing Conditions:

1.	Utilities:  Verify the locations and sizes of stubouts for water sources indicated on drawings as the source of water supply to the underground irrigation system.  Prior to excavation, determine the locations of all newly constructed and existing cables, conduits, sewers, water lines, and other underground utilities.  Do not damage or disturb underground utilities.  If a conflict exists between the location of underground utilities and the proposed work, notify the SDR in writing and arrange for relocations.  Proceed in the above manner if a rock layer or other unanticipated conditions are encountered underground.  Repair utility damage as directed by the SDR.

2.	Digging Permit:  Contact SDR for Digging Permit requirements.

3.	Construction:  Use extreme caution when working near existing construction.  Do not damage existing features not specifically indicated to be removed.  Repair any accidental damage as directed by the SDR.

B.	Sequencing/Scheduling:  Coordinate irrigation system with related work.  Grade site within 1 inch of finish grade prior to trenching. Install irrigation system prior to plant installation.

1.07	WARRANTY

A.	General:  Warranty underground irrigation system through the specified warranty period against operational deficiencies due to inferior material or workmanship.  Correct deficiencies immediately as directed by the SDR at no additional cost to SNL, including damage caused by such defects.

B.	Settlement:  Warranty underground irrigation system through the specified warranty period against settlement damage.  Adjust, restore, or replace pipes, valves, sprinkler heads, planting, paving, or other improvements at no additional cost to SNL.

1.08	MAINTENANCE

A.	Extra Materials:  Provide four extra pop-up heads and four extra nozzles of each type indicated and two sets of special wrenches for each type of head or nozzle.  Provide wrenches from the same manufacturer as heads and nozzles, designed for installing, removing, and adjusting heads and nozzles.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

A.	Manufacturer:  Subject to compliance with requirements, provide products as scheduled or specified in this Section. Substitutions are allowed only under provisions of section 1600.

2.02	MATERIALS

A.	Pipe and Pipe Fittings:

1.	Pipe:

a.	Pressure Pipe:  Provide pipe in accordance with Division 2 Section, "Exterior Water Distribution" or provide Schedule 40 PVC pipe meeting requirements below.

b.	Master Lines and Intermittent Pressure Laterals:  Schedule 40 PVC pipe, continuously marked with identification of the manufacturer,  type,  class,  and size, complying with ASTM D 1785 for Schedule 40 pipe and ASTM D 1784 for PVC compounds.  Provide pipe in 20-foot lengths, free of holes, foreign material, blisters, wrinkles or dents.

2.	PVC Fittings:  Schedule 40 PVC socket fitting, Type 1, Cell Classification 12454-B,  complying with  ASTM D 2466, D 2467, and D 1784.

3.	Threaded Nipples:  Schedule 80 PVC pipe.

4.	Risers:  Schedule 40 galvanized steel pipe, unless otherwise indicated.

5.	Cleaner, Primer, and Solvent Cements:

a.	Cleaner:  Uni-Weld 7300 cleaner or approved substitute.

b.	Primer:  Uni-Weld 8700 Hi-Etch purple primer, ASTM F656, or an approved substitute.

c.	Solvent Cements:  Uni-Weld 2200 clear, light viscosity type, for lateral lines, Uni-Weld 1700 gray, heavy duty viscosity type, for lateral lines larger than 2-1/2" diameter, and Uni-Weld 6700 for clear, light viscosity type for Flex/PVC connections or approved substitute.

6.	Sealing Tapes and Pastes:

a.	Threaded Connections between PVC and Metal Pipe: Rectorseal No. 100 virgin heavy duty sealing paste, Plastojoint Stick as manufactured by Lake Chemical Company, or Teflon tape.

b.	Metal to Metal Connection:  Rectorseal No. 5 slow dry, soft set pipe thread compound.

c.	PVC to PVC Connections:  Teflon tape.

d.	Plastic Irrigation Head or Plastic Valve to Pipe Connections:  Teflon tape.

7.	Pipe Lubricant:  As provided by pipe manufacturer for "O" ring gasket and pipe spigot ends.  If not provided, use I.P.S. Weld- On No. 787 gasket lubricant as manufactured by Industrial Polychemical Service.

8.	Flexible Nipples:  Cobra Connector, U.S. Patent #s  5,039,011 & 5,221,114, with 1/2" Nominal  I.P.S. heavy wall flexible  hose, as manufactured by F. P. Parker Manufacturing Co. Inc.,  230-A Coney Island Dr., Sparks, Nevada,  89431, (702) 358-7900 or (510) 657-1641,  Fax (800) 372-6272, or approved substitute.   Material is available from Neumark Inc., Albuquerque, New Mexico.

9.	Sleeves:  Schedule 40 PVC when under Contractor-installed  or removed and replaced pavement, Schedule 40 steel for sleeves under existing paving to remain.

B.	Valve Boxes:  Precast concrete, fiberglass reinforced, or other type noted on the drawings, size as indicated on drawings.

C.	Valve Cover and Frame:  Cast iron.

D.	Valves:

1.	Automatic Valves:  As indicated on drawings or approved substitute.

a.	Provide valves with a manual bleed screw on the bonnet and bleed ports protected with built-in filter.  Provide valve which may be installed at any angle and has a flow control and manual shutoff.

b.	Material:  Noncorrosive.

c.	Operation:  Open and close smoothly with low pressure loss.

d.	Solenoid:  24 volts A.C. 60 Hz, energy consumption not exceeding 6 watts.

e.	Identification:  Clearly tag with legible permanent brass waterproof label indicating the controller zone number.

2.	Manual Valves:  Curb stop per applicable sections of Underground Water Distribution specification.

E.	Controllers:  Existing on site.  Provide and install Mini-Clik Freeze Sensor, Model 401 as manufactured by Glen-Hilton Products Inc., P.O. Box 31614, Richmond, Virginia 23294, (804)264-0055.  Product is distributed locally by Ellen Irrigation Co., (505) 344-3474.

F.	Wire:

1.	UL approved for direct burial, type UF, rated for 600 volts, PVC insulated.

2.	Minimum Wire Size:  No. 16 AWG.  Manufactured in minimum 2,500- foot reels.

3.	Common Wire:  Plastic coated, white color.

4.	Control Wire:  Insulated, single-strand copper designed for 24 to 50 volts, plastic coated, red color.

5.	Copper Strand:  Meet or exceed ASTM B3.

G.	Wire Splicing Materials:  Provide watertight splices using Spears #300 connectors and #100 glue, 3M brand, DBY connectors, or approved substitute.

H.	Backflow Preventers:  As indicated on drawings.

I.	Flood Bubblers and Spray Heads:

1.	General:  As scheduled, Rain Bird Sprinkler Mfg. Corp. or approved substitute.  Include a serviceable screen on the bubbler and spray heads to prevent foreign materials from entering the sprinkler.  Set flow adjustment to ensure even coverage and to avoid overspray.

2.	Bubbler:  Fixed pattern.

3.	Pop-Up Spray:  Fixed pattern, with screw-type flow adjustment, stainless steel retraction spring, and PRS module where noted on the drawings.

J.	Automatic Drain Valves:  Corrosion-resistant PVC plastic, with 1/2 inch male pipe threaded connections.  The valve shall open when pressure in the line decreases to 9 psi and seal again when pressure increases to 10 psi.  Provide a screen on both inlet and outlet.  Install automatic valves only on laterals of average pipe size 1-1/2 inch or less.  Install at low points and at 100-feet on center in the laterals.  Provide King Technology, Inc. automatic drain valve or approved substitute.

K.	Pressure Regulator:  As indicated on drawings or approved substitute.

L.	Backfill Material:  Use on-site material, except rock, large stones, brush, sod, frozen material or other unsuitable material as determined by the SDR.  If additional backfill material is required, supply earth, loam, sandy clay, sand, or other approved material free of large clods of earth or sharp stones, capable of sustaining the same relative density of the surrounding ground.

PART 3 - EXECUTION

3.01	SYSTEM DESIGN

A.	The drawings are diagrammatic and indicative of the work to be installed.

3.02	EXAMINATION

A.	General:  Carefully investigate the structural and finished conditions affecting the work, and plan work accordingly to furnish fittings and appurtenances which are required to meet field conditions.  Examine related work and surfaces before installing the work.  Report in writing to the SDR conditions which will prevent proper execution.

3.03	PREPARATION

A.	Trenching:

1.	Excavate to sufficient depth and width to permit proper handling and installation of the pipe and fittings.  Cut trenches for pipe to the required grade lines.  Compact the trench bottom to provide an accurate grade and uniform bearing for the full length of the line.  Excavate trenches in straight lines.  When two pipes are laid in the same trench, maintain a minimum of four inches between the pipe.  In areas where trees are present, adjust trench location beyond the dripline of the tree.

2.	Depth:  Excavate trenches of sufficient depth to provide specified soil cover for master lines and lateral lines.

3.	Staking:  Stake all trench, sprinkler head and valve locations.  Obtain SDR approval prior to trenching.

4.	Trim:  Accurately trim trenches to provide a uniform bed, free of rocks, clods or other sharp-edged objects.

5.	Dewatering:  Pump out or otherwise remove water encountered or accumulated in the excavation to keep the bottom of the trench or excavation free and clear of water during the progress of the work.

6.	Sleeved Crossings:  Sleeve pipe and wiring under sidewalks, roadways, parking lots, or through walls.  Provide sleeves a minimum of one inch in diameter greater than the pipe or wire bundle to be sleeved.

7.	Existing Lawns:  Where trenching is required across existing lawns, uniformly cut strips of sod 6 inches wider than trench.  Remove sod in rolls of suitable size for handling and keep moistened until replanted.

8.	Irrigation Line Slope:  The minimum pitch of irrigation lines to automatic drain valves shall be 3 inches in 100 feet.

3.04	INSTALLATION

A.	General:  Install material and equipment in accordance with manufacturer's recommendations, Uniform Plumbing Code, and ASTM 2774.  Install the work to avoid conflicts between underground irrigation installation, existing utilities, planting and other existing features.

B.	Maintain uninterrupted water service to building during normal working hours.  Arrange for temporary water shut-off with SDR.

C.	Pipe:

1.	Provide connections between plastic pipe and metal valves or steel pipe with screw fitting, using plastic male adapters with the specified pipe sealant applied to male threads. Connect screwed connections with light wrench pressure.  Do not screw steel pipe into plastic fittings except at head risers.

2.	Apply cleaner and solvent in accordance with ASTM D 2855 using the following procedure in sequence.

a.	Apply an even coat of cleaner to the outside of the pipe and to the inside of the fittings.  Remove dirt, dust, and moisture completely.

b.	Apply primer to outside of pipe and inside of fittings in accordance with manufacturer's instructions.

c.	Apply an even coat of solvent to the outside of the pipe and to the inside of the fittings.  Reapply a light coat of solvent to outside of pipe, ensuring the coated area of pipe is equal to the full depth of the fitting socket.

d.	Insert pipe quickly into fitting and turn approximately one-half turn to distribute solvent and remove air bubbles; check tees and ells for correct position.

e.	Wipe off excess solvent with clean rags.

f.	Allow solvent-welded joints to cure for 15 minutes before moving or handling.

g.	Pressure test piping after solvent-welded joints have cured for 24 hours.

3.	Do not lay pipe in water or in trench when weather conditions are unsuitable for work, except when expressly directed by the SDR.  Rest the full length of each pipe section solidly on the pipe bed with recesses excavated to accommodate bells and joints.

4.	Thoroughly clean the interior of pipe and remove rocks, gravel, soil, and other objects prior to assembly.  To insure a clean system, hold each joint of pipe in an upright position to allow foreign objects to fall out before the joint is attached to the system.  As each additional joint is installed, ensure foreign objects do not enter the free end of the joint.  At the end of a work period, cap open ends on installed pipe to keep out foreign matter.  Securely close open ends of pipe and fittings to prevent trench water, earth or other substances from entering the pipes or fittings.

5.	Replace defective sections of pipe discovered before or after laying with sound pipe.

6.	Provide 4 inches minimum horizontal clearance between lines in the same trench.  Install master lines (lines from master valve to automatic valves) with a minimum soil cover of 28 inches, exclusive of mulch or paving.  Install lateral irrigation lines (lines from automatic valves to sprinkler heads) with a minimum soil cover of 18 inches, exclusive of mulch or paving.

7.	Sterilize piping up to backflow preventer in accordance with Division 2 Section "Exterior Water Distribution ".

8.	Provide for expansion/contraction of piping in accordance with manufacturer's recommendations.

D.	Saddle Taps:  Do not use saddle taps.  Use fittings and reducers to attach branches to the system.  Do not use  bushings, street ells, or close nipples, except where indicated.

E.	Jacked or Bored Sleeves:  Use the following procedure to bore under paved surfaces.

1.	Bore hole under paved surfaces with a pneumatic boring device.

2.	Insert steel sleeves through hole with the pneumatic device, or by other methods approved by the SDR.

3.	Conditions of Bore.

a.	Locate bore a minimum of 2'-6" below grade of the paved surface, unless otherwise directed by the SDR where sleeves cross existing utilities.

b.	Bore hole a maximum 1 inch diameter larger than steel sleeves inserts.

c.	Fill voids greater than 1 inch around the sleeve and bad bores with grout.  Provide high strength grout, 5,000-6,000 PSI, 6 inch slump pumped at 1.3 cf/min., or approved by the SDR.

d.	Weld multiple lengths of sleeves together or, if couplings fit within bore hole, couple together.

e.	Do not use sleeves shorter than the length of the metallic part of the pneumatic boring device.

f.	Repair or replace any damage caused by borings including, but in not limited to, cracks, bulges, and settlement in adjacent pavings and surfaces.

g.	Verify boring locations.  Do not penetrate existing utilities.

F.	Controllers:  Install controllers in locations shown.  Make power connections.  Mount and wire the controllers in accordance with manufacturer's approved procedures.  Install freeze sensor in accordance with manufacturer's recommendations.

G.	Sprinkler Heads:  Install sprinkler heads at grade unless otherwise indicated.  Install sprinkler heads with a minimum of 4 inches and a maximum of 6 inches clearance from curbs, walks, driveways, etc. and a minimum of 12 inches and a maximum of 18 inches from buildings and walls.  Teflon tape shall be used on threaded connections at heads and joints.  Install heads in vertical position, hand backfilled and compacted to near original density.  Adjust all sprinkler heads to ensure proper watering of plant material.

H.	Valves and Valve Boxes:  Cover automatic and manual control valves with valve boxes.  Set top of boxes at grade.  Install automatic valves according to manufacturer's recommendations and as shown.  Set Pressure Regulating Module to 45 PSI or as directed by SDR. Coordinate valve boxes locations with planting plan.  Install valve boxes square with buildings or walks.  Wire each valve to a separate station on the controller.  Clearly tag each valve with a legible, permanent, waterproof tag indicating the controller zone number

I.	Control Wiring:  Install control wires in same trenches as irrigation main lines and laterals whenever practical.  Snake wires in the trench to allow for displacement of the wire during backfilling.  Securely tape wires running in the same trench together at 10-foot intervals.  Place wiring bundles to one side of piping (east of north/south lines and north of east/west  lines) at a maximum of 3 inches from piping.  If wiring is not in the same trench as piping or is under paving, install in Schedule 40 PVC piping and provide 18 inches minimum cover.

J.	Splices:  Minimize wire splices.  Where splices are required, use common splice boxes located in valve boxes.  Provide a slack-wire loop at each valve with enough slack so that wire splices can be extended 24 inches above ground level to facilitate testing and trouble shooting.

K.	Codes and Other Electrical Information:  Install 115 volt AC wiring in accordance with requirements of the National Electrical Code and electrical specifications.  Provide electrical service to controllers consisting of one black and one white wire in rigid conduit. Connect electrically-operated devices and metal enclosures to ground, in accordance with manufacturer's recommendations.

L.	Automatic Drain Valves:  Install automatic drain valves on lateral lines only, at low points, 100 foot o.c.; install one cubic foot washed gravel, with filter fabric completely surrounding gravel at each drain valve.  Install automatic drain valves 3 inches below top of gravel.  Install a 2-inch diameter Class 200 PVC pipe vertically above drain valve.  Do not connect to pipe.  Install with slip cap (not solvent welded), with 1/2-inch diameter hole.  Install top of pipe flush with gravel

M.	Backflow Preventer:  Install as detailed and in conformance with the Uniform Plumbing Code.

N.	Thrust Block:  On lines over 2 inches in diameter, install concrete thrust blocks at tees, bends, and pipe ends.

3.05	FIELD QUALITY CONTROL

A.	Inspection and Testing:

1.	Inspection:  The SDR may inspect the work at any time.  Maintain proper facilities and provide safe access for inspection.  When testing or approval is required, notify the SDR 24 hours in advance where and when testing will take place.  Do not cover up work before testing or approval is obtained.  If work is covered up before testing or approval is obtained, uncover, test, and restore surface at no expense to SNL.

2.	Rejection:  If any portion of the work done or any materials delivered fail to comply with requirements, immediately correct the deficiency at no additional expense.  Remove rejected materials from the site.

3.	Pressure Testing:  Pressure test PVC main lines piping after laying and completing joints and setting valves but prior to backfilling.  Pressure test using the following procedure.

a.	Load each pipe length with a small amount of backfill to prevent arching or slipping under pressure.  Do not cover up fittings.

b.	Flush out all lines, then cap all outlets and hydro- statically test the complete system.  Test line between master valves and remote control valves (where applicable) at a pressure of 100 psi.  Test laterals (intermittently pressurized) in the same manner at existing available static pressure.

c.	Expose joints for inspection during the pressure test.  Swing joints may be installed prior to pressure test.  Maintain pressure tests on plastic pipe for not less than 4 hours for master lines and 2 hours for lateral lines.  If pressure loss occurs, beyond extent acceptable to SDR, repair affected line and repeat tests until the entire system has been proven tight.  Conceal lines passing hydrostatic pressure test the same day if temperatures 32 degrees and below are anticipated.  Install pressure gauges on the line being tested.

3.06	BACKFILLING

A.	After pipe joints have been visually inspected and pressure testing has been accomplished and approved, begin backfilling.  Backfill when the pipe is not in an expanded condition due to heat or pressure.  Cool pipe by operating the system for a short time before backfill, or by backfilling early in the morning before the heat of the day.

B.	Place backfill in horizontal layers not exceeding 8 inches in loose depth.  Thoroughly tamp and use water compaction by flooding trenches after each lift and allowing for settlement.  Do not water flood any trenches adjacent to walls, sidewalks, curbs, or buildings.  Backfill and compact trenches adjacent to walls, sidewalks, or buildings with a mechanical compactor after each lift.  Compact to original density or 90 percent in unpaved areas and 95 percent in paved areas. Compact to maximum density at optimum moisture in accordance with ASTM D 1557 or AASHTO T180, whichever is greater, to minimize settlement.

C.	Place backfill to the original ground level or to the grades indicated and fill with topsoil to finish grade.

3.07	COVERAGE AND ADJUSTMENT

A.	When the underground irrigation system installation is complete, perform a coverage test to determine if the water coverage for planting areas is complete and adequate and that spray does not hit buildings, walks and other locations where not required.  Correct coverage inadequacies.

B.	Adjust all heads and valves.  Program controller to provide optimum underground irrigation system performance.

END OF SECTION