## 25F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 049R1
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6556.5273
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 454.53 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 679.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 573.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1630.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 679.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3362.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1401.48 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3230.08 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1518.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 3098.19 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1630.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 573.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3143.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1518.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3279.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3279.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3362.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3017.12 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1000 | 140 | 2344.94 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3083.81 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3017.12 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 454.53 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3230.08 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1401.48 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 3075.93 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3143.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 3083.81 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2344.94 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
1400 | 775 | 3098.19 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 3075.93 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 049R1
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6424.8353
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 619.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 838.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 731.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1774.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 838.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3458.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1549.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3164.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1665.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 3026.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1774.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 731.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3250.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1665.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3309.09 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3309.09 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV]
525 | 775 | 3458.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3148.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3140.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3013.03 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3148.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 619.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3164.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1549.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 3004.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3250.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 3013.03 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3140.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3026.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 3004.86 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 049R1
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 5982.414
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 524.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 743.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 638.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1645.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 743.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3337.65 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1416.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2864.27 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 1534.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2453.94 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1645.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 638.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3097.18 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1534.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3231.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3231.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3337.65 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3075.31 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3066.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2797.53 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 3075.31 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 524.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2864.27 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1416.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2933.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3097.18 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2797.53 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3066.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2453.94 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2933.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 049R1
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4919.9693
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1823.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1988.37 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1941 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1825.6 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1988.37 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1555.57 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2517.79 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1074.1 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 2158.9 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 664.68 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1825.6 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 1941 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2252.1 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2158.9 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 1893.25 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1893.25 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1555.57 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1400.23 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1782.6 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 990.89 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 1400.23 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1823.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1074.1 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2517.79 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1343.89 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2252.1 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 990.89 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1782.6 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 664.68 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1343.89 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 049R1
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4584.3513
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1777.98 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1094.25 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1435.26 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 935.92 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1094.25 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 655.88 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1615.88 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 175.5 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 1251.34 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -232.53 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 935.92 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1435.26 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 1334.16 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1251.34 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 992.67 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 992.67 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 655.88 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 508.77 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 859.78 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 97.75 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 508.77 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1777.98 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 175.5 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1615.88 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 452.07 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1334.16 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 97.75 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 859.78 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | -232.53 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 452.07 | MOD BFR: Covington 230kV West Bus | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
G0 | 454.53 | 619.2 | 524.73 | 1823.28 | 1777.98
G1 | 573.29 | 731.36 | 638.82 | 1941 | 1435.26 | Season/Year: | WINTER 2009
G2 | 679.35 | 838.82 | 743.84 | 1988.37 | 1094.25 | Direction: | North-to-South (NS)
G3 | 1401.48 | 1549.47 | 1416.6 | 2517.79 | 1615.88 | Case Loads: | Heavy Loads
G4 | 1518.6 | 1665.77 | 1534.23 | 2158.9 | 1251.34 | Outage: | 049R1
G5 | 1630.6 | 1774.21 | 1645.09 | 1825.6 | 935.92 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3143.78 | 3250.83 | 3097.18 | 2252.1 | 1334.16 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3279.76 | 3309.09 | 3231.94 | 1893.25 | 992.67 | Study Person: | JGO7470
G8 | 3362.29 | 3458.76 | 3337.65 | 1555.57 | 655.88 | Source: | 049R1WINTER09v5NSH
G9 | 2344.94 | 3140.29 | 3066.02 | 1782.6 | 859.78
G10 | 3017.12 | 3148.5 | 3075.31 | 1400.23 | 508.77
G11 | 3230.08 | 3164.47 | 2864.27 | 1074.1 | 175.5
G12 | 3075.93 | 3004.86 | 2933.26 | 1343.89 | 452.07
G13 | 3083.81 | 3013.03 | 2797.53 | 990.89 | 97.75
G14 | 3098.19 | 3026.56 | 2453.94 | 664.68 | -232.53
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 049R1 | Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6556.5273 | 454.53 | 573.29 | 679.35 | 1401.48 | 1518.6 | 1630.6 | 3143.78 | 3279.76 | 3362.29 | 2344.94 | 3017.12 | 3230.08 | 3075.93 | 3083.81 | 3098.19
35F | 6424.8353 | 619.2 | 731.36 | 838.82 | 1549.47 | 1665.77 | 1774.21 | 3250.83 | 3309.09 | 3458.76 | 3140.29 | 3148.5 | 3164.47 | 3004.86 | 3013.03 | 3026.56
45F | 5982.414 | 524.73 | 638.82 | 743.84 | 1416.6 | 1534.23 | 1645.09 | 3097.18 | 3231.94 | 3337.65 | 3066.02 | 3075.31 | 2864.27 | 2933.26 | 2797.53 | 2453.94
60F | 4919.9693 | 1823.28 | 1941 | 1988.37 | 2517.79 | 2158.9 | 1825.6 | 2252.1 | 1893.25 | 1555.57 | 1782.6 | 1400.23 | 1074.1 | 1343.89 | 990.89 | 664.68
70F | 4584.3513 | 1777.98 | 1435.26 | 1094.25 | 1615.88 | 1251.34 | 935.92 | 1334.16 | 992.67 | 655.88 | 859.78 | 508.77 | 175.5 | 452.07 | 97.75 | -232.53

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 453.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 475.83 | 475.89 | 6560.3 | 454.53 | -2.43 | FULL
G1 | 572.37 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 476.42 | 476.44 | 6489.49 | 573.29 | 96.69 | FULL
G2 | 679.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 476.75 | 476.7 | 6500.87 | 679.35 | 187.95 | FULL
G3 | 1403.4 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 485.46 | 485.47 | 6557.05 | 1401.48 | 598.87 | FULL
G4 | 1519.87 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 486.07 | 486.07 | 6489.44 | 1518.6 | 696.68 | FULL
G5 | 1632.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 486.66 | 486.57 | 6503.56 | 1630.6 | 789.81 | FULL
G6 | 3159.4 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 490.52 | 490.5 | 6600.9 | 3143.78 | 1671.09 | FULL
G7 | 3296.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 490.23 | 490.2 | 6538.71 | 3279.76 | 1781.05 | FULL
G8 | 3380.36 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 490.16 | 490.11 | 6557.37 | 3362.29 | 1871.95 | FULL
G9 | 2356.55 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 31.52 | 1108.62 | 1405.29 | 6609.44 | 2344.94 | 1439.09 | CTG_FAIL_IN_FULL
G10 | 3033.13 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 31.52 | 1277.72 | 1325.46 | 6557.42 | 3017.12 | 1831.16 | FULL
G11 | 3246.19 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -510.83 | -510.39 | 6578.15 | 3230.08 | 1984.99 | FULL
G12 | 3090.3 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -512.33 | -511.78 | 6639.65 | 3075.93 | 1981.54 | FULL
G13 | 3098.99 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -512.06 | -511.54 | 6574.54 | 3083.81 | 2014.77 | FULL
G14 | 3113.49 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -512.65 | -512.1 | 6591.02 | 3098.19 | 2052.48 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 616.61 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 469.76 | 469.56 | 6423.56 | 619.2 | 124.56 | FULL
G1 | 730.97 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 470.1 | 469.95 | 6353.54 | 731.36 | 219.55 | FULL
G2 | 838.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 470.37 | 470.16 | 6365.75 | 838.82 | 311.13 | FULL
G3 | 1554.09 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 478.08 | 478.13 | 6423.63 | 1549.47 | 710.3 | FULL
G4 | 1669.52 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 478.43 | 478.62 | 6356.68 | 1665.77 | 806.51 | FULL
G5 | 1779.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 478.98 | 479.13 | 6371.93 | 1774.21 | 897.41 | FULL
G6 | 3266.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 481.13 | 481.08 | 6471.76 | 3250.83 | 1779.86 | FULL
G7 | 3326.26 | Branch MONROE (40749) TO MONROE (40747) CKT 1 [500.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 31.52 | 1322.43 | 1172.44 | 6408.73 | 3309.09 | 1840.22 | CTG_FAIL_IN_FULL
G8 | 3477.79 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 480.42 | 480.19 | 6429.96 | 3458.76 | 1949.97 | FULL
G9 | 3156.49 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -499.45 | -498.83 | 6492.48 | 3140.29 | 1914.7 | FULL
G10 | 3164.49 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -498.86 | -498.2 | 6427.24 | 3148.5 | 1947.34 | FULL
G11 | 3180.49 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -500.48 | -499.85 | 6444.07 | 3164.47 | 1968.22 | FULL
G12 | 3019.68 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -501.8 | -501.31 | 6504.96 | 3004.86 | 1988.43 | FULL
G13 | 3027.45 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -501.83 | -501.56 | 6440.6 | 3013.03 | 1991.54 | FULL
G14 | 3041.35 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -502.18 | -501.89 | 6457.64 | 3026.56 | 2047.02 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 525.49 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 437.28 | 437.17 | 5983.16 | 524.73 | 96.61 | FULL
G1 | 637.79 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 437.59 | 437.49 | 5913.45 | 638.82 | 192.69 | FULL
G2 | 743.17 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 437.71 | 437.61 | 5925.97 | 743.84 | 282.97 | FULL
G3 | 1419.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 443.08 | 443.31 | 5983.19 | 1416.6 | 660.7 | FULL
G4 | 1537.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 443.6 | 443.76 | 5916.31 | 1534.23 | 757.93 | FULL
G5 | 1647.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 444.24 | 444.35 | 5932.02 | 1645.09 | 849.88 | FULL
G6 | 3113.07 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 445.19 | 445.44 | 6029.7 | 3097.18 | 1693.75 | FULL
G7 | 3248.4 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 446.4 | 446.34 | 5967.8 | 3231.94 | 1827.61 | FULL
G8 | 3354.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 445.88 | 445.81 | 5988.47 | 3337.65 | 1906.25 | FULL
G9 | 3081.21 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -492.65 | -492.24 | 6052.48 | 3066.02 | 1874.59 | FULL
G10 | 3090.43 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -492.36 | -491.97 | 5987.5 | 3075.31 | 1908.84 | FULL
G11 | 2877.22 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 674.36 | 674.34 | 5996.41 | 2864.27 | 1823.66 | FULL
G12 | 2946.41 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -493.65 | -493 | 6064.8 | 2933.26 | 1981.3 | FULL
G13 | 2810.49 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 674.24 | 674.22 | 5997.49 | 2797.53 | 1904.09 | FULL
G14 | 2463.56 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 674.74 | 674.72 | 5997.46 | 2453.94 | 1761.2 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1828.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 444.35 | 444.5 | 4945.17 | 1823.28 | 941.23 | FULL
G1 | 1945.72 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 444.73 | 444.86 | 4881.01 | 1941 | 1037.42 | FULL
G2 | 1995.21 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642.31 | 642.31 | 4897.59 | 1988.37 | 1093.78 | FULL
G3 | 2527.38 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642.11 | 642.1 | 4964.24 | 2517.79 | 1387.53 | FULL
G4 | 2166.4 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642.28 | 642.28 | 4890.48 | 2158.9 | 1220.64 | FULL
G5 | 1830.43 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642.28 | 642.27 | 4898.69 | 1825.6 | 1064.53 | FULL
G6 | 2259.64 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642.22 | 642.21 | 4966.69 | 2252.1 | 1353.67 | FULL
G7 | 1898.88 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642.35 | 642.34 | 4891.3 | 1893.25 | 1188.31 | FULL
G8 | 1558.97 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642.51 | 642.5 | 4899.13 | 1555.57 | 1033.08 | FULL
G9 | 1788.26 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642 | 642 | 4973.18 | 1782.6 | 1283.71 | FULL
G10 | 1402.9 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642.27 | 642.26 | 4896.84 | 1400.23 | 1116.52 | FULL
G11 | 1075.9 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642.59 | 642.59 | 4905.29 | 1074.1 | 966.84 | FULL
G12 | 1348.07 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642.17 | 642.16 | 4976.75 | 1343.89 | 1203.08 | FULL
G13 | 992.63 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642.35 | 642.34 | 4902.15 | 990.89 | 1039.81 | FULL
G14 | 663.58 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 642.68 | 642.63 | 4911.03 | 664.68 | 890.54 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1784.21 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 619.85 | 619.84 | 4624.72 | 1777.98 | 939.57 | FULL
G1 | 1437.93 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 620.13 | 620.02 | 4552.9 | 1435.26 | 781.59 | FULL
G2 | 1094.88 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 620.09 | 620.09 | 4564.18 | 1094.25 | 622.46 | FULL
G3 | 1619.6 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 619.94 | 619.93 | 4623.8 | 1615.88 | 911.14 | FULL
G4 | 1254.64 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 619.91 | 619.91 | 4551.63 | 1251.34 | 741.94 | FULL
G5 | 935.49 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 620.15 | 620.15 | 4563.39 | 935.92 | 606.41 | FULL
G6 | 1335.55 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 619.84 | 619.88 | 4623.99 | 1334.16 | 871.59 | FULL
G7 | 992.88 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 620.06 | 619.95 | 4552.53 | 992.67 | 724.46 | FULL
G8 | 654.77 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 620.14 | 620.05 | 4564.15 | 655.88 | 567.09 | FULL
G9 | 859.67 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 619.85 | 619.85 | 4630.77 | 859.78 | 820.6 | FULL
G10 | 508.99 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 620.11 | 620 | 4559.39 | 508.77 | 656.74 | FULL
G11 | 173.71 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 620.24 | 620.13 | 4571.15 | 175.5 | 500.89 | FULL
G12 | 451.88 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 620.03 | 619.92 | 4637.07 | 452.07 | 744.74 | FULL
G13 | 96.66 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 620.06 | 620.06 | 4566.18 | 97.75 | 578.08 | FULL
G14 | -233.59 | Branch CHRISTOP (42505) TO TACOMA (41049) CKT 2 [230.00 - 230.00 kV] | MOD BFR: Covington 230kV West Bus | 4.23 | 620.23 | 620.19 | 4579.42 | -232.53 | 426.09 | FULL
049R1WINTER09v5NSH