## 25F nomo
ALL LINES IN SERVICE
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 060
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3340.778
Gen Level |  | Trans | Worst | Limiting |  |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [6 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3428.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G3 | 100 | 775 | 3442.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3436.11 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G6 | 260 | 775 | 3293.7 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3442.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G9 | 525 | 775 | 3020.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3270.61 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G12 | 1000 | 775 | 2590.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3280.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G15 | 1400 | 775 | 2451.44 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3293.7 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G2 | 100 | 465 | 3436.11 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2987.45 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G5 | 260 | 460 | 3280.56 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3003.93 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G8 | 525 | 460 | 3003.93 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3020.64 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G11 | 1000 | 460 | 2590.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2565.8 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G14 | 1400 | 460 | 2434.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2590.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G1 | 100 | 140 | 3428.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2590.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G4 | 260 | 140 | 3270.61 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2424.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G7 | 525 | 140 | 2987.45 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2434.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G10 | 1000 | 140 | 2565.8 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2451.44 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  |  | G13 | 1400 | 140 | 2424.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450
G1
789

## 35F nomo
ALL LINES IN SERVICE
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 060
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2664.0473
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3306.19 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3324.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3310.19 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3145.72 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3324.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2871.76 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3137.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2460.04 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3140 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2318.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3145.72 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3310.19 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2851.85 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3140 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2863.12 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2863.12 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2871.76 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2455.91 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2446.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2297.65 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2455.91 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3306.19 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2460.04 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 3137.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2293.1 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2851.85 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2297.65 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2446.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2318.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2293.1 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
ALL LINES IN SERVICE
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 060
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2423.764
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3196.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3211.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3198.22 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3053.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3211.02 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2772.27 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3030.14 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2350.17 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3040.53 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2204.57 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3053.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3198.22 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2753.34 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3040.53 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2762.08 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2762.08 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2772.27 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2345.98 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2325.87 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2189.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2345.98 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3196.42 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2350.17 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 3030.14 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2184.27 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2753.34 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2189.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2325.87 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2204.57 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2184.27 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
ALL LINES IN SERVICE
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 060
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2943.2987
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3153.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3159.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3161.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3012.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3159.01 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2733.36 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3003.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2311 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3012.44 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2173 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3012.77 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 3161.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2721.99 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 3012.44 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2726.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2726.63 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2733.36 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2302.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2298 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2160.45 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2302.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3153.28 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2311 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 3003.49 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2139.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2721.99 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2160.45 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2298 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2173 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2139.29 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
ALL LINES IN SERVICE
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 060
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3294.6173
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3094.59 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3124.24 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3099.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2954.39 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3124.24 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2675.7 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2933.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2259.59 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2943.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2105.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2954.39 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3099.43 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2659.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2943.06 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2667.7 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2667.7 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2675.7 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2248.27 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2227.95 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2095.61 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2248.27 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 3094.59 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2259.59 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2933.26 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2081.89 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2659.25 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2095.61 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2227.95 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2105.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2081.89 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | ALL LINES IN SERVICE
G0 | 3428.21 | 3306.19 | 3196.42 | 3153.28 | 3094.59
G1 | 3436.11 | 3310.19 | 3198.22 | 3161.2 | 3099.43 | Season/Year: | WINTER 2009
G2 | 3442.42 | 3324.25 | 3211.02 | 3159.01 | 3124.24 | Direction: | North-to-South (NS)
G3 | 3270.61 | 3137.77 | 3030.14 | 3003.49 | 2933.26 | Case Loads: | Light Loads
G4 | 3280.56 | 3140 | 3040.53 | 3012.44 | 2943.06 | Outage: | 060
G5 | 3293.7 | 3145.72 | 3053.5 | 3012.77 | 2954.39 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2987.45 | 2851.85 | 2753.34 | 2721.99 | 2659.25 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3003.93 | 2863.12 | 2762.08 | 2726.63 | 2667.7 | Study Person: | FRP9899
G8 | 3020.64 | 2871.76 | 2772.27 | 2733.36 | 2675.7 | Source: | 060WINTER09v2NSL
G9 | 2565.8 | 2446.96 | 2325.87 | 2298 | 2227.95
G10 | 2590.29 | 2455.91 | 2345.98 | 2302.28 | 2248.27
G11 | 2590.5 | 2460.04 | 2350.17 | 2311 | 2259.59
G12 | 2424.49 | 2293.1 | 2184.27 | 2139.29 | 2081.89
G13 | 2434.29 | 2297.65 | 2189.63 | 2160.45 | 2095.61
G14 | 2451.44 | 2318.96 | 2204.57 | 2173 | 2105.21
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Light Loads |  |  | 060 | ALL LINES IN SERVICE
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3340.778 | 3428.21 | 3436.11 | 3442.42 | 3270.61 | 3280.56 | 3293.7 | 2987.45 | 3003.93 | 3020.64 | 2565.8 | 2590.29 | 2590.5 | 2424.49 | 2434.29 | 2451.44
35F | 2664.0473 | 3306.19 | 3310.19 | 3324.25 | 3137.77 | 3140 | 3145.72 | 2851.85 | 2863.12 | 2871.76 | 2446.96 | 2455.91 | 2460.04 | 2293.1 | 2297.65 | 2318.96
45F | 2423.764 | 3196.42 | 3198.22 | 3211.02 | 3030.14 | 3040.53 | 3053.5 | 2753.34 | 2762.08 | 2772.27 | 2325.87 | 2345.98 | 2350.17 | 2184.27 | 2189.63 | 2204.57
60F | 2943.2987 | 3153.28 | 3161.2 | 3159.01 | 3003.49 | 3012.44 | 3012.77 | 2721.99 | 2726.63 | 2733.36 | 2298 | 2302.28 | 2311 | 2139.29 | 2160.45 | 2173
70F | 3294.6173 | 3094.59 | 3099.43 | 3124.24 | 2933.26 | 2943.06 | 2954.39 | 2659.25 | 2667.7 | 2675.7 | 2227.95 | 2248.27 | 2259.59 | 2081.89 | 2095.61 | 2105.21

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3446.61 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -491.73 | -491.97 | 3369.98 | 3428.21 | 1699.99 | FULL
G1 | 3455.14 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -490.62 | -490.84 | 3306.62 | 3436.11 | 1739.02 | FULL
G2 | 3461.55 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -491.65 | -491.56 | 3325.5 | 3442.42 | 1766.04 | FULL
G3 | 3287.65 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -501.54 | -501.62 | 3367.97 | 3270.61 | 1675.91 | FULL
G4 | 3297.78 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -501.36 | -501.36 | 3304.75 | 3280.56 | 1711.14 | FULL
G5 | 3310.84 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -501.98 | -502.55 | 3323.52 | 3293.7 | 1746.74 | FULL
G6 | 3001.46 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -507.99 | -507.73 | 3368.75 | 2987.45 | 1640.85 | FULL
G7 | 3017.6 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -510.51 | -509.47 | 3305.39 | 3003.93 | 1672.31 | FULL
G8 | 3035.27 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -508.69 | -507.72 | 3325.62 | 3020.64 | 1710.25 | FULL
G9 | 2576.44 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -516.96 | -516.31 | 3378.68 | 2565.8 | 1605.52 | FULL
G10 | 2600.55 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -519.09 | -518.27 | 3315.7 | 2590.29 | 1644.75 | FULL
G11 | 2601.01 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -517.31 | -516.98 | 3335.27 | 2590.5 | 1672.06 | FULL
G12 | 2433.42 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -517.26 | -517.46 | 3396.77 | 2424.49 | 1665.8 | FULL
G13 | 2442.05 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -516.1 | -517.02 | 3333.73 | 2434.29 | 1704.88 | FULL
G14 | 2459.75 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -516.91 | -517.12 | 3353.42 | 2451.44 | 1743.79 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3323.57 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -486.44 | -486.43 | 2691.7 | 3306.19 | 1688.47 | FULL
G1 | 3327.66 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -484.89 | -485.7 | 2628.62 | 3310.19 | 1718.89 | FULL
G2 | 3341.72 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -485.74 | -486.87 | 2648.26 | 3324.25 | 1749.41 | FULL
G3 | 3153.26 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -499.07 | -499.35 | 2689.8 | 3137.77 | 1655.8 | FULL
G4 | 3155.31 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -499.25 | -499.62 | 2626.98 | 3140 | 1684.02 | FULL
G5 | 3161.14 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -494.77 | -494.5 | 2646.58 | 3145.72 | 1719.12 | FULL
G6 | 2864.48 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -498.76 | -502.06 | 2691.05 | 2851.85 | 1614.23 | FULL
G7 | 2874.84 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -500.59 | -499.42 | 2629.02 | 2863.12 | 1648.42 | FULL
G8 | 2884.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -499.62 | -499.44 | 2648.72 | 2871.76 | 1680.56 | FULL
G9 | 2455.29 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -507.27 | -506.49 | 2701.88 | 2446.96 | 1590.6 | FULL
G10 | 2464.44 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -507.17 | -506.41 | 2639.59 | 2455.91 | 1623.7 | FULL
G11 | 2468.74 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -504.21 | -503.47 | 2660.07 | 2460.04 | 1644.84 | FULL
G12 | 2300.59 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -507.68 | -507.21 | 2720.09 | 2293.1 | 1651.48 | FULL
G13 | 2305.62 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -506.16 | -505.49 | 2659.09 | 2297.65 | 1671.42 | FULL
G14 | 2327.17 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -506.26 | -505.83 | 2679.26 | 2318.96 | 1713.73 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3212.47 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -483.67 | -483.08 | 2449.22 | 3196.42 | 1661.03 | FULL
G1 | 3214.3 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -481.68 | -481.14 | 2387.85 | 3198.22 | 1686.07 | FULL
G2 | 3227.24 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -480.31 | -479.78 | 2406.99 | 3211.02 | 1723.81 | FULL
G3 | 3044.46 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -491.03 | -490.63 | 2448.26 | 3030.14 | 1630.52 | FULL
G4 | 3055.38 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -490.2 | -489.74 | 2386.68 | 3040.53 | 1661.74 | FULL
G5 | 3068.25 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -490.58 | -490.17 | 2406.54 | 3053.5 | 1695.81 | FULL
G6 | 2764.67 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -494.23 | -493.8 | 2450.64 | 2753.34 | 1590.52 | FULL
G7 | 2773.58 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -490.99 | -490.57 | 2387.69 | 2762.08 | 1625.7 | FULL
G8 | 2783.88 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -490.26 | -489.8 | 2408.14 | 2772.27 | 1658.04 | FULL
G9 | 2333.96 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -494.92 | -494.47 | 2462.57 | 2325.87 | 1547.79 | FULL
G10 | 2353.15 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -495.29 | -494.5 | 2400.15 | 2345.98 | 1594.18 | FULL
G11 | 2358.77 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -492.08 | -491.53 | 2420.11 | 2350.17 | 1624.76 | FULL
G12 | 2191.55 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -494.13 | -493.29 | 2481.54 | 2184.27 | 1622.74 | FULL
G13 | 2196.07 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -492.1 | -491.29 | 2419.46 | 2189.63 | 1654.57 | FULL
G14 | 2211.4 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -493.66 | -492.89 | 2440.62 | 2204.57 | 1680.61 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3168.81 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -462.75 | -462.38 | 2970.55 | 3153.28 | 1601.12 | FULL
G1 | 3176.84 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -462.28 | -461.97 | 2907.33 | 3161.2 | 1633.7 | FULL
G2 | 3174.71 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.93 | -461.14 | -460.82 | 2926.78 | 3159.01 | 1644.56 | FULL
G3 | 3017.57 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -471.43 | -470.52 | 2969.19 | 3003.49 | 1580.68 | FULL
G4 | 3026.43 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -471.06 | -469.99 | 2906.16 | 3012.44 | 1614.01 | FULL
G5 | 3027.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -470.34 | -469.95 | 2926.36 | 3012.77 | 1638.71 | FULL
G6 | 2733.12 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -472.07 | -471.32 | 2971.41 | 2721.99 | 1540.26 | FULL
G7 | 2737.2 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -470.28 | -469.85 | 2908.5 | 2726.63 | 1570.76 | FULL
G8 | 2743.92 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -469.92 | -469.58 | 2927.47 | 2733.36 | 1601.82 | FULL
G9 | 2305.35 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -474.39 | -473.82 | 2982.53 | 2298 | 1504.86 | FULL
G10 | 2309.13 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -474.4 | -473.83 | 2919.11 | 2302.28 | 1535.4 | FULL
G11 | 2318.29 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -473.11 | -472.58 | 2938.28 | 2311 | 1558.78 | FULL
G12 | 2144.81 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -473.68 | -472.93 | 3001.14 | 2139.29 | 1545.9 | FULL
G13 | 2167.16 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -474.34 | -473.58 | 2937.43 | 2160.45 | 1594.72 | FULL
G14 | 2179.69 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -473.47 | -472.69 | 2957.24 | 2173 | 1635.42 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3108.96 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -450.86 | -450.38 | 3322.56 | 3094.59 | 1556.7 | FULL
G1 | 3114.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -450.11 | -449.71 | 3259.45 | 3099.43 | 1576.94 | FULL
G2 | 3139.78 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -450.03 | -449.36 | 3277.45 | 3124.24 | 1632.02 | FULL
G3 | 2946.42 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -456.63 | -455.5 | 3320.86 | 2933.26 | 1536.28 | FULL
G4 | 2956.33 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -455.7 | -454.84 | 3257.53 | 2943.06 | 1565.53 | FULL
G5 | 2967.5 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -457.07 | -456.08 | 3276.04 | 2954.39 | 1600.56 | FULL
G6 | 2669.85 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -457.32 | -456.36 | 3323.61 | 2659.25 | 1490.56 | FULL
G7 | 2678.5 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -457.19 | -456.23 | 3260.17 | 2667.7 | 1523.6 | FULL
G8 | 2685.99 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -456.97 | -456.06 | 3278.42 | 2675.7 | 1556.4 | FULL
G9 | 2234.43 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -457.38 | -456.54 | 3334.65 | 2227.95 | 1447.07 | FULL
G10 | 2255.83 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -460.57 | -459.73 | 3270.62 | 2248.27 | 1497.84 | FULL
G11 | 2266.24 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -458.39 | -457.83 | 3289.46 | 2259.59 | 1537.98 | FULL
G12 | 2087.56 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -459.21 | -458.24 | 3351.34 | 2081.89 | 1523.01 | FULL
G13 | 2102.14 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -458.85 | -457.88 | 3288.85 | 2095.61 | 1555.28 | FULL
G14 | 2111.54 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.67 | -457.76 | -456.8 | 3308.25 | 2105.21 | 1584.34 | FULL
060WINTER09v2NSL