## Design Worksheet
U.S. DEPARTMENT OF AGRICULTURE
NATURAL RESOURCES CONSERVATION SERVICE
DRY HYDRANT DESIGN WORKSHEET
[13 empty] | Date | 2008-12-17
Date
1. Check with the local fire department for the desired design capacity | [14 empty] | gpm
2. Determine required usable volume of water. | [14 empty] | ft3
3. Determine available useable volume of water. | [14 empty] | ft3
*** Available volume must be greater than required volume. ***
4. Determine the SHL (static head loss) between the centerline of the strainer and the centerline of the intake pump
on the pumper. Consult with the local fire department on the pumper intake height.
feet
5. Choose a pipe size and determine the ISL (intake strainer loss) from Table A.
Intake strainer open area shall be at least 4 times the pipe area. | [14 empty] | Inches
feet
Table A - Intake Strainer Head Loss - feet
| Dia/Flow |  |  | 500 gpm |  | 750 gpm | 1000 gpm |  |  | 1250 gpm |  | 1500 gpm |  | 2000 gpm
| 6" |  |  | 0.4 |  | 0.8 | 1.4 |  |  | 2.2 |  | 3.2 |  | 5.6
| 8" |  |  | 0.1 |  | 0.3 | 0.4 |  |  | 0.7 |  | 1 |  | 1.8
| 10" |  |  | 0.1 |  | 0.1 | 0.2 |  |  | 0.3 |  | 0.4 |  | 0.7
| 12" |  |  | -- |  | 0.1 | 0.1 |  |  | 0.2 |  | 0.3 |  | 0.3
6. Determine the PHL (pipe head loss) for the horizontal pipe and standpipe by calculating the equivalent length of
pipe and multiplying it by the friction head loss (f) in feet per foot from Table B.
| PHL 1 Horizontal Pipe Date | [6 empty] | PHL2 Standpipe Data (6" diam. Recommended)
[5 empty] | Inches |  |  |  | Six-inch standpipe length | [5 empty] | feet +
[5 empty] | feet |  |  |  | 90o elbows |  |  | at 20 feet each |  |  | feet +
[9 empty] | 30o/45o elbows |  |  | at 10 feet each |  |  | feet +
[9 empty] | Reducers |  |  | at 10 feet each |  |  | feet +
[9 empty] | In line strainers |  |  | at 10 feet each |  |  | feet =
[8 empty] | Total Standpipe Equivalent Length | [6 empty] | feet
| PHL1 = (f) x (pipe length) | [6 empty] | PHL2 = (f) x (total standpipe equivalent length)
| PHL1 = | ( | )x( |  | ) = | feet |  | PHL2 = | ( |  | )x( | ) = | feet
feet
Table B - Friction Head Loss - (f) - feet/foot
| Dia/Flow |  |  | 500 gpm |  | 750 gpm | 1000 gpm |  |  | 1250 gpm |  | 1500 gpm |  | 2000 gpm
| 6" |  |  | 0.016 |  | 0.033 | 0.057 |  |  | 0.086 |  | 0.12 |  | 0.204
| 8" |  |  | 0.004 |  | 0.008 | 0.014 |  |  | 0.021 |  | 0.03 |  | 0.05
| 10" |  |  | 0.001 |  | 0.003 | 0.005 |  |  | 0.007 |  | 0.01 |  | 0.017
| 12" |  |  | 0.001 |  | 0.001 | 0.002 |  |  | 0.003 |  | 0.004 |  | 0.007
7. Determine the THL (Total Head Loss) = SHL + ISL + PHL =
[9 empty] | ( |  | )+( | )+( | ) = |  | feet
The THL is recommended not to exceed 15 feet (20 feet maximum).
Increase horizontal pipe diameter and redesign if necessary.
Design for
hrs. (min. 2 hrs) =
ft (min. 2' ) =
gpm x
8 x
ft2 x depth
PHL = PHL1 + PHL2 =
SHL =
ISL =
area
Pipe diameter
Pipe length
THL =
IN-ENG-50D 10/02
Owner
Designed by
Checked by
Location
Pipe Size =

## Dry Hydrant Detail
ELEV.
ELEV.
ELEV.
ELEV.
FT. USABLE WATER FOR
ELEV.
12
LANDUSER
COUNTY SWCD, INDIANA
LOCATION
[8 empty] | Sec. | T |  |  | R
DRAWING NO. IN-ENG-50-1.XLS (REV. 10/02)
DETAILS OF DRY FIRE HYDRANT INDIANA
U.S. DEPARTMENT OF AGRICULTURE
NATURAL RESOURCES CONSERVATION SERVICE
[7 empty] | Designed |  | Date |  | Approved by |  |  | Date
2002-10-09
[7 empty] | Drawn |  | 2002-10-09 |  | Title
[7 empty] | Traced |  |  |  | Title
[7 empty] | Checked |  |  |  | Sheet | Drawing No.
No.
of
IN-ENG-50 (1 OF 2)
L
C
L
C
SUCTION INLET OF PUMP
SECTION THROUGH INSTALLATION
2' MIN. FOR SEDIMENT ACCUMULATION
INTAKE STRAINER (SEE ALTERNATE DETAILS)
NORMAL WATER LEVEL
GROUND LINE AT PIPE
FIRE SUPPRESSION (2' MIN.)
CU. FT.
NOTE: 1 - CHECK WITH LOCAL FIRE DEPARTMET FOR APPROVED TYPE OF CONNECTIONS AND STRAINERS. 2 - USE 20' LENGTH SECTION OF PIPE INTO WATER. JOINTS SHALL BE SOLVENT-CEMENT WELDED. 3 - INTAKE STRAINER CAN BE WELL SCREEN WITH MINIMUM OPENINGS OF 4 TIMES AREA OF PIPE OR DRILL HOLES AS SHOWN IN CHART IN BOTTOM 2/3 OF PIPE. DO NOT DRILL HOLES IN TOP 1/3 OF PIPE. COMMERCIALLY MANUFACTURED STRAINERS FOR FIRE PROTECTION SYSTEMS MAY ALSO BE USED.
NOT TO SCALE
END VIEW
ALTERNATE INTAKE STRAINER DETAIL
12" COVERING OF #2 IDOH COARSE AGGREGATE (NOT REQUIRED IF AT LEAST 2 FEET OF WATER BELOW INTAKE STRAINER)
END CAP
INTAKE STRAINER
6" MIN. DIA. INTAKE PIPE
STANDPIPE DETAIL
PVC ELBOW (ACTUAL NO. OF 30O, 45O , AND/OR 90O ELBOWS DEPENDS ON SITE CONDITIONS)
6" MIN. DIAM. INTAKE PVC PIPE (MIN. SCHEDULE 40)
24"
L
STANDPIPE DISCHARGE
6"X 5" 90O REDUCING ELBOW
STEAMER NOZZLE CAP - SEE NOTE 1
5" N.P.T. X 4 1/2" STEAMER NOZZLE
NUMBER OF HOLES FOR 4 TIMES AREA OF PIPE
PIPE SIZE
HOLE SIZE
MINIMUM LENGTH *
6" 8" 10" 12"
365 257 143 655 455 256 1024 711 400 1475 1024 576
0.625" 0.75" 1" 5/8" 3/4"
5' 6' 7.5' 9'
3' SOUTH OR 4' NORTH OF U.S. HWY 40 FOR EVAPORATION LOSSES OR ICE POTENTIAL
STATIC HEAD
24"
PROVIDE POST FOR IDENTIFICATION AND PROTECTION
EXTEND STANDPIPE BELOW NORMAL WATER LEVEL.
THE DEPTH OF COVER OVER THE PIPE SHALL BE GREATER THAN MAXIMUM FROST DEPTH.
STANDPIPE DISCHARGE
ROAD
STANDPIPE
C
ALL WEATHER
*BASED ON HOLE SPACING = 2 HOLE DIAMETERS

## Specifications
Seed
[8 empty] | at |  |  |  |  | lbs/acre
[8 empty] | at |  |  |  |  | lbs/acre
|  |  |  | Apply mulch at the rate of | [6 empty] | tons of straw per
acre
12
LANDUSER
COUNTY SWCD, INDIANA
LOCATION
[7 empty] | Sec. |  | T |  |  | R
DRAWING NO. IN-ENG-50-2.XLS (REV. 10/02)
DRY FIRE HYDRANT SPECIFICATIONS INDIANA
U.S. DEPARTMENT OF AGRICULTURE
| Apply lime to raise the pH to |  | at a |  | NATURAL RESOURCES CONSERVATION SERVICE
[6 empty] | Designed |  |  | Date |  | Approved by |  |  | Date
| rate of | tons per acre, if required | [6 empty] | 2002-10-09
[6 empty] | Drawn |  |  | 2002-10-09 |  | Title
[6 empty] | Traced |  |  |  |  | Title
[6 empty] | Checked |  |  |  |  | Sheet | Drawing No.
No.
of
IN-ENG-50 (2 OF 2)
OPERATION AND MAINTENANCE System must be checked and pump tested upon completion to verify system capacity and condition. Perform regular pump test and back flushing on at least an annual basis or as per NFPA recommendations. Records and schedules should be coordinated with local fire department training and testing needs. Maintain access to dry hydrant free of debris and woody vegetation. Keep the all-weather road clear of snow and debris and in good repair. Maintain area in pond around intake strainer free from floating debris and all pond vegetation that could become lodged in the strainer during pumping. Water weeds must not be allowed to plug the inlet of the pipe.
Fertilize according to soil test recommendations or at a rate of 500 pounds of 12-12-12 fertilizer (or equivalent) per acre as soon as the basin has been installed if within seeding dates. Work the fertilizer and lime into the soil to a depth of 2 - 3 inches with a harrow, disk or hand tools. Seeding will be done at the following rates:
Dormant seeding may be done between December 10 and February 28. Liming, fertilizing, seedbed preparation and mulching may be done at the end of construction ahead of the dormant seeding. The seed may be broadcast on top of the mulch with a 50% increase in rate.
GENERAL Construction operations shall be carried out in such a manner and sequence that erosion and pollution potential will be minimized. Ideally, a dry hydrant should be installed during the initial construction of a pond. The competed job shall present an appearance of good workmanship and shall conform to the lines, grades, and elevations shown on the drawings. All operations shall be carried out in a safe and skillful manner. Safety and health regulations shall be observed and appropriate safety measures used. SITE PREPARATION All trees, stumps, brush, and similar materials are to be removed from the construction area and disposed in a manner consistent with environmental concerns and proper functioning of the structure. EXCAVATION To the extent needed, all suitable materials removed from the specified excavation shall be used in the backfill for the dry hydrant and connection pipe. All excess material shall be spread adjacent to the structure, sloped to drain and vegetated or otherwise disposed of in an acceptable manner. CONSTRUCTION TOLERANCES Dry hydrant dimensions and elevations: 0.1 feet Connection Pipe length: 2.0 feet Connection Pipe elevations: 0.2 feet FINISH AND CLEANUP The area and designated spoil areas will be finished in a relatively smooth condition ready for seeding. All rocks 3 inches in diameter or larger and roots shall be removed from the surface areas. VEGETATIVE ESTABLISHMENT All disturbed areas shall be vegetated unless otherwise protected from erosion.
+
+
+

## SITE AND LOCATION
12
LANDUSER
COUNTY SWCD, INDIANA
LOCATION
|  |  | Sec. | T |  |  | R
DRAWING NO. IN-ENG-42.XLS (REV. 10/02)
SITE AND LOCATION MAP
U.S. DEPARTMENT OF AGRICULTURE
NATURAL RESOURCES CONSERVATION SERVICE
|  | Designed |  | Date |  | Approved by |  |  | Date
2002-10-09
|  | Drawn |  | 2002-10-09 |  | Title
|  | Traced |  |  |  | Title
|  | Checked |  |  |  | Sheet | Drawing No.
No.
of
IN-ENG-42

## Charts (hidden)
Table A
Dia/Flow | 500 | 750 | 1000 | 1250 | 1500 | 2000
6 | 0.4 | 0.8 | 1.4 | 2.2 | 3.2 | 5.6
8 | 0.1 | 0.3 | 0.4 | 0.7 | 1 | 1.8
10 | 0.1 | 0.1 | 0.2 | 0.3 | 0.4 | 0.7
12 | -- | 0.1 | 0.1 | 0.2 | 0.3 | 0.3
Table B
Dia/Flow | 500 | 750 | 1000 | 1250 | 1500 | 2000
6 | 0.016 | 0.033 | 0.057 | 0.086 | 0.012 | 0.204
8 | 0.004 | 0.008 | 0.014 | 0.021 | 0.03 | 0.05
10 | 0.001 | 0.003 | 0.005 | 0.007 | 0.01 | 0.017
12 | 0.001 | 0.001 | 0.002 | 0.003 | 0.004 | 0.007