## Overall Requirements
CONTROLS REQUIREMENTS FOR NuMI
2003-03-11
Ref # | System / Device | Name | Controller | MADC Twinax | MADC BNC/TWIN | MADC BNC | Beam Permit | Controls Assignments | Comments | Contact
Ordering of System / Device: Power Supplies, Trim Supplies, Instrumentation, Vacuum, Water, Special, Timing, Digital I/O, MADC, Beam Permit, Ethernet, VME, Console
MI-60 Service Building - South " 60S" | [8 empty] | Existing Controls Infrastructure is Thought to be Adequate Here for NuMI Requirements.
1 | Single Turn Extraction Kicker | I:KPS6N | 466 | 5 |  |  | 2A 1D | CC $63 | PS in South PS Room. Controls for PS in South Equipment Room. ~MI60124 | Chris Jensen
2 | Main Injector Performance Parameters | [7 empty] | Alberto is the Lead Here and Will Be Joined by Others | Alberto Marchionni
2-1 | Main Injector Low Level RF System Nominal Operation | [5 empty] | 1D |  | To Be Defined. Thought to Include RF Frequency and Radial Position as Nominal | Alberto Marchionni
2-2 | P-Bar Production Beam Not Present Before NuMI Extraction |  |  |  | 1 |  | 1D or 1A |  | To Be Derived From Local Beam Monitors | Alberto Marchionni
2-3 | P-Bar Extraction Through P150 Line Not Exceptionally Lossy |  |  |  | 1 |  | 1A |  | Information from a Selected P150 Line Loss Monitor | Alberto Marchionni
2-4 | Longitudinal Bunch Length Nominal Before NuMI Extraction |  |  |  | 1 |  | 1A |  |  | Alberto Marchionni
2-5 | Other Reasonably Derived Qualifications |  |  |  | ? |  | A or D |  |  | Alberto Marchionni
3 | Flourinert Cooling System with Local PID Controller |  |  |  |  | 6 | 1A |  | Skid in South Power Supply Room | Chris Jensen Scott Reeves
4 | Clock Event Scaler |  | 333 | [5 empty] | Events of Interest: $A5, $23, $19, $52 After $19, $53 After $19, MIBS $74, $A9, $A6 | Greg Vogel Bob Ducar
5 | MIBS Timing Channel Ref $74 |  | 479 | [5 empty] | Actually Fires the Kicker. NuMI BP ANDed with Pulse Output within the Module. | Chris Jensen Greg Vogel
5-1 | Internal Fire Kicker 479 Timing Pulse ANDed with Beam Permit False and Stretched by One-Shot | [5 empty] | 1D |  | To Record the Loss of Beam Permit After MIBS $74 Has Been Issued. | Greg Vogel Bob Ducar
6 | MIBS $74 Request Ref $23 |  | 377 | [5 empty] | Other Channels Also Needed. See Jensen for Details and Possible Names. | Chris Jensen Greg Vogel
7 | Digital In - Digital Out Facility |  | 184 |  |  |  |  | CC $63 | Potential for Control and Monitor of Local Systems. May Be Needed for Flourinert Cooling System. | Greg Vogel Bob Ducar
8 | MADC Facility | MADC #65 | 290 |  |  |  |  | CC $63 | 14 Bit Resolution Required Here. Expect to Use Already Installed MADC #65 That Has Lots of Free Channels. | KC Seino Rupe Crouch
9 | NuMI Beam Permit |  | 200 |  |  |  |  | CC $63 N22 | 1 x 200 is Thought to be Enough Here. This Location is the End of the Beam Permit "Loop". Location of 201 is at MINOS Service Building. | Greg Vogel Bob Ducar
9-1 | Radiation Safety System Beam Permit Input | [5 empty] | 1D |  | Other 200 Module Locations May Be More Convenient for Input. | Chuck Worel Bob Ducar
10 | Beam Permit Process Channel Interface and Controller |  | 204 |  |  |  | 1D |  | Output to Local 200 Beam Permit Module. | Al Franck Bob Ducar
11 | Ethernet Connectivity | [7 empty] | Already Exists at this Location | Dan Stenman
12 | VME with Connection to Ethernet | [7 empty] | Already Exists at this Location | Dan Stenman
13 | ACNET Console X Terminal | [7 empty] | Already Exists at this Location | Dan Stenman
MI-60 Service Bldg - North "60N" | [8 empty] | Existing Controls Infrastructure is Thought to be Adequate Here for NuMI Requirements. Expect Most of the Big Power Supply Controllers for the Below to be Located in Equipment Racks MI60218 and MI60220.
1 | Lambertson Power Supply for LAM60 | I:LAM60 | 468 | 4 * |  |  | 3A 1D | CC $73 N15-16 | Big PEI/Transrex in North Equipment Gallery. Ramped. Critical Device | Steve Hays
2 | Lambertson Power Supply for LAM61A and LAM61B | I:LAM61 | 468 | 4 * |  |  | 3A 1D |  | Big PEI/Transrex in North Equipment Gallery. Ramped. Critical Device | Steve Hays
3 | C Magnet Power Supply | E:V100 | 468 | 4 * |  |  | 3A 1D | CC $73 N17-18 | Big PEI/Transrex in North Equipment Gallery. Ramped. Critical Device | Steve Hays
4 | EPB Dipole String (6) | E:HV101 | 468 | 6 ** |  |  | 3A 1D | CC $73 N19-20 | Three Big PEI/Transrex in North Power Supply Room. Ramped. Critical Device | Steve Hays
4-1 | Local PLC for Extended Power Supply Status |  | PLC Ethernet | [6 empty] | Steve Hays
5 | Horizontal Trim Dipole | E:H104 | 466 | 4 * |  |  | 3A 1D |  | Smaller PEI. In North Equipment Gallery. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
6 | Quadrupole Power Supply (3Q120) | E:Q101 | 466 | 4 * |  |  | 3A 1D | CC $73 N2 | Smaller PEI. In North Equipment Gallery. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
7 | Quadrupole Power Supply (3Q120) | E:Q102 | 466 | 4 * |  |  | 3A 1D | CC $73 N3 | Smaller PEI. In North Equipment Gallery. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
8 | Quadrupole Power Supply (3Q120) | E:Q103 | 466 | 4 * |  |  | 3A 1D | CC $73 N4 | Smaller PEI. In North Equipment Gallery. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
9 | Quadrupole Power Supply (3Q60) | E:Q104 | 466 | 4 * |  |  | 3A 1D |  | Smaller PEI. In North Equipment Gallery. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
10 | Quadrupole Power Supply (3Q120) | E:Q105 | 466 | 4 * |  |  | 3A 1D |  | Smaller PEI. In North Equipment Gallery. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
11 | Quadrupole Power Supply (3Q120) | E:Q106 | 466 | 4 * |  |  | 3A 1D |  | Smaller PEI. In North Equipment Gallery. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
12 | Trim Element Regulators (10) |  | The CAMAC 453 Slot Assignments Reflect a Reordering Suggested by Leon Bartelson to Align Controls Modules with Regulator Placement. | [5 empty] | These Trims Elements Controlled from Existing MI Regulator System at MI-60 North in Equipment Rack MI60205 | Leon Bartelson
12-1 | Horizontal Trim Element #1 Located Upstream of HV101-1 EPB Dipole | E:HT102 | .25 x 453 | 4 Direct to MADC 77 |  |  | 1D | CC $74 N12-13 | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-2 | Vertical Trim Element #2 Located Upstream of Q103 | E:VT103 | .25 x 453 | 4 Direct to MADC 77 |  |  | 1D | CC $74 N12-13 | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-3 | Horizontal Trim Element #3 Located Downstream of Q105 | E:HT105 | .25 x 453 | 4 Direct to MADC 77 |  |  | 1D | CC $74 N12-13 | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-4 | Vertical Trim Element #4 Located Downstream of Q106 | E:VT106 | .25 x 453 | 4 Direct to MADC 77 |  |  | 1D | CC $74 N12-13 | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-5 | Horizontal Trim Element #5 Located Downstream of Q107 | E:HT107 | .25 x 453 | 4 Direct to MADC 77 |  |  | 1D | CC $74 N14-15 | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-6 | Vertical Trim Element #6 Located Upstream of Q108 | E:VT108 | .25 x 453 | 4 Direct to MADC 77 |  |  | 1D | CC $74 N14-15 | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-7 | Horizontal Trim Element #7 Located Upstream of Q109 | E:HT109 | .25 x 453 | 4 Direct to MADC 77 |  |  | 1D | CC $74 N14-15 | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-8 | Vertical Trim Element #8 Located Upstream of Q110 | E:VT110 | .25 x 453 | 4 Direct to MADC 77 |  |  | 1D | CC $74 N14-15 | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-9 | Vertical Trim Element #9 Located Upstream of Q111 | E:VT111 | .25 x 453 | 4 Direct to MADC 77 |  |  | 1D | CC $74 N16-17 | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-10 | Horizontal Trim Element #10 Located Upstream of Q112 | E:HT112 | .25 x 453 | 4 Direct to MADC 77 |  |  | 1D | CC $74 N16-17 | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-11 | Spare Channel |  | .25 x 453 |  |  |  |  | CC $74 N16-17 |  | Leon Bartelson
12-12 | Spare Channel |  | .25 x 453 |  |  |  |  | CC $74 N16-17 |  | Leon Bartelson
13 | Beam Position Detectors (13 Total) |  |  | MI-60N Cable Distances | MI-62 Cable Distances |  |  |  | Located Here at MI-60N to Save 8K Ft of Cable. Using 3/8" Andrew Heliax LDF2-50 Cable. Suggest Positioning VME Crate in Rack MI60203. | Gianni Tassotto Vic Scarpine
13-1 | Vertical BPM Downstream of Q101 | E:VP101 | VME Ethrnt | 175 | 838 |  | No |  | Four BPMs per VME Module | Gianni Tassotto Vic Scarpine
13-2 | Horizontal BPM Downstream of Q101 | E:HP101 | VME Ethrnt | 175 | 837 |  | No |  |  | Gianni Tassotto Vic Scarpine
13-3 | Horizontal BPM Downstream of Q102 | E:HP102 | VME Ethrnt | 226 | 788 |  | No |  |  | Gianni Tassotto Vic Scarpine
13-4 | Vertical BPM Downstream of Q103 | E:VP103 | VME Ethrnt | 273 | 741 |  | No |  |  | Gianni Tassotto Vic Scarpine
13-5 | Horizontal BPM Upstream of Q104 | E:HP104 | VME Ethrnt | 291 | 716 |  | No |  | Four BPMs per VME Module | Gianni Tassotto Vic Scarpine
13-6 | Horizontal BPM Upstream of Q105 | E:HP105 | VME Ethrnt | 304 | 703 |  | No |  |  | Gianni Tassotto Vic Scarpine
13-7 | Vertical BPM Upstream of Q106 | E:VP106 | VME Ethrnt | 360 | 645 |  | No |  |  | Gianni Tassotto Vic Scarpine
13-8 | Horizontal BPM Upstream of Q107 | E:HP107 | VME Ethrnt | 425 | 610 |  | No |  |  | Gianni Tassotto Vic Scarpine
13-9 | Vertical BPM Upstream of Q108 | E:VP108 | VME Ethrnt | 473 | 578 |  | No |  | Four BPMs per VME Module | Gianni Tassotto Vic Scarpine
13-10 | Horizontal BPM Downstream of Q109 | E:HP109 | VME Ethrnt | 539 | 677 |  | No |  |  | Gianni Tassotto Vic Scarpine
13-11 | Vertical BPM Downstream of Q110 | E:VP110 | VME Ethrnt | 570 | 626 |  | No |  |  | Gianni Tassotto Vic Scarpine
13-12 | Vertical BPM Downstream of Q111 | E:VP111 | VME Ethrnt | 655 | 621 |  | No |  |  | Gianni Tassotto Vic Scarpine
13-13 | Horizontal BPM Downstream of Q112 | E:HP112 | VME Ethrnt | 670 | 636 |  | No |  | Four BPMs per VME Module | Gianni Tassotto Vic Scarpine
|  |  | Total Feet @ 2 Each | 10272 | 18032
14 | Beam Profile Monitors - Multiwires (5 Total) |  |  | MI-60N Cable Distances | MI-62 Cable Distances |  |  |  | Located Here at MI-60N or MI-62 ???? Cable Distances and Rack Space Will Decide. Investigate Locating in Rack MI60218 or MI60226. | Gianni Tassotto Dan Schoo
14-1 | Multiwire Downstream of Q101 | E:PM101 | ARCNET VME Ethrnt | 175 | 837 |  | 1D |  | Motor Drive Hardware Handles Four Multiwires | Gianni Tassotto Dan Schoo
14-2 | Multiwire Upstream of Q105 | E:PM105 | ARCNET VME Ethrnt | 304 | 703 |  | 1D |  |  | Gianni Tassotto Dan Schoo
14-3 | Multiwire Upstream of Q107 | E:PM107 | ARCNET VME Ethrnt | 425 | 610 |  | 1D |  | Beam Permit Only If Multiwire is IN or OUT, Not In Between | Gianni Tassotto Dan Schoo
14-4 | Multiwire Upstream of Q108 | E:PM108 | ARCNET VME Ethrnt | 473 | 578 |  | 1D |  |  | Gianni Tassotto Dan Schoo
14-5 | Multiwire Downstream of Q112 | E:PM112 | ARCNET VME Ethrnt | 670 | 636 |  | 1D |  | Motor Drive Hardware Handles Four Multiwires | Gianni Tassotto Dan Schoo
|  |  | Total Feet @ 2 Each | 4094 | 6728
14-6 | Clearing High Voltage Power Supplies |  | 2x053 ? |  | 5 |  | No |  | For Kopp Style MW. PREP NIM Modules at 1 per MW. Some Control Interface Required. | Gianni Tassotto Dan Schoo
15 | Loss Monitors (Chassis #1) | [7 empty] | Reg Loss Monitor Electronics Packages 12 Channels in One Chassis with HV Supply. Investigate Locating in Rack MI60218 or MI60219 or MI60226. | Gianni Tassotto Marv Olson
15-1 | Regular Loss Monitor HV Supply Output Chassis #1 | E:LMHV1O |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-2 | Regular Loss Monitor HV Supply Return Chassis #1 | E:LMHV1R |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-3 | Loss Monitor #1 at KM602A | I:LMNKMA |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-4 | Loss Monitor #2 at KM602B | I:LMNKMB |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-5 | Loss Monitor #3 at KM602C | I:LMNKMC |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-6 | Loss Monitor #4 at LAM60 | I:LML60 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-7 | Loss Monitor #5 at LAM61A | I:LML61A |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-8 | Loss Monitor #6 at LAM61B | I:LML61B |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-9 | Loss Monitor #7 at V100 | E:LMV100 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-10 | Loss Monitor #8 at Q101 | E:LMQ101 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-11 | Loss Monitor #9 at HV101-1 | E:LM1011 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-12 | Loss Monitor #10 at HV101-2 | E:LM1012 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
15-13 | Loss Monitor #11 - Spare | E:LM1C11 | [7 empty] | Gianni Tassotto Marv Olson
15-14 | Loss Monitor #12 - Spare | E:LM1C12 | [7 empty] | Gianni Tassotto Marv Olson
16 | Loss Monitors (Chassis #2) | [7 empty] | Reg Loss Monitor Electronics Packages 12 Channels in One Chassis with HV Supply. Investigate Locating in Rack MI60218 or MI60219 or MI60226. | Gianni Tassotto Marv Olson
16-1 | Regular Loss Monitor HV Supply Output Chassis #2 | E:LMHV2O |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-2 | Regular Loss Monitor HV Supply Return Chassis #2 | E:LMHV2R |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-3 | Loss Monitor #1 at Q102 | E:LMQ102 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-4 | Loss Monitor #2 at HV101-3 | E:LM1013 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-5 | Loss Monitor #3 at HV101-4 | E:LM1014 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-6 | Loss Monitor #4 at HV101-5 | E:LM1015 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-7 | Loss Monitor #5 at HV101-6 | E:LM1016 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-8 | Loss Monitor #6 at Q104 | E:LMQ104 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-9 | Loss Monitor #7 at H104 | E:LMH104 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-10 | Loss Monitor #8 at Q105 | E:LMQ105 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-11 | Loss Monitor #9 at Q106 | E:LMQ106 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-12 | Loss Monitor #10 at Q107 | E:LMQ107 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
16-13 | Loss Monitor #11 - Spare | E:LM2C11 | [7 empty] | Gianni Tassotto Marv Olson
16-14 | Loss Monitor #12 - Spare | E:LM2C12 | [7 empty] | Gianni Tassotto Marv Olson
17 | Vacuum (MI System Additions) |  | ARCNET VME Ethrnt | [6 empty] | Leon Bartelson
17-1 | 40L/Sec Ion Pumps (Quantity 12) | I: |  |  |  |  | No |  | 4 for Each of Three Lambertsons | Leon Bartelson
17-2 | Pirani Gauges | I: |  |  |  |  | No |  | Proximate to Lambertsons | Leon Bartelson
17-3 | Isolation Valves | I: |  |  |  |  | 1D |  | Downstream of Lambertsons. Isolates MI from NuMI Vacuum. | Leon Bartelson
18 | MADC Facility |  | 290 | [5 empty] | 14 Bit Resolution Required Here. Some Chance of Needing Another MADC Here. | KC Seino Rupe Crouch
19 | NuMI Beam Permit |  | 2 x 200 |  |  |  |  | CC $73 N21 CC $73 N22 |  | Greg Vogel Bob Ducar
20 | Beam Permit Process Channel Interface and Controller |  | 2 x 204 |  |  |  | 2D |  | Outputs to Local 200 Beam Permit Modules. 33 Power Supply and 24 Loss Monitor Channels. | Al Franck Bob Ducar
21 | Ethernet Connectivity | [7 empty] | Already Exists at this Location | Dan Stenman
22 | VME with Connection to Ethernet | [7 empty] | Already Exists at this Location | Dan Stenman
23 | ACNET Console X Terminal | [7 empty] | Already Exists at this Location | Dan Stenman
MI-62 Service Building "62SB" |  |  | Note to Joe Gomilar: 468 Module at CAMAC Crate $6C N2-3 is No Longer Required. | [5 empty] | Basic Controls Infrastructure is Present. Likely to Need Additional Crates and MADCs. Four New Racks (MI62111-114) Have Been Installed in Controls/Kicker Room. These Will Support Vacuum (111 & 112) and Instrumentation (113 & 114).
1 | B2 Dipole String (6) | E:V108 | 468 | 6 ** |  |  | 3A 1D | CC $6C N4-5 | A Relocated Main Ring Power Supply Will Accommodate This Load. Located in Power Supply Room. | Steve Hays
2 | Quadrupole Power Supply (3Q120) | E:Q107 | 466 | 4 * |  |  | 3A 1D | CC $6C N14 | Smaller PEI in Power Supply Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
3 | Quadrupole Power Supply (3Q120) | E:Q108 | 466 | 4 * |  |  | 3A 1D | CC $6C N15 | Smaller PEI in Power Supply Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
4 | Quadrupole Power Supply (3Q120) | E:Q109 | 466 | 4 * |  |  | 3A 1D | CC $6C N16 | Smaller PEI in Power Supply Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
5 | Quadrupole Power Supply (3Q60) | E:Q110 | 466 | 4 * |  |  | 3A 1D | CC $6C N17 | Smaller PEI in Power Supply Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
6 | Quadrupole Power Supply (3Q120) | E:Q111 | 466 | 4 * |  |  | 3A 1D | CC $6C N18 | Smaller PEI in Power Supply Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
7 | Quadrupole Power Supply (3Q120) | E:Q112 | 466 | 4 * |  |  | 3A 1D |  | Smaller PEI in Power Supply Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
8 | Beam Profile Monitors - Multiwires (5 Total) |  |  | MI-60N Cable Distances | MI-62 Cable Distances |  |  |  | Located Here at MI-62 or MI-60N ???? Cable Distances and Available Rack Space at MI-60N Will Decide. | Gianni Tassotto Dan Schoo
8-1 | Multiwire Downstream of Q101 | E:PM101 | ARCNET VME Ethrnt | 175 | 837 |  | 1D |  | Motor Drive Hardware Handles Four Multiwires | Gianni Tassotto Dan Schoo
8-2 | Multiwire Upstream of Q105 | E:PM105 | ARCNET VME Ethrnt | 304 | 703 |  | 1D |  |  | Gianni Tassotto Dan Schoo
8-3 | Multiwire Upstream of Q107 | E:PM107 | ARCNET VME Ethrnt | 425 | 610 |  | 1D |  | Beam Permit Only If Multiwire is IN or OUT, Not In Between | Gianni Tassotto Dan Schoo
8-4 | Multiwire Upstream of Q108 | E:PM108 | ARCNET VME Ethrnt | 473 | 578 |  | 1D |  |  | Gianni Tassotto Dan Schoo
8-5 | Multiwire Downstream of Q112 | E:PM112 | ARCNET VME Ethrnt | 670 | 636 |  | 1D |  | Motor Drive Hardware Handles Four Multiwires | Gianni Tassotto Dan Schoo
|  |  | Total Feet @ 2 Each | 4094 | 6728
8-6 | Clearing High Voltage Power Supplies |  | 2x053 ? |  | 5 |  | No |  | For Kopp Style MW. PREP NIM Modules at 1 per MW. Some Control Interface Required. | Gianni Tassotto Dan Schoo
9 | Loss Monitors (Chassis #3) | [7 empty] | Reg Loss Monitor Electronics Packages 12 Channels in One Chassis with HV Supply | Gianni Tassotto Marv Olson
9-1 | Regular Loss Monitor HV Supply Output Chassis #3 | E:LMHV3O |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-2 | Regular Loss Monitor HV Supply Return Chassis #3 | E:LMHV3R |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-3 | Loss Monitor #1 at Q108 | E:LMQ108 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-4 | Loss Monitor #2 at V108-1 | E:LM1081 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-5 | Loss Monitor #3 at V108-2 | E:LM1082 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-6 | Loss Monitor #4 at Q109 | E:LMQ109 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-7 | Loss Monitor #5 at V108-3 | E:LM1083 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-8 | Loss Monitor #6 at V108-4 | E:LM1084 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-9 | Loss Monitor #7 at Q110 | E:LMQ110 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-10 | Loss Monitor #8 at V108-5 | E:LM1085 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-11 | Loss Monitor #9 at V108-6 | E:LM1086 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-12 | Loss Monitor #10 at Q111 | E:LMQ111 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-13 | Loss Monitor #11 at Q112 | E:LMQ112 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
9-14 | Loss Monitor #12 - Spare | E:LM3C12 |  |  |  | 1 |  |  |  | Gianni Tassotto Marv Olson
10 | Total Loss Monitors (4 Total) | [7 empty] | These TLMs Are Likely to be Inputs to Beam Loss Budget Monitor (BLBM) Facility | Gianni Tassotto
10-1 | Total Loss Monitor #1 for NuMI Stub and Lucas Room | E:TLMNS |  |  | 1 |  | 1A |  |  | Gianni Tassotto
10-2 | Total Loss Monitor #2 for Carrier Tunnel Upstream End | E:TLMCTU |  |  | 1 |  | 1A |  |  | Gianni Tassotto
10-3 | Total Loss Monitor #3 for Carrier Tunnel Downstream End | E:TLMCTD |  |  | 1 |  | 1A |  |  | Gianni Tassotto
10-4 | Total Loss Monitor #4 for Pre-Target Area | E:TLMPT |  |  | 1 |  | 1A |  |  | Gianni Tassotto
10-5 | Total Loss Monitor High Voltage | E:TLMHV |  |  | 1 |  | 1A |  | Details Unknown | Gianni Tassotto
10-6 | Total Loss Monitor Gas Flow | E:TLMGF |  |  | 1 |  | 1D or 1A |  | Details Unknown | Gianni Tassotto
11 | Beam Intensity Toroid #1 | E:NIUP |  |  | 1 |  | No |  |  | Gianni Tassotto
12 | Beam Intensity Toroid #2 | E:NIDN |  |  | 1 |  | No |  | Long Cable Run into Pre-Target Area | Gianni Tassotto
13 | Beam Intensity Toroid Difference Signal (Toroid #1 - Toroid #2) | E:NIDIFF |  |  | 1 |  | 1A |  |  | Gianni Tassotto
14 | Vacuum (All of NuMI Beamline) |  | ARCNET VME Ethrnt | [5 empty] | Vacuum Equipment in Controls/Kicker Room Rack MI62111 and MI62112 | Leon Bartelson Jim Klen
14-1 | 500L/Sec Ion Pumps (Quantity 4) | [5 empty] | No |  | 2 Each at Either End of 12 Inch Beam Pipe in Upstream Portion of Carrier Tunnel | Leon Bartelson Jim Klen
14-2 | 40L/Sec Ion Pumps (Quantity 38) | [5 empty] | No |  | Distributed Throughout the Beamline. Locations Remain to be Detailed. | Leon Bartelson Jim Klen
14-3 | Pirani Gauges (Quantity 6) | [5 empty] | 3A |  | 2 Gauges at Each End of the Three Sections of the NuMI Vacuum System. | Leon Bartelson Jim Klen
14-4 | Isolation Valves (Quantity 3) But One of These Controlled by MI System at MI-60N | [5 empty] | 3D |  | First is Located Just Downstream of Lambertsons and Controlled by MI System. 2nd and 3rd at Either End of 12 Inch Beam Pipe in Upstream Portion of Carrier Tunnel. | Leon Bartelson Jim Klen
15 | MI-62 LCW and Pond Water Systems |  | PLC Ethernet | [5 empty] | PLC Hardware Expected to be Located in Large Hoffman Style Enclosure on East Wall of Controls/Kicker Room Behind Rack MI62109 | Dave Pushka Maurice Ball KC Seino
15-1 | Various NuMI LCW Control and Monitor Points | E:62Winn | PLC Ethernet |  |  |  | 1D |  | Detailed Separately | Dave Pushka Bob Ducar
15-2 | Various Pond Water Control and Monitor Points | E:62Pinn | PLC Ethernet |  |  |  | No |  | Detailed Separately | Dave Pushka Bob Ducar
16 | MIBS Timing Capability |  | 479 | [5 empty] | Likely Necessary for Instrumentation (?) | Greg Vogel Rupe Crouch
17 | MADC Facility |  | ? X 290 | [5 empty] | New Requirements Not Fully Established. 12 Bit Resolution for Loss Monitors is OK. | KC Seino Rupe Crouch
18 | NuMI Beam Permit |  | 2 x 200 |  |  |  |  | CC $6A N21 CC $6A N22 |  | Greg Vogel Bob Ducar
19 | Beam Permit Process Channel Interface and Controller |  | 2 x 204 |  |  |  | 2D |  | Outputs to Local 200 Beam Permit Modules. 21 Power Supply, 18 Loss Monitor and 4 or More Miscellaneous. | Al Franck Bob Ducar
20 | Ethernet Connectivity | [7 empty] | Already Exists at this Location | Dan Stenman
21 | VME with Connection to Ethernet | [7 empty] | Already Exists at this Location | Dan Stenman
22 | ACNET Console X Terminal | [7 empty] | Already Exists at this Location | Dan Stenman
MI-65 Service Bldg Electronics Rm "65SB" |  |  | Beneficial Occupancy September 2003 | [5 empty] | New Basic Controls Infrastructure is Required Here. Will Link to Existing Controls at MI-62. This Location Will Support Similar Infrastructure in the Power Supply Support Room ~120 Feet Below. Room for ~9 Equipment Racks Here - Way More Than Enough Room for Needed Equipment.
1 | Horizontal Trim Dipole | E:H117 | 466 | 4 * |  |  | 3A 1D | CC $ | Smaller PEI in Electrical Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
2 | B2 Dipole String (4) in Pre-Target Area | E:V118 | 468 | 6 ** |  |  | 3A 1D | CC $ | Multiple Larger PEI/Transrex Supplies Will Likely Accommodate This Load. Located in Electrical Room. | Steve Hays
2-1 | Local PLC for Extended Power Supply Status |  | PLC Ethernet | [6 empty] | Steve Hays
3 | Quadrupole Power Supply (3Q120) | E:Q113 | 466 | 4 * |  |  | 3A 1D | CC $ | Smaller PEI in Electrical Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
4 | Quadrupole Power Supply (3Q120) | E:Q114 | 466 | 4 * |  |  | 3A 1D | CC $ | Smaller PEI in Electrical Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
5 | Quadrupole Power Supply (3Q60) | E:Q115 | 466 | 4 * |  |  | 3A 1D | CC $ | Smaller PEI in Electrical Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
6 | Quadrupole Power Supply (3Q120) | E:Q116 | 466 | 4 * |  |  | 3A 1D | CC $ | Smaller PEI in Electrical Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
7 | Quadrupole Power Supply (3Q120) | E:Q117 | 466 | 4 * |  |  | 3A 1D | CC $ | Smaller PEI in Electrical Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
8 | Quadrupole Power Supply (3Q120) | E:Q118 | 466 | 4 * |  |  | 3A 1D | CC $ | Smaller PEI in Electrical Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
9 | Quadrupole Power Supply (3Q60) | E:Q119 | 466 | 4 * |  |  | 3A 1D | CC $ | Smaller PEI in Electrical Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
10 | Quadrupole Power Supply (3Q120) | E:Q120 | 466 | 4 * |  |  | 3A 1D | CC $ | Smaller PEI in Electrical Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
11 | Quadrupole Power Supply (3Q120) | E:Q121 | 466 | 4 * |  |  | 3A 1D | CC $ | Smaller PEI in Electrical Room. Could Run DC but 466 Gives Option to Ramp. | Steve Hays
12 | Trim Element Regulators (9) | [7 empty] | All Trim Elements Controlled from New Regulator System in Electronics Room | Leon Bartelson
12-1 | Vertical Trim Element #1 Located Downstream of Q113 | E:VT113 | .25 x 453 | 4 Direct to MADC |  |  | 1D | CC $ | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-2 | Horizontal Trim Element #2 Located Upstream of Q114 | E:HT114 | .25 x 453 | 4 Direct to MADC |  |  | 1D | CC $ | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-3 | Horizontal Trim Element #3 Located Downstream of Q115 | E:HT115 | .25 x 453 | 4 Direct to MADC |  |  | 1D | CC $ | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-4 | Vertical Trim Element #4 Located Downstream of Q116 | E:VT116 | .25 x 453 | 4 Direct to MADC |  |  | 1D | CC $ | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-5 | Horizontal Trim Element #5 Located Downstream of Q117 | E:HT117 | .25 x 453 | 4 Direct to MADC |  |  | 1D | CC $ | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-6 | Vertical Trim Element #6 Located Downstream of Q118 | E:VT118 | .25 x 453 | 4 Direct to MADC |  |  | 1D | CC $ | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-7 | Horizontal Trim Element #7 Located Upstream of Q119 | E:HT119 | .25 x 453 | 4 Direct to MADC |  |  | 1D | CC $ | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-8 | Horizontal Trim Element #8 Located Downstream of Q121 | E:HT121 | .25 x 453 | 4 Direct to MADC |  |  | 1D | CC $ | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-9 | Vertical Trim Element #9 Located Downstream of Q121 | E:VT121 | .25 x 453 | 4 Direct to MADC |  |  | 1D | CC $ | Plan to Ramp to Keep RMS Power Low. Analog Mon: Vref, Vout, I out, I rms | Leon Bartelson
12-10 | Spare Channel |  | .25 x 453 |  |  |  |  | CC $ |  | Leon Bartelson
12-11 | Spare Channel |  | .25 x 453 |  |  |  |  | CC $ |  | Leon Bartelson
12-12 | Spare Channel |  | .25 x 453 |  |  |  |  | CC $ |  | Leon Bartelson
13 | Beam Position Detectors (11) | [7 empty] | Using 3/8" Andrew Heliax LDF2-50RN Cable. | Gianni Tassotto Vic Scarpine
13-1 | Vertical BPM Upstream of Q113 | E:VP113 | VME Ethrnt |  |  |  | No |  | Four BPMs per VME Module | Gianni Tassotto Vic Scarpine
13-2 | Horizontal BPM Downstream of Q114 | E:HP114 | VME Ethrnt |  |  |  | No |  |  | Gianni Tassotto Vic Scarpine
13-3 | Horizontal BPM Upstream of Q115 | E:HP115 | VME Ethrnt |  |  |  | No |  |  | Gianni Tassotto Vic Scarpine
13-4 | Vertical BPM Upstream of Q116 | E:VP116 | VME Ethrnt |  |  |  | No |  |  | Gianni Tassotto Vic Scarpine
13-5 | Horizontal BPM Upstream of Q117 | E:HP117 | VME Ethrnt |  |  |  | No |  | Four BPMs per VME Module | Gianni Tassotto Vic Scarpine
13-6 | Vertical BPM Upstream of Q118 | E:VP118 | VME Ethrnt |  |  |  | No |  |  | Gianni Tassotto Vic Scarpine
13-7 | Horizontal BPM Downstream of Q119 | E:HP119 | VME Ethrnt |  |  |  | No |  |  | Gianni Tassotto Vic Scarpine
13-8 | Horizontal BPM Downstream of Q121 | E:HP121 | VME Ethrnt |  |  |  | No |  |  | Gianni Tassotto Vic Scarpine
13-9 | Vertical BPM Downstream of Q121 | E:VP121 | VME Ethrnt |  |  |  | No |  | Four BPMs per VME Module | Gianni Tassotto Vic Scarpine
13-10 | Horizontal BPM Upstream of Target | E:HPTAR | VME Ethrnt |  |  |  | No |  |  | Gianni Tassotto Vic Scarpine
13-11 | Vertical BPM Upstream of Target | E:VPTAR | VME Ethrnt |  |  |  | No |  |  | Gianni Tassotto Vic Scarpine
14 | Beam Profile Monitors - Multiwires (5 Total) | [7 empty] | Associated Electronics Located in Electronics Room. | Gianni Tassotto Dan Schoo
14-1 | Multiwire Downstream of Q114 | E:PM114 | ARCNET VME Ethrnt |  |  |  | 1D |  | Motor Drive Hardware Handles Four Multiwires | Gianni Tassotto Dan Schoo
14-2 | Multiwire Upstream of Q115 | E:PM115 | ARCNET VME Ethrnt |  |  |  | 1D |  |  | Gianni Tassotto Dan Schoo
14-3 | Multiwire Upstream of Q117 | E:PM117 | ARCNET VME Ethrnt |  |  |  | 1D |  | Beam Permit Only If Multiwire is IN or OUT, Not In Between | Gianni Tassotto Dan Schoo
14-4 | Multiwire Downstream of Q121 | E:PM121 | ARCNET VME Ethrnt |  |  |  | 1D |  |  | Gianni Tassotto Dan Schoo
14-5 | Multiwire Upstream of Target | E:PMTAR | ARCNET VME Ethrnt |  |  |  | 1D |  | Motor Drive Hardware Handles Four Multiwires | Gianni Tassotto Dan Schoo
14-6 | Clearing High Voltage Power Supplies |  | 2x053 ? |  | 5 |  | No |  | For Kopp Style MW. PREP NIM Modules at 1 per MW. Some Control Interface Required. | Gianni Tassotto Dan Schoo
15 | TCLK Timing Capability |  | 178 + 377 | [5 empty] | For Local Instrumentation | Al Franck Bob Ducar
16 | MIBS Timing Capability |  | 479 | [5 empty] | For Local Instrumentation | Greg Vogel Bob Ducar
17 | MADC Facility |  | 2 x 290 | [5 empty] | 14 Bit Resolution Required Here for Power Supplies. Could Get By With a12 Bit for Trim Elements? | KC Seino Rupe Crouch
18 | NuMI Beam Permit |  | 200 | [6 empty] | Greg Vogel Bob Ducar
19 | Beam Permit Process Channel Interface and Controller |  | 204 | [5 empty] | Output to Local 200 Beam Permit Module. | Al Franck Bob Ducar
20 | Ethernet Connectivity | [7 empty] | Needed for Interface of Local Electronics and Console | Dan Stenman
21 | VME with Connection to Ethernet | [7 empty] | Needed for Interface of Local Electronics | Dan Stenman
22 | ACNET Console X Terminal | [7 empty] | Surely a Good Location | Dan Stenman
Target Hall Support Rooms (Below MI-65 Near Target Hall) "THSR" |  |  | Beneficial Occupancy September 2003 | [5 empty] | New Basic Controls Infrastructure is Required Here. Will Link to Existing Controls at MI-65 Above. All Controls Equipment Located in Power Supply Support Room.
1 | Horn Power Supply |  | IRM and CAMAC | [5 empty] | Two PEI 240KW and a Capacitor Bank. Much Control and Status for the Horn PS System Has Already Been Successfully Interfaced at MI-8 Via the IRM and Is Not Explicity Detailed Here. ~205,000 Amps to Horns. | Ken Bourkland Jim Biggs
1-1 | PEI-A Power Supply | E:NHSA | 468 |  |  |  | 1D |  | PS ON Digital Status to Beam Permit System. 2V Into 100 Ohms. | Ken Bourkland Jim Biggs
1-2 | PEI-B Power Supply | E:NHSB | 468 |  |  |  | 1D |  | PS ON Digital Status to Beam Permit System. 2V Into 100 Ohms. | Ken Bourkland Jim Biggs
1-3 | E:NHSA Output Waveform Reference | E:NHSAR | (468) | 1 |  |  | 1A |  | Local Selector Switch Selects One of These Waveforms as the Input to the Slow Start Module. E:NHSAR Is Normally Selected. | Ken Bourkland Jim Biggs
1-4 | E:NHSB Output Waveform Reference | E:NHSBR | (468) | 1 |  |  | 1A
1-5 | Waveform Reference to PEI-A After Slow Start Module | E:NHSASR | Slow Start Kluge | 1 |  |  | 1A |  | These Monitors Expected to Be Similar When Both Supplies Are Being Used and After the Slow Start. | Ken Bourkland Jim Biggs
1-6 | Waveform Reference to PEI-B After Slow Start Module | E:NHSBSR | Slow Start Kluge | 1 |  |  | 1A
1-7 | Current Output of PEI-A Power Supply to Capacitor Bank | E:NHSAI |  | 1 |  |  | 1A |  |  | Ken Bourkland Jim Biggs
1-8 | Current Output of PEI-B Power Supply to Capacitor Bank | E:NHSBI |  | 1 |  |  | 1A |  |  | Ken Bourkland Jim Biggs
1-9 | Power Supply Interlock (Permit) From "Local Controls" Electronics |  | Mr. Biggs |  |  |  | 1D |  |  | Ken Bourkland Jim Biggs
1-10 | Stripline Current for Horns (Horn 1 and Horn 2 in Series) | E:NHSLI | (377) | 1 |  |  | 1A |  | Stripline Current is Triggered About 1 Millisecond Before Beam, Likely by 377. | Ken Bourkland Jim Biggs
1-11 | Peak Stripline Current for Horns (Horn 1 and Horn 2 in Series) | E:NHSLIP |  | 1 |  |  | 1A |  | Sample and Hold Output | Ken Bourkland Jim Biggs
2 | Loss Monitors (Chassis #4) | [7 empty] | Reg Loss Monitor Electronics Packages 12 Channels in One Chassis with HV Supply | Gianni Tassotto Marv Olson
2-1 | Regular Loss Monitor HV Supply Output Chassis #4 | E:LMHV4O |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
2-2 | Regular Loss Monitor HV Supply Return Chassis #4 | E:LMHV4R |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
2-3 | Loss Monitor #1 at Q113 | E:LMQ113 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
2-4 | Loss Monitor #2 at Q114 | E:LMQ114 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
2-5 | Loss Monitor #3 at Q115 | E:LMQ115 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
2-6 | Loss Monitor #4 at Q116 | E:LMQ116 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
2-7 | Loss Monitor #5 at Q117 | E:LMQ117 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
2-8 | Loss Monitor #6 at H117 | E:LMH117 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
2-9 | Loss Monitor #7 at Q118 | E:LMQ118 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
2-10 | Loss Monitor #8 at V118-1 | E:LM1181 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
2-11 | Loss Monitor #9 at V118-2 | E:LM1182 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
2-12 | Loss Monitor #10 at Q119 | E:LMQ119 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
2-13 | Loss Monitor #11 - Spare | E:LM4C11 | [7 empty] | Gianni Tassotto Marv Olson
2-14 | Loss Monitor #12 - Spare | E:LM4C12 | [7 empty] | Gianni Tassotto Marv Olson
3 | Loss Monitors (Chassis #5) | [7 empty] | Reg Loss Monitor Electronics Packages 12 Channels in One Chassis with HV Supply | Gianni Tassotto Marv Olson
3-1 | Regular Loss Monitor HV Supply Output Chassis #5 | E:LMHV5O |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
3-2 | Regular Loss Monitor HV Supply Return Chassis #5 | E:LMHV5R |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
3-3 | Loss Monitor #1 at V118-3 | E:LM1183 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
3-4 | Loss Monitor #2 at V118-4 | E:LM1184 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
3-5 | Loss Monitor #3 at Q120 | E:LMQ120 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
3-6 | Loss Monitor #4 at Q121 | E:LMQ121 |  |  |  | 1 | 1A |  |  | Gianni Tassotto Marv Olson
3-7 | Loss Monitor #5 - Spare | E:LM5C5 |  |  |  | 1 ? | No |  | Loss Monitor For Horn 1 Alignment Could Be Assigned Here. | Gianni Tassotto Marv Olson Hylen/Talaga
3-8 | Loss Monitor #6 - Spare | E:LM5C6 |  |  |  | 1 ? | No |  | Loss Monitor For Horn 2 Alignment Could Be Assigned Here. | Gianni Tassotto Marv Olson Hylen/Talaga
3-9 | Loss Monitor #7 - Spare | E:LM5C7 | [7 empty] | Gianni Tassotto Marv Olson
3-10 | Loss Monitor #8 - Spare | E:LM5C8 | [7 empty] | Gianni Tassotto Marv Olson
3-11 | Loss Monitor #9 - Spare | E:LM5C9 | [7 empty] | Gianni Tassotto Marv Olson
3-12 | Loss Monitor #10 - Spare | E:LM5C10 | [7 empty] | Gianni Tassotto Marv Olson
3-13 | Loss Monitor #11 - Spare | E:LM5C11 | [7 empty] | Gianni Tassotto Marv Olson
3-14 | Loss Monitor #12 - Spare | E:LM5C12 | [7 empty] | Gianni Tassotto Marv Olson
4 | Pre-Target Beam Position Monitor - X and Y Plus Intensity | E:NOTCHP | Custom | 3 |  |  |  |  | Electronics Independent of Beamline BPM Systems | Jim Hylen Rich Talaga
5 | Baffle and Target Instrumentation | [8 empty] | Jim Hylen Rich Talaga
5-1 | Baffle Thermocouples (2 + Spare) | E:BTHTnn | Custom | 3 |  |  | 2A |  | Electronics Independent of PLC | Jim Hylen Rich Talaga
5-2 | Baffle/Target Carrier Thermocouples | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 2 Channels | Jim Hylen Rich Talaga
5-3 | Target Thermocouple | E:BTHTnn | PLC Ethernet |  |  |  | 1A |  | Details of Signal Origin Not Known | Jim Hylen Rich Talaga
5-4 | Target Budal Monitor for X |  | Custom | 1 |  |  | No |  | Monitor Not Suitable to PLC (?) | Jim Hylen Rich Talaga
5-5 | Target Budal Monitor for Y |  | Custom | 1 |  |  | No |  | Monitor Not Suitable to PLC (?) | Jim Hylen Rich Talaga
5-6 | Target to Ground Impedance |  | Custom (?) | 1 |  |  | No |  | Monitor Not Suitable to PLC (?) | Jim Hylen Rich Talaga
5-7 | Target Vacuum Pirani Gauge | E:BTHVnn | PLC Ethrnt or Custom | 1 ? |  |  | No |  | Details of Signal Origin Not Known | Jim Hylen Rich Talaga
5-8 | Target Helium Pressure Gauge | E:BTHPnn | PLC Ethrnt or Custom | 1 ? |  |  | No |  | Details of Signal Origin Not Known | Jim Hylen Rich Talaga
6 | Horn and Horn Stripline Iinstrumentation | [8 empty] | Jim Hylen Rich Talaga
6-1 | Horn 1 Magnetic Field Monitors B-Dot Coils |  | Custom | 9 |  |  | No |  | Associated Sample & Hold? | Jim Hylen Rich Talaga
6-2 | Horn 2 Magnetic Field Monitors B-Dot Coils |  | Custom | 9 |  |  | No |  | Associated Sample & Hold? | Jim Hylen Rich Talaga
6-3 | Horn 1 Module Support Thermocouples | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 4 Channels | Jim Hylen Rich Talaga
6-4 | Horn 2 Module Support Thermocouples | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 4 Channels | Jim Hylen Rich Talaga
6-5 | Horn 1 Carriage Thermocouples | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 2 Channels | Jim Hylen Rich Talaga
6-6 | Horn 2 Carriage Thermocouples | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 2 Channels | Jim Hylen Rich Talaga
6-7 | Horn 1 Body Thermocouples | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 6 Channels | Jim Hylen Rich Talaga
6-8 | Horn 2 Body Thermocouples | E:BTHTnn | PLC Ethernet |  |  |  | No |  | 6 Channels | Jim Hylen Rich Talaga
7 | Decay Pipe Vacuum Controls |  | PLC Ethernet |  |  |  | 1D |  | Controls Also at Downstream End by Absorber. | Dave Pushka
7-1 | Various Control and Monitor Points | E:DPVinn | PLC Ethrnt | [5 empty] | Detailed Separately | Dave Pushka
8 | Target and Baffle RAW System |  | PLC Ethernet |  |  |  | 1D |  |  | Dave Pushka
8-1 | Various Control and Monitor Points | E:TBRinn | PLC Ethrnt | [5 empty] | Detailed Separately | Dave Pushka
9 | Horn 1 RAW System |  | PLC Ethernet |  |  |  | 1D |  |  | Dave Pushka
9-1 | Various Control and Monitor Points | E:H1Rinn | PLC Ethrnt | [5 empty] | Detailed Separately | Dave Pushka
10 | Horn 2 RAW System |  | PLC Ethernet |  |  |  | 1D |  |  | Dave Pushka
10-1 | Various Control and Monitor Points | E:H2Rinn | PLC Ethrnt | [5 empty] | Detailed Separately | Dave Pushka
11 | Intermediate Water Cooling for Horn 1 and Horn 2 RAW Systems |  | PLC Ethernet |  |  |  | 1D |  |  | Dave Pushka
11-1 | Various Control and Monitor Points | E:HHIinn | PLC Ethrnt | [5 empty] | Detailed Separately | Dave Pushka
12 | Decay Pipe Cooling RAW System - Upstream End |  | PLC Ethernet |  |  |  | 1D |  |  | Dave Pushka
12-1 | Various Control and Monitor Points | E:DURinn | PLC Ethrnt | [5 empty] | Detailed Separately | Dave Pushka
13 | Target Pile Air Cooling System |  | PLC Ethernet |  |  |  | 1D |  | Primary Components Include a Chiller, Reheater, Fan and Filters. Various Monitor Points of Temperature, Pressure and Humidity. | Andy Stefanik
13-1 | Various Control and Monitor Points | E:TPCinn | PLC Ethrnt | [5 empty] | Detailed Separately | Andy Stefanik
13-2 | Fan Differential Pressure | E:TPCPnn | Custom | 1 |  |  | 1A |  | Electronics Independent of PLC | Jim Hylen Rich Talaga
13-3 | Target Pile Air Supply Temperature | E:TPCTnn | Custom | 1 |  |  | 1A |  | Electronics Independent of PLC | Jim Hylen Rich Talaga
14 | Target Positioning System |  | ARCNET VME Ethrnt |  |  |  | No |  | 5 Motors and Similar to AP0 | Al Legan Kris Anderson
15 | Positioning System for Horn #1 |  | ARCNET VME Ethrnt |  |  |  | No |  | 4 Motors and Similar to AP0 | Al Legan Kris Anderson
16 | TCLK Timing Capability |  | 178 + 377 | [5 empty] | Horn Timing and Also for Local Instrumentation | Ken Bourkland Bob Ducar
17 | MIBS Timing Capability (Ref $74) |  | 479 | [5 empty] | Horn Timing and Also for Local Instrumentation | Ken Bourkland Bob Ducar
18 | MADC Facility |  | 290 | [5 empty] | 14 Bit Resolution Required Here. If a Second MADC is Required, 12 Bit Should be OK. | KC Seino Rupe Crouch
19 | NuMI Beam Permit |  | 200 | [5 empty] | Qty 1 Probably Sufficient. | Greg Vogel Bob Ducar
20 | Beam Permit Process Channel Interface and Controller |  | 204 |  |  |  | 1D |  | Output to Local 200 Beam Permit Module. | Al Franck Bob Ducar
21 | Ethernet Connectivity | [7 empty] | Needed for Interface of Local Electronics and Console | Dan Stenman
22 | VME with Connection to Ethernet | [7 empty] | Needed for Interface of Local Electronics | Dan Stenman
23 | ACNET Console X Terminal | [7 empty] | Thought to Reside Here Permanently. Definitely Necessary During Commissioning. | Dan Stenman
MINOS Service Building (West of Lederman Science Center) "MSB" |  |  | Beneficial Occupancy December 2003 | [5 empty] | Little Controls Infrastructure is Required Here in Mechanical Areas. Main Purpose is to Provide Repeater Stations for Necessary Signals Linking Controls Infrastructure. Basic Control and Monitoring Anticipated, But Nothing Especially Complex.
1 | TCLK Timing Capability |  | 178 | [5 empty] | Not Thought Necessary for Equipment, But Useful for Diagnostics. | Greg Vogel Bob Ducar
2 | Digital In - Digital Out Facility |  | 184 | [5 empty] | Potential for Control and Monitor of Local Systems | Greg Vogel Bob Ducar
3 | NuMI Beam Permit Origin Module |  | 201 | [5 empty] | Most Distant Location for the Extraction Kicker. Close the Loop With TCLK $A6. | Greg Vogel Bob Ducar
4 | NuMI Beam Permit |  | 200 |  |  |  | None |  | Useful for Diagnostics if Checking Return of Permit Signal from Absorber Area. | Greg Vogel Bob Ducar
5 | Ethernet Connectivity | [7 empty] | Thought Necessary Because of Distances Involved | Dan Stenman
MINOS Near Detector Hall (350 Ft Below MINOS Service Bldg) "MND" |  |  | Beneficial Occupancy December 2003 | [5 empty] | New Controls Infrastructure Required Here Linked by Fiber to Above MINOS Building. Link from here to Absorber Access Tunnel. Fiber Connectivity to Feynman Supported on Controls Singlemode Fibers.
1 | Detector Magnet Power Supply |  | 218 ? |  |  |  | No |  | PEI 150-5 with a Reversing Switch. Expected to Run DC. | Cat James
2 | MINOS LCW System |  | PLC Ethernet |  |  |  | No |  | Includes Analysis Magnet and Its Power Supply and Detector Electronics Rack Cooling. Also Controlling Heat Exchangers Using Clean and Cold Sump Water. | Dave Pushka
2-1 | Various Control and Monitor Points | E:MNWinn | PLC Ethrnt | [5 empty] | Detailed Separately | Dave Pushka
3 | Area Temperature & Humidity Sensors | [5 empty] | No |  | Likely to be Instrumented Thru Above Local PLC | Cat James
4 | TCLK Capability |  | 178 + 377 | [5 empty] | Diagnostics and Other Potential Utility | Greg Vogel Bob Ducar
5 | MIBS Timing Capability (Ref $74) |  | 479 | [5 empty] | May Need 53 MHz for Clocking | Cat James Vogel/Ducar
6 | Digital In - Digital Out Facility |  | 184 | [5 empty] | Potential for Control and Monitor of Local Systems in Lieu of Local PLC | Greg Vogel Bob Ducar
7 | MADC Facility |  | 290 | [5 empty] | 12 Bit Resolution Should be OK Here. May Eliminated in Lieu of Local PLC. | KC Seino Rupe Crouch
8 | NuMI Beam Permit |  | 200 |  |  |  | None |  | Status of Permit Loop and Diagnostics Afforded. No Inputs Planned Here. | Greg Vogel Bob Ducar
9 | Ethernet Connectivity | [8 empty] | Dan Stenman
Absorber Access Tunnel (Near Absorber at End of Decay Pipe) "AAT" |  |  | Beneficial Occupancy December 2003 | [5 empty] | New Controls Infrastructure Required Here Linked by Fiber to MINOS Near Detector - About 700 Feet Away.
1 | High Voltage Supply for Hadron Monitor |  | PLC Ethernet |  |  |  | No |  | Monitor and Control Likely Via Local PLC | Debbie Harris Sacha Kopp
2 | High Voltage Supply for Muon Monitor in Alcove 1. Quantity 3. |  | PLC Ethernet |  |  |  | No |  | Monitor and Control Likely Via Local PLC | Debbie Harris Sacha Kopp
3 | High Voltage Supply for Muon Monitor in Alcove 2. Quantity 3. |  | PLC Ethernet |  |  |  | No |  | Monitor and Control Likely Via Local PLC | Debbie Harris Sacha Kopp
4 | High Voltage Supply for Muon Monitor in Alcove 3. Quantity 3. |  | PLC Ethernet |  |  |  | No |  | Monitor and Control Likely Via Local PLC | Debbie Harris Sacha Kopp
5 | Hadron Monitor Instrumentation |  | ARCNET VME Ethrnt |  |  |  | No |  | Detectors Installed Between Decay Pipe End and Absorber. Using Multiwire Hardware for Readout. | Debbie Harris Sacha Kopp
6 | Muon Monitor Instrumentation for Alcove 1 |  | ARCNET VME Ethrnt |  |  |  | No |  | Detectors Installed at Muon Alcove 1. Using Multiwire Hardware for Readout. | Debbie Harris Sacha Kopp
7 | Muon Monitor Instrumentation for Alcove 2 |  | ARCNET VME Ethrnt |  |  |  | No |  | Detectors Installed at Muon Alcove 2. Using Multiwire Hardware for Readout. | Debbie Harris Sacha Kopp
8 | Muon Monitor Instrumentation for Alcove 3 |  | ARCNET VME Ethrnt |  |  |  | No |  | Detectors Installed at Muon Alcove 3. Using Multiwire Hardware for Readout. | Debbie Harris Sacha Kopp
9 | Absorber Instrumentation | [5 empty] | 1D |  | Mostly Thermocouples and Humidity Sensors | Ernie Villegas
9-1 | Various Control and Monitor Points | E:ABSinn | PLC Ethrnt | [5 empty] | Mostly Thermocouples. Detailed Separately. | Ernie Villegas
10 | Decay Pipe Vacuum System | [5 empty] | 1D |  | Controls Also at Upstream End. | Dave Pushka
10-1 | Various Control and Monitor Points | E:DPVinn | PLC Ethrnt | [5 empty] | Detailed Separately | Dave Pushka
11 | Absorber Cooling RAW System | [5 empty] | 1D |  |  | Dave Pushka
11-1 | Various Control and Monitor Points | E:ABRinn | PLC Ethrnt | [5 empty] | Detailed Separately | Dave Pushka
12 | Intermediate Water Cooling for Absorber RAW System | [5 empty] | No |  |  | Dave Pushka
12-1 | Various Control and Monitor Points | E:ABIinn | PLC Ethrnt | [5 empty] | Detailed Separately | Dave Pushka
13 | Decay Pipe Cooling RAW System - Downstream End | [5 empty] | 1D |  |  | Dave Pushka
13-1 | Various Control and Monitor Points | E:DDRinn | PLC Ethrnt | [5 empty] | Detailed Separately | Dave Pushka
14 | TCLK Capability |  | 178 | [5 empty] | Needs Not Specific at this Time But Useful for Diagnostics. | Greg Vogel Bob Ducar
15 | MIBS Timing Capability (Ref $74) |  | 479 | [5 empty] | Thought Necessary for Hadron and Muon Monitor Instrumentation. | Debbie Harris Sacha Kopp
16 | NuMI Beam Permit |  | 200 | [6 empty] | Greg Vogel Bob Ducar
17 | Ethernet Connectivity | [7 empty] | Needed for Interface of Console and Possibly for Local Electronics | Dan Stenman
18 | VME with Connection to Ethernet | [7 empty] | May be Needed for Interface of Local Electronics - Especially Detector Instrumentation | Dan Stenman
19 | ACNET Console X Terminal | [7 empty] | May Not Reside Here Permanently But Thought Convenient During Commissioning | Dan Stenman
MADC Utility is Expected to Be 14 Bit Resolution Unless Otherwise Noted
* Power Supply Analog Monitors Include: Current Reference, Current Out, Voltage Out, and Current Error.
** Power Supply Analog Monitors Include: Current Reference, Current Out, Voltage Out, Current Error, + Voltage to Ground, and - Voltage to Ground.
TWINAX CONVENTION Cable End: Pin is Plus, Socket is Minus. Analog Entry Box Bulkhead: Socket is Plus, Pin is Minus.

## Controls Summary
SUMMARY OF CONTROLS HARDWIRE REQUIREMENTS
LOCATION | 178 | 184 | 200 | 201 | 204 & PCI | 218 | 278 | 290 | 333 | 377 | 453 | 466 | 468 | 479 | 12 Bit MADC | 14 Bit MADC | SWIC SCANNER | CIA | PLC | NEW CAMAC CRATE | NIM BIN | VME | NEW CONSOLE | EQUIP RACKS
60S |  | 1 | 1 |  | 1 |  |  | 1 | 1 | 1 |  | 1 |  |  |  | 1
60N |  |  | 2 |  | 2 |  |  | 1 or 2 |  |  | 3 | 7 | 4 |  | 1 ? | 1 | 3 or 5 |  |  |  | 1 ? | 1
62SB |  |  | 2 |  | 2 | [6 empty] | 6 | 1 | 1 ? | 1 | 1 | 2 or None | 1 | 1 |  | 1 ? | 1
65SB | 1 |  | 1 |  | 1 |  |  | 2 |  | 1 | 3 | 10 | 1 | 1 ? | 1 | 1 | 5 |  |  | 1 | 1 ? | 1 | 1 | 8 ?
THSR |  |  | 2 |  | 1 |  |  | 2 |  |  |  |  | 2 | 1 | 1 | 1 |  |  | 1 | 1 |  |  | 1 | 9 ?
MSB | 1 | 1 ? | 1 | 1 | [15 empty] | 1 |  |  | No | 2
MND | 1 | 1 ? | 1 |  |  | 1? |  | 1 ? |  | 1 |  |  |  | 1 | 1 ? |  |  |  | 1 | 1 |  |  | Otherwise Available | 2
AAT | 1 |  | 1 | [10 empty] | 1 |  |  | 4 |  | 1 | 1 | 2 or 3 | 1 | 1 | 6
Totals | 4 | 1 to 3 | 11 | 1 | 7 | 1 ? | 0 | 6 to 8 | 1 | 3 | 6 | 24 | 8 | 3 to 5 | 3 to 5 | 5 | 15 | 1 | 4 | 5 | 2 to 6 | 4 | 3 | 27 ?
FIRUS by Al Legan and Co.
Target and Horn Motion Control by Al Legan and Co.
Some Hardware Already Installed at 60S, 60N and 62SB.

## General PLC Conventions
NuMI PLC Systems
Summary of Instrumentation and Control Signals
Proposal for ACNET Database Names and Device Descriptions
General Name | System Description | Instrumentation Types
E:62W i nn | MI-62 LCW System | Character i = | Description
E:62P i nn | Pond Water Cooling for MI-62 LCW System (PV-9) | F | Flow
E:BTHinn | Baffle, Target and Horn Instrumentation | H | Humidity
E:TBR i nn | Target & Baffle RAW System | I | Current
E:H1R i nn | Horn 1 RAW System | L | Liquid Level
E:H2R i nn | Horn 2 RAW System | P | Pressure
E:HHI i nn | Intermediate Water Cooling for Horn 1 and Horn 2 RAW Systems | R | Resistivity
E:DUR i nn | Decay Pipe Cooling RAW System - Upstream | S | Motor or Actuator
E:TPCinn | Target Pile Air Cooling System | T | Temperature
E:ABSinn | Absorber Instrumentation | V | Valve
E:DPVinn | Decay Pipe Vacuum System | W | Three Way Control Valve
E:ABR i nn | Absorber Cooling RAW System | X | Position
E:ABI i nn | Intermediate Water Cooling for Absorber RAW System
E:DDR i nn | Decay Pipe Cooling RAW System - Downstream | Characters nn = | Description
E:MNW i nn | MINOS LCW System | 01 thru 99 Max | Number for a Given Type

## MI Encl Distances
Measured Distances in the MI Enclosure
Downstream from Q608 Quad | Reference Point | Upstream from Q624 Quad
-0.5 | MI-60 Equipment Gallery RF19 Penetration | 770.75
0 | Q608 Center | 770.25
0.5 | MI-60 Equipment Gallery RF18 Penetration | 769.75
3.25 | MI-60 Equipment Gallery RF17 Penetration | 767.25
4.25 | MI-60 Equipment Gallery RF16 Penetration | 766.25
50 | Downstream Wall of Q609 Alcove | 720.25
58 | Q609 Center | 712.25
77.75 | Barrier Gate | 692.5
99.92 | Q610 Center | 670.33
142.67 | Q611 Center | 627.58
185.5 | Q612 Center | 584.75
188.25 | Exit Door Center Line | 582
227.33 | Q613 Center | 542.92
244 | Dual LCW Headers From MI-62 Transition Over Aisle | 526.25
264.42 | Edge of Wall Dividing A150 Line and Main Injector | 505.83
285 | Q614 Center | 485.25
343 | Q615 Center | 427.25
359.17 | Edge of Wall Dividing NuMI Stub and Main Injector | 411.08
372.58 | Enclosure Takes a Step Change in Width | 397.67
385.17 | Q616 Center | 385.08
400.33 | 2nd Level of Dual 18 Inch Tray Moves 10 Feet Toward Stub | 369.92
427.92 | Q617 Center | 342.33
432.83 | Enclosure Takes a Step Change in Width | 337.42
436.67 | Center Line of Passage to NuMI Stub Access | 333.58
470.75 | Q618 Centerline | 299.5
504.92 | Center Line of Penetrations to NuMI Stub | 265.33
512.75 | Q619 Center | 257.5
513.5 | Center Line of Exhaust Pipe from NuMI Stub | 256.75
570.5 | Q620 Center | 199.75
583.33 | End of 2nd Level of Dual 18 Inch Cable Tray | 186.92
627.5 | Q621 Center | 142.75
685.42 | Q622 Center | 84.83
727.58 | Q623 Center | 42.67
744.83 | MI-62 Controls/Kicker Room K1 Penetration | 25.42
758.17 | MI-62 Controls/Kicker Room K12 Penetration | 12.08
762.42 | Upstream Wall of MI-62 Alcove | 7.83
763.25 | MI-62 Power Supply Room Penetrations 1 and 11 | 7
767.33 | Ceiling LCW Penetrations | 2.92
770.25 | Q624 Center | 0
771.33 | MI-62 Power Supply Room Penetrations 10 and 20 | -1.08
778.33 | Downstream Wall of MI-62 Alcove | -8.08