## 25F nomo
Raver-Echo Lake #1 500kV Line (Covington-Creston bypassed to Covington West Bus)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 033
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6644.3693
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 538.95 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1170 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 871.91 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1342.38 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1170 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1617.3 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 697.1 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2095.66 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1058.37 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2474.1 | N-1: Echo Lk-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1342.38 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 871.91 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 988.39 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1058.37 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1333.51 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1333.51 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1617.3 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1808.27 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1497.59 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2154.76 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1808.27 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 538.95 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2095.66 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 697.1 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1818.85 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 988.39 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2154.76 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1497.59 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2474.1 | N-1: Echo Lk-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1818.85 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Raver-Echo Lake #1 500kV Line (Covington-Creston bypassed to Covington West Bus)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 033
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6315.5767
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 784.57 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1432.17 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1118.72 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1593.68 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1432.17 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1803.79 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 888.57 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2275.36 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1267.88 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2717.47 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1593.68 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1118.72 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1166.24 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1267.88 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1483.13 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1483.13 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1803.79 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1956.17 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1648.53 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2407.87 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1956.17 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 784.57 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2275.36 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 888.57 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2054.99 | N-1: Echo Lk-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1166.24 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2407.87 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1648.53 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2717.47 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2054.99 | N-1: Echo Lk-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Raver-Echo Lake #1 500kV Line (Covington-Creston bypassed to Covington West Bus)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 033
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6035.726
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 914.05 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1600.36 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1247.35 | N-1: Echo Lk-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1721.48 | N-1: Echo Lk-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1600.36 | N-1: Schultz-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1993.61 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1058.16 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2473.32 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1404.12 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2880.45 | N-1: Echo Lk-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1721.48 | N-1: Echo Lk-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1247.35 | N-1: Echo Lk-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1366.88 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1404.12 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1706.62 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1706.62 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1993.61 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2158.22 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1839.05 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2588.5 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2158.22 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 914.05 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2473.32 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1058.16 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2234.25 | N-1: Echo Lk-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1366.88 | N-1: Shultz-Echo Lake 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2588.5 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1839.05 | BFR: 5078 Shultz-Echo Lake 500kV | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2880.45 | N-1: Echo Lk-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2234.25 | N-1: Echo Lk-Kangley Tap 500kV line | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Raver-Echo Lake #1 500kV Line (Covington-Creston bypassed to Covington West Bus)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 033
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4970.6367
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1812.96 | N-1: Shultz-Echo Lake 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2460.12 | N-1: Echo Lk-Kangley Tap 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2146.06 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2618.07 | N-1: Echo Lk-Kangley Tap 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2460.12 | N-1: Echo Lk-Kangley Tap 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2934.39 | N-1: Schultz-Kangley Tap 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1982 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3314.55 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV]
260 | 460 | 2304.05 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1765.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2618.07 | N-1: Echo Lk-Kangley Tap 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 2146.06 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2243.08 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2304.05 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2592.28 | N-1: Shultz-Echo Lake 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2592.28 | N-1: Shultz-Echo Lake 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2934.39 | N-1: Schultz-Kangley Tap 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3073.83 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2761.31 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1863.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3073.83 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1812.96 | N-1: Shultz-Echo Lake 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3314.55 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1982 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1965.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2243.08 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1863.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2761.31 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1765.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1965.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Raver-Echo Lake #1 500kV Line (Covington-Creston bypassed to Covington West Bus)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 033
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4635.84
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2020.46 | N-1: Shultz-Echo Lake 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2628.95 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2350.71 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2577.63 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2628.95 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2784.97 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2202.72 | N-1: Shultz-Echo Lake 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3087.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2509.69 | N-1: Shultz-Echo Lake 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1586.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2577.63 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2350.71 | BFR: 5078 Shultz-Echo Lake 500kV | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2495.38 | N-1: Echo Lk-Kangley Tap 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2509.69 | N-1: Shultz-Echo Lake 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2769.47 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2769.47 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2784.97 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3071.45 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 2938.71 | N-1: Shultz-Echo Lake 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1676.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3071.45 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2020.46 | N-1: Shultz-Echo Lake 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3087.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2202.72 | N-1: Shultz-Echo Lake 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1777.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2495.38 | N-1: Echo Lk-Kangley Tap 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1676.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2938.71 | N-1: Shultz-Echo Lake 500kV line | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1586.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1777.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Raver-Echo Lake #1 500kV Line (Covington-Creston bypassed to Covington West Bus)
G0 | 538.95 | 784.57 | 914.05 | 1812.96 | 2020.46
G1 | 871.91 | 1118.72 | 1247.35 | 2146.06 | 2350.71 | Season/Year: | WINTER 2009
G2 | 1170 | 1432.17 | 1600.36 | 2460.12 | 2628.95 | Direction: | South-to-North (SN)
G3 | 697.1 | 888.57 | 1058.16 | 1982 | 2202.72 | Case Loads: | Heavy Loads
G4 | 1058.37 | 1267.88 | 1404.12 | 2304.05 | 2509.69 | Outage: | 033
G5 | 1342.38 | 1593.68 | 1721.48 | 2618.07 | 2577.63 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 988.39 | 1166.24 | 1366.88 | 2243.08 | 2495.38 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 1333.51 | 1483.13 | 1706.62 | 2592.28 | 2769.47 | Study Person: | FRP9899
G8 | 1617.3 | 1803.79 | 1993.61 | 2934.39 | 2784.97 | Source: | 033WINTER09v1SNH
G9 | 1497.59 | 1648.53 | 1839.05 | 2761.31 | 2938.71
G10 | 1808.27 | 1956.17 | 2158.22 | 3073.83 | 3071.45
G11 | 2095.66 | 2275.36 | 2473.32 | 3314.55 | 3087.42
G12 | 1818.85 | 2054.99 | 2234.25 | 1965.17 | 1777.59
G13 | 2154.76 | 2407.87 | 2588.5 | 1863.27 | 1676.99
G14 | 2474.1 | 2717.47 | 2880.45 | 1765.95 | 1586.92
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 033 | Raver-Echo Lake #1 500kV Line (Covington-Creston bypassed to Covington West Bus)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6644.3693 | 538.95 | 871.91 | 1170 | 697.1 | 1058.37 | 1342.38 | 988.39 | 1333.51 | 1617.3 | 1497.59 | 1808.27 | 2095.66 | 1818.85 | 2154.76 | 2474.1
35F | 6315.5767 | 784.57 | 1118.72 | 1432.17 | 888.57 | 1267.88 | 1593.68 | 1166.24 | 1483.13 | 1803.79 | 1648.53 | 1956.17 | 2275.36 | 2054.99 | 2407.87 | 2717.47
45F | 6035.726 | 914.05 | 1247.35 | 1600.36 | 1058.16 | 1404.12 | 1721.48 | 1366.88 | 1706.62 | 1993.61 | 1839.05 | 2158.22 | 2473.32 | 2234.25 | 2588.5 | 2880.45
60F | 4970.6367 | 1812.96 | 2146.06 | 2460.12 | 1982 | 2304.05 | 2618.07 | 2243.08 | 2592.28 | 2934.39 | 2761.31 | 3073.83 | 3314.55 | 1965.17 | 1863.27 | 1765.95
70F | 4635.84 | 2020.46 | 2350.71 | 2628.95 | 2202.72 | 2509.69 | 2577.63 | 2495.38 | 2769.47 | 2784.97 | 2938.71 | 3071.45 | 3087.42 | 1777.59 | 1676.99 | 1586.92

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 538.22 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 509.38 | 509.26 | 6675.28 | 538.95 | -375.42 | FULL
G1 | 871.38 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 509.16 | 509.35 | 6612.75 | 871.91 | -531.25 | FULL
G2 | 1508.86 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.53 | 530.86 | 530.83 | 6641.8 | 1170 | -851.11 | CTG_FAIL_IN_FULL
G3 | 696.67 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 509.45 | 509.67 | 6674.64 | 697.1 | -395.65 | FULL
G4 | 1057.93 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 510.24 | 510.12 | 6612.39 | 1058.37 | -570.43 | FULL
G5 | 1342.04 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 509.27 | 509.17 | 6632.28 | 1342.38 | -693.47 | FULL
G6 | 988.23 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 510.43 | 510.54 | 6675.17 | 988.39 | -438.31 | FULL
G7 | 1333.37 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 510.68 | 510.87 | 6612.81 | 1333.51 | -607.25 | FULL
G8 | 1616.76 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 510.33 | 510.51 | 6633.48 | 1617.3 | -747.4 | FULL
G9 | 1497.56 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 511.73 | 511.55 | 6680.89 | 1497.59 | -525.76 | FULL
G10 | 1808.05 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 510.86 | 510.98 | 6618.64 | 1808.27 | -671.44 | FULL
G11 | 2096.15 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 510.93 | 510.73 | 6639.42 | 2095.66 | -813.79 | FULL
G12 | 1818.99 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 506.91 | 507.06 | 6685.71 | 1818.85 | -558.51 | FULL
G13 | 2154.85 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 507.82 | 508.01 | 6624.81 | 2154.76 | -719.17 | FULL
G14 | 2473.95 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Echo Lk-Kangley Tap 500kV line | 7.64 | 507.67 | 507.51 | 6645.47 | 2474.1 | -869.73 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 784.18 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 495.89 | 495.74 | 6346.13 | 784.57 | -477.09 | FULL
G1 | 1118.38 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 495.8 | 495.68 | 6284.9 | 1118.72 | -633.27 | FULL
G2 | 1431.61 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 496.78 | 496.65 | 6305.87 | 1432.17 | -781.63 | FULL
G3 | 888.22 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 7.64 | 491.93 | 492.09 | 6344 | 888.57 | -474.17 | FULL
G4 | 1267.39 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 495.66 | 495.79 | 6283.98 | 1267.88 | -657.36 | FULL
G5 | 1593.25 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 495.94 | 496.14 | 6305.36 | 1593.68 | -812.54 | FULL
G6 | 1166.06 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 492.63 | 492.75 | 6344.94 | 1166.24 | -514.15 | FULL
G7 | 1482.68 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 491.93 | 492.09 | 6283.56 | 1483.13 | -662.49 | FULL
G8 | 1803.17 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 491.88 | 492.03 | 6304.51 | 1803.79 | -815.65 | FULL
G9 | 1648.57 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 492.86 | 492.96 | 6351.36 | 1648.53 | -581.58 | FULL
G10 | 1955.52 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 492.34 | 492.49 | 6290.17 | 1956.17 | -725.84 | FULL
G11 | 2275.07 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 492 | 491.86 | 6311.48 | 2275.36 | -878.28 | FULL
G12 | 2055.14 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Echo Lk-Kangley Tap 500kV line | 7.64 | 493.3 | 493.09 | 6358.51 | 2054.99 | -659.15 | FULL
G13 | 2408.22 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 7.64 | 494.3 | 494.1 | 6298.42 | 2407.87 | -826.14 | FULL
G14 | 2717.91 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 7.64 | 493.99 | 493.88 | 6320.46 | 2717.47 | -978.5 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 913.79 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 480.2 | 480.4 | 6064.01 | 914.05 | -537.29 | FULL
G1 | 1247.07 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Echo Lk-Kangley Tap 500kV line | 7.64 | 480.34 | 480.51 | 6003.36 | 1247.35 | -692.33 | FULL
G2 | 1600.41 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 7.64 | 483.6 | 483.72 | 6026.78 | 1600.36 | -853.93 | FULL
G3 | 1057.82 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 480.26 | 480.37 | 6063.83 | 1058.16 | -551.53 | FULL
G4 | 1403.8 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 7.64 | 480.47 | 480.69 | 6003.4 | 1404.12 | -710.62 | FULL
G5 | 1720.93 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Echo Lk-Kangley Tap 500kV line | 7.64 | 480.32 | 480.53 | 6024.56 | 1721.48 | -868.29 | FULL
G6 | 1366.79 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 7.64 | 481.51 | 481.62 | 6065.03 | 1366.88 | -611.63 | FULL
G7 | 1706.22 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 7.64 | 481.91 | 481.77 | 6004.68 | 1706.62 | -767.99 | FULL
G8 | 1992.77 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 7.64 | 480.67 | 480.83 | 6025.81 | 1993.61 | -903.72 | FULL
G9 | 1838.82 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 481.86 | 481.75 | 6072.12 | 1839.05 | -674.59 | FULL
G10 | 2157.4 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 481.57 | 481.37 | 6011.59 | 2158.22 | -824.17 | FULL
G11 | 2472.92 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 481.39 | 481.17 | 6033.76 | 2473.32 | -975.55 | FULL
G12 | 2233.97 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Echo Lk-Kangley Tap 500kV line | 7.64 | 481.79 | 481.95 | 6079.94 | 2234.25 | -747.52 | FULL
G13 | 2588.87 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 7.64 | 482.55 | 482.41 | 6019.78 | 2588.5 | -915.52 | FULL
G14 | 2880.93 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-1: Echo Lk-Kangley Tap 500kV line | 7.64 | 482.16 | 482.3 | 6037.24 | 2880.45 | -1048.87 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1812.99 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 18.1 | 973.99 | 974.51 | 5004.85 | 1812.96 | -933.08 | FULL
G1 | 2146.3 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 18.1 | 975.56 | 975.1 | 4947.28 | 2146.06 | -1091.03 | FULL
G2 | 2458.29 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | N-1: Echo Lk-Kangley Tap 500kV line | 18.1 | 977.65 | 977.84 | 4973.79 | 2460.12 | -1234.86 | FULL
G3 | 1982.76 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 18.1 | 975.97 | 975.76 | 5006 | 1982 | -964.21 | FULL
G4 | 2304.88 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 18.1 | 976.06 | 975.82 | 4948.72 | 2304.05 | -1113.26 | FULL
G5 | 2617.92 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | N-1: Echo Lk-Kangley Tap 500kV line | 18.1 | 979.41 | 979.14 | 4973.45 | 2618.07 | -1272.46 | FULL
G6 | 2243.36 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 18.1 | 975.21 | 975.75 | 5007.91 | 2243.08 | -999.2 | FULL
G7 | 2590.33 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 18.1 | 979.03 | 979.54 | 4950.94 | 2592.28 | -1170.48 | FULL
G8 | 2934.92 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | N-1: Schultz-Kangley Tap 500kV line | 18.1 | 988.65 | 988.95 | 4976.14 | 2934.39 | -1332.52 | FULL
G9 | 2761.78 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 18.1 | 980.96 | 981.24 | 5016.77 | 2761.31 | -1088.39 | FULL
G10 | 3075.92 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 18.1 | 980.57 | 980.98 | 4960.1 | 3073.83 | -1237.69 | FULL
G11 | 3317.03 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | -100 | -3286.85 | -3287.41 | 4977.35 | 3314.55 | -1347.47 | FULL
G12 | 1965.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.77 | -424.4 | -424.33 | 4982.41 | 1965.17 | -525.57 | FULL
G13 | 1863.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.77 | -423 | -422.99 | 4911.42 | 1863.27 | -452.21 | FULL
G14 | 1765.87 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.77 | -422.02 | -421.95 | 4922.42 | 1765.95 | -380.76 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2020.04 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 18.1 | 947.16 | 947.65 | 4675.63 | 2020.46 | -1022.73 | FULL
G1 | 2350.84 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | BFR: 5078 Shultz-Echo Lake 500kV | 18.1 | 945.55 | 945.92 | 4617.85 | 2350.71 | -1179.11 | FULL
G2 | 2629.4 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.71 | 451.32 | 451.66 | 4637.21 | 2628.95 | -1315.34 | FULL
G3 | 2202.85 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 18.1 | 947.04 | 947.22 | 4675.79 | 2202.72 | -1062.04 | FULL
G4 | 2510.41 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 18.1 | 948.6 | 948.92 | 4620.67 | 2509.69 | -1207.55 | FULL
G5 | 2579.88 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.07 | -2148.33 | -2150.08 | 4632.55 | 2577.63 | -1223.11 | FULL
G6 | 2495.78 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | N-1: Echo Lk-Kangley Tap 500kV line | 18.1 | 951.34 | 951.57 | 4678.44 | 2495.38 | -1113.42 | FULL
G7 | 2769.76 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.07 | -2161 | -2159.9 | 4621 | 2769.47 | -1245.78 | FULL
G8 | 2786.73 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.07 | -2161.85 | -2162.52 | 4631.37 | 2784.97 | -1234.35 | FULL
G9 | 2936.77 | Branch CHRISTOP (42505) TO OBRIEN (42503) CKT 1 [230.00 - 230.00 kV] | N-1: Shultz-Echo Lake 500kV line | 18.1 | 950.48 | 950.73 | 4687.74 | 2938.71 | -1168.85 | FULL
G10 | 3071.88 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.07 | -2153.17 | -2151.34 | 4622.26 | 3071.45 | -1220.25 | FULL
G11 | 3090.09 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.07 | -2154.26 | -2152.51 | 4633.6 | 3087.42 | -1209.38 | FULL
G12 | 1777.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.77 | -425.1 | -425.06 | 4643.4 | 1777.59 | -406.83 | FULL
G13 | 1676.75 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.77 | -424.31 | -424.26 | 4573.5 | 1676.99 | -334.32 | FULL
G14 | 1586.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.77 | -423.63 | -423.59 | 4586.59 | 1586.92 | -267.47 | FULL
033WINTER09v1SNH