## 25F nomo
Tacoma-Raver #1&2 500kV Line, Monroe 500kV PCB 4672, Raver 500kV PCB 4305 & Bellingham 230/115kV Bank #1 O/S
Winter 2008
South-to-North (SN)
Light Loads
Outage: |  | 574R1
Temp: |  | 25 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 3331.4513
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3096.14 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 650 | 3022.53 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3131.09 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 650 | 3206.74 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3022.53 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 650 | 3472.57 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 3228.5 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 650 | 3006.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3236.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 650 | 1085.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3206.74 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 380 | 3131.09 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3427.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 380 | 3236.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3455.36 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 380 | 3455.36 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3472.57 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 380 | 2991.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 3126.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 380 | 1162.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2991.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 100 | 3096.14 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3006.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 100 | 3228.5 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 1204.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 100 | 3427.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1162.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 100 | 3126.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 1085.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 100 | 1204.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Tacoma-Raver #1&2 500kV Line, Monroe 500kV PCB 4672, Raver 500kV PCB 4305 & Bellingham 230/115kV Bank #1 O/S
Winter 2008
South-to-North (SN)
Light Loads
Outage: |  | 574R1
Temp: |  | 35 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 2642.8133
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3124.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 650 | 2911.03 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3050.79 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 650 | 3123.13 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2911.03 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 650 | 3429.45 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3191.74 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 650 | 2280.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3222.12 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 650 | 295.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3123.13 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 380 | 3050.79 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 3411.14 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 380 | 3222.12 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3423.02 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 380 | 3423.02 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3429.45 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 380 | 2380.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2416.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 380 | 340.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2380.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 100 | 3124.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 2280.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 100 | 3191.74 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 426.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 100 | 3411.14 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 340.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 100 | 2416.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 295.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 100 | 426.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Tacoma-Raver #1&2 500kV Line, Monroe 500kV PCB 4672, Raver 500kV PCB 4305 & Bellingham 230/115kV Bank #1 O/S
Winter 2008
South-to-North (SN)
Light Loads
Outage: |  | 574R1
Temp: |  | 45 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 2399.516
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3057.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 650 | 2975.34 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3059.67 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 650 | 3105.61 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2975.34 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 650 | 3414.7 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 3129.96 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 650 | 1444.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3196.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 650 | -812.77 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3105.61 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 380 | 3059.67 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 3377.17 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 380 | 3196.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3362.26 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 380 | 3362.26 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3414.7 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 380 | 1538.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1653.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 380 | -842.48 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1538.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 100 | 3057.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1444.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 100 | 3129.96 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -799.6 | T-1: Bellingham 230/115kV Bank#2 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 100 | 3377.17 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -842.48 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 100 | 1653.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -812.77 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 100 | -799.6 | T-1: Bellingham 230/115kV Bank#2 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Tacoma-Raver #1&2 500kV Line, Monroe 500kV PCB 4672, Raver 500kV PCB 4305 & Bellingham 230/115kV Bank #1 O/S
Winter 2008
South-to-North (SN)
Light Loads
Outage: |  | 574R1
Temp: |  | 60 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 2921.9487
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2810.11 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 650 | 2876.36 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2828.56 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 650 | 2954.63 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2876.36 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 650 | 3176.17 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2926.62 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 650 | 1825.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2966.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 650 | -166.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2954.63 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 380 | 2828.56 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3138.18 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 380 | 2966.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3156.94 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 380 | 3156.94 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3176.17 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 380 | 1924.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2032.37 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 380 | -151.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1924.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 100 | 2810.11 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1825.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 100 | 2926.62 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -49.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 100 | 3138.18 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -151.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 100 | 2032.37 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -166.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 100 | -49.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Tacoma-Raver #1&2 500kV Line, Monroe 500kV PCB 4672, Raver 500kV PCB 4305 & Bellingham 230/115kV Bank #1 O/S
Winter 2008
South-to-North (SN)
Light Loads
Outage: |  | 574R1
Temp: |  | 70 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 3274.556
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2665.35 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 650 | 2729.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2682.12 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 650 | 2836.16 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2729.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 650 | 3026.7 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2792.9 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 650 | 1916.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2811.2 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 650 | -111.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2836.16 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 380 | 2682.12 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3001.51 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 380 | 2811.2 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3016.44 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 380 | 3016.44 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3026.7 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 380 | 2025.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2120.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 380 | -66.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2025.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 100 | 2665.35 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1916.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 100 | 2792.9 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 22.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 100 | 3001.51 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -66.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 100 | 2120.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -111.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 100 | 22.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Pink Table
South-to-North (SN) |  |  |  | Light Loads |  |  | 574R1 | Tacoma-Raver #1&2 500kV Line, Monroe 500kV PCB 4672, Raver 500kV PCB 4305 & Bellingham 230/115kV Bank #1 O/S
PSE Gen |  | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25 Fahrenheit | 3331.4513 | 3096.14 | 3131.09 | 3022.53 | 3228.5 | 3236.66 | 3206.74 | 3427.06 | 3455.36 | 3472.57 | 3126.01 | 2991.87 | 3006.54 | 1204.61 | 1162.12 | 1085.41
35 Fahrenheit | 2642.8133 | 3124.91 | 3050.79 | 2911.03 | 3191.74 | 3222.12 | 3123.13 | 3411.14 | 3423.02 | 3429.45 | 2416.76 | 2380.39 | 2280.32 | 426.64 | 340.71 | 295.25
45 Fahrenheit | 2399.516 | 3057.61 | 3059.67 | 2975.34 | 3129.96 | 3196.37 | 3105.61 | 3377.17 | 3362.26 | 3414.7 | 1653.43 | 1538.68 | 1444.79 | -799.6 | -842.48 | -812.77
60 Fahrenheit | 2921.9487 | 2810.11 | 2828.56 | 2876.36 | 2926.62 | 2966.03 | 2954.63 | 3138.18 | 3156.94 | 3176.17 | 2032.37 | 1924.24 | 1825.79 | -49.74 | -151.68 | -166.83
70 Fahrenheit | 3274.556 | 2665.35 | 2682.12 | 2729.32 | 2792.9 | 2811.2 | 2836.16 | 3001.51 | 3016.44 | 3026.7 | 2120.17 | 2025.69 | 1916.47 | 22.08 | -66.92 | -111.55

## Results
Description: |  | Tacoma-Raver #1&2 500kV Line, Monroe 500kV PCB 4672, Raver 500kV PCB 4305 & Bellingham 230/115kV Bank #1 O/S
Season/Year: |  | Winter 2008
Direction: |  | South-to-North (SN)
Case Loads: |  | Light Loads
Outage: |  | 574R1
Power World: |  | 13.0 (*.exe Date: 02/24/08)
File Location: |  | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2008\WINTER_2008
Study Person: |  | FRP9899
Temp: | 25 Fahrenheit |  | Average Puget Sound Net Area Load = 3331 MW
Gen. | Transfer | Worst | Limiting | PASTE RESULTS BELOW
Pattern | Limit | Contingency | Facility | 25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201)
1 | 3096.14 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G0 | 3096.31 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.01 | -2486.85 | -2487.02 | 3396.09 | 3096.14
2 | 3131.09 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G1 | 3129.39 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.01 | -2491.73 | -2490.68 | 3324.95 | 3131.09
3 | 3022.53 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G2 | 3021.54 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | 15.74 | 505.64 | 505.97 | 3332.52 | 3022.53
4 | 3228.5 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G3 | 3226.88 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.01 | -2500.65 | -2499.52 | 3396.49 | 3228.5
5 | 3236.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G4 | 3236.58 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2495.83 | -2497.1 | 3326.92 | 3236.66
6 | 3206.74 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G5 | 3207.45 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | 15.74 | 495.98 | 495.63 | 3335.4 | 3206.74
7 | 3427.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G6 | 3426.07 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2481.52 | -2483.35 | 3396.02 | 3427.06
8 | 3455.36 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G7 | 3454.79 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2493.51 | -2494.98 | 3326.84 | 3455.36
9 | 3472.57 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G8 | 3472.31 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2515.31 | -2514.52 | 3339.2 | 3472.57
10 | 3126.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G9 | 3125.38 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -466.59 | -466.46 | 3363.28 | 3126.01
11 | 2991.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G10 | 2991.06 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -465.5 | -465.37 | 3289.82 | 2991.87
12 | 3006.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G11 | 3006.52 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -472.05 | -472.01 | 3301.58 | 3006.54
13 | 1204.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G12 | 1203.96 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -468.6 | -468.62 | 3320.62 | 1204.61
14 | 1162.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G13 | 1162.99 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -472.33 | -472.38 | 3253.27 | 1162.12
15 | 1085.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G14 | 1086.48 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -473.75 | -473.8 | 3268.77 | 1085.41
Temp: | 35 Fahrenheit |  | Average Puget Sound Net Area Load = 2643 MW
Gen. | Transfer | Worst | Limiting
Pattern | Limit | Contingency | Facility | 35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201)
1 | 3124.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G0 | 3123.12 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2430.72 | -2429.2 | 2709.24 | 3124.91
2 | 3050.79 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G1 | 3051.84 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | 15.74 | 490.28 | 490.61 | 2633.61 | 3050.79
3 | 2911.03 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G2 | 2911.48 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | 15.74 | 492.15 | 491.85 | 2640.12 | 2911.03
4 | 3191.74 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G3 | 3190.11 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2358.5 | -2357 | 2708.6 | 3191.74
5 | 3222.12 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G4 | 3222.84 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2414.84 | -2413.43 | 2638.24 | 3222.12
6 | 3123.13 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G5 | 3123.1 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | 15.74 | 498.06 | 497.65 | 2644.87 | 3123.13
7 | 3411.14 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G6 | 3410.95 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2369.61 | -2370.9 | 2707.64 | 3411.14
8 | 3423.02 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G7 | 3422.53 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2372.46 | -2370.41 | 2639.11 | 3423.02
9 | 3429.45 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G8 | 3427.96 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | 15.74 | 492.67 | 492.21 | 2651.31 | 3429.45
10 | 2416.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G9 | 2416.26 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -458.75 | -458.69 | 2657.72 | 2416.76
11 | 2380.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G10 | 2381.05 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -463.71 | -463.58 | 2588.21 | 2380.39
12 | 2280.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G11 | 2281.01 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -462.71 | -462.58 | 2600.5 | 2280.32
13 | 426.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G12 | 427.59 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -458.05 | -457.97 | 2644.71 | 426.64
14 | 340.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G13 | 341.5 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -460.45 | -460.35 | 2580.75 | 340.71
15 | 295.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G14 | 296.51 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -462.77 | -462.75 | 2597.57 | 295.25
Temp: | 45 Fahrenheit |  | Average Puget Sound Net Area Load = 2400 MW
Gen. | Transfer | Worst | Limiting
Pattern | Limit | Contingency | Facility | 45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201)
1 | 3057.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G0 | 3058.16 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2376.74 | -2377.76 | 2460.99 | 3057.61
2 | 3059.67 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G1 | 3059.95 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | 15.74 | 476.56 | 476.22 | 2388.32 | 3059.67
3 | 2975.34 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G2 | 2974.58 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | 15.74 | 474.98 | 475.25 | 2396.23 | 2975.34
4 | 3129.96 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G3 | 3130.35 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2292.36 | -2291.14 | 2459.68 | 3129.96
5 | 3196.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G4 | 3195.64 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2385.12 | -2383.93 | 2392.38 | 3196.37
6 | 3105.61 | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G5 | 3105.74 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: 4522 EL-MON-SNK & CHJ-MON | 15.74 | 482.41 | 482.5 | 2400.11 | 3105.61
7 | 3377.17 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G6 | 3377.06 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2323.15 | -2323.66 | 2459.94 | 3377.17
8 | 3362.26 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G7 | 3361.35 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2304.94 | -2302.33 | 2391.31 | 3362.26
9 | 3414.7 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G8 | 3413.66 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2390.05 | -2391.22 | 2405.83 | 3414.7
10 | 1653.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G9 | 1653.25 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -430.59 | -430.77 | 2400.56 | 1653.43
11 | 1538.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G10 | 1539.04 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -430.13 | -430.17 | 2332.06 | 1538.68
12 | 1444.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G11 | 1446.02 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -430.75 | -430.78 | 2346.73 | 1444.79
13 | -799.6 | T-1: Bellingham 230/115kV Bank#2 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G12 | -798.9 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | T-1: Bellingham 230/115kV Bank#2 | -2.9 | -425.87 | -424.06 | 2422.01 | -799.6
14 | -842.48 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G13 | -841.7 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.99 | -427.65 | -427.74 | 2358.3 | -842.48
15 | -812.77 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G14 | -812.86 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.99 | -431.69 | -431.65 | 2378.29 | -812.77
Temp: | 60 Fahrenheit |  | Average Puget Sound Net Area Load = 2922 MW
Gen. | Transfer | Worst | Limiting
Pattern | Limit | Contingency | Facility | 60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201)
1 | 2810.11 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G0 | 2810.02 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2208.95 | -2210.03 | 2980.19 | 2810.11
2 | 2828.56 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G1 | 2828.48 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2214.8 | -2214 | 2911.81 | 2828.56
3 | 2876.36 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G2 | 2875.71 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2269.64 | -2268.34 | 2923.89 | 2876.36
4 | 2926.62 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G3 | 2927.77 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2214.67 | -2216.48 | 2979.74 | 2926.62
5 | 2966.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G4 | 2966.02 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2266.19 | -2264.29 | 2913.39 | 2966.03
6 | 2954.63 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G5 | 2954.77 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2201.88 | -2203.24 | 2924.3 | 2954.63
7 | 3138.18 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G6 | 3138.56 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2226.72 | -2227.57 | 2979.3 | 3138.18
8 | 3156.94 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G7 | 3157.19 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2271.57 | -2270.61 | 2911.65 | 3156.94
9 | 3176.17 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G8 | 3176.5 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2218.68 | -2219.71 | 2924.83 | 3176.17
10 | 2032.37 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G9 | 2032.91 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -432.09 | -432.21 | 2935.5 | 2032.37
11 | 1924.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G10 | 1926.21 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -431.1 | -431.14 | 2865.55 | 1924.24
12 | 1825.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G11 | 1826.02 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -430.49 | -430.39 | 2878.42 | 1825.79
13 | -49.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G12 | -48.6 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -427.46 | -427.38 | 2937.11 | -49.74
14 | -151.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G13 | -151.86 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -428.13 | -428.27 | 2872.85 | -151.68
15 | -166.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G14 | -166.92 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -432.81 | -432.88 | 2890.7 | -166.83
Temp: | 70 Fahrenheit |  | Average Puget Sound Net Area Load = 3275 MW
Gen. | Transfer | Worst | Limiting
Pattern | Limit | Contingency | Facility | 70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201)
1 | 2665.35 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G0 | 2665.44 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2130.76 | -2130.81 | 3330.78 | 2665.35
2 | 2682.12 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G1 | 2682.2 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2118.36 | -2116.41 | 3262.21 | 2682.12
3 | 2729.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G2 | 2729.38 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2186.53 | -2188.59 | 3275.97 | 2729.32
4 | 2792.9 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G3 | 2792.86 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.01 | -2201.24 | -2200.56 | 3330.32 | 2792.9
5 | 2811.2 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G4 | 2811.16 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.01 | -2187.04 | -2186.42 | 3262.27 | 2811.2
6 | 2836.16 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G5 | 2836.09 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2183.43 | -2182.72 | 3275.49 | 2836.16
7 | 3001.51 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G6 | 3002.54 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.01 | -2203.95 | -2205.22 | 3330.89 | 3001.51
8 | 3016.44 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G7 | 3016.54 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.73 | -2190.65 | -2189.31 | 3262.01 | 3016.44
9 | 3026.7 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G8 | 3026.66 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.2 | -2129.06 | -2128.08 | 3274.73 | 3026.7
10 | 2120.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G9 | 2120.87 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -431.24 | -431.34 | 3293.62 | 2120.17
11 | 2025.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G10 | 2026.24 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -432.25 | -432.36 | 3223.66 | 2025.69
12 | 1916.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G11 | 1917.69 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -432.02 | -432.1 | 3235.49 | 1916.47
13 | 22.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G12 | 21.31 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -426.3 | -426.34 | 3291.15 | 22.08
14 | -66.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G13 | -66.64 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -428.4 | -428.47 | 3226.24 | -66.92
15 | -111.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G14 | -111.62 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.34 | -431.01 | -431.03 | 3243.51 | -111.55