## 25F nomo
Tacoma-Raver #1&2 500kV & North-Shoreline 115kV Lines, Monroe 500kV PCB 4672 & Bellingham 230/115kV Transformer Bank #1 O/S
Winter 2008
South-to-North (SN)
Light Loads
Outage: |  | 583
Temp: |  | 25 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 3332.3287
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3090.65 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 650 | 3019.53 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3103.66 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 650 | 3260.28 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 3019.53 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 650 | 3487.54 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 3218.81 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 650 | 3008.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3248.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 650 | 1085.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3260.28 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 380 | 3103.66 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3399.44 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 380 | 3248.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3463.04 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 380 | 3463.04 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3487.54 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 380 | 2997.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 3238.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 380 | 1186.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2997.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 100 | 3090.65 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3008.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 100 | 3218.81 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 1301.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 100 | 3399.44 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1186.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 100 | 3238.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 1085.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 100 | 1301.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Tacoma-Raver #1&2 500kV & North-Shoreline 115kV Lines, Monroe 500kV PCB 4672 & Bellingham 230/115kV Transformer Bank #1 O/S
Winter 2008
South-to-North (SN)
Light Loads
Outage: |  | 583
Temp: |  | 35 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 2643.4727
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3109.22 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 650 | 2919.78 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3052.21 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 650 | 3178.33 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2919.78 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 650 | 3476.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 3181.29 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 650 | 2282.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3221.23 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 650 | 297.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3178.33 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 380 | 3052.21 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 3416.82 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 380 | 3221.23 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3426 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 380 | 3426 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3476.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 380 | 2383.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2544.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 380 | 388.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2383.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 100 | 3109.22 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 2282.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 100 | 3181.29 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 438.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 100 | 3416.82 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 388.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 100 | 2544.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 297.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 100 | 438.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Tacoma-Raver #1&2 500kV & North-Shoreline 115kV Lines, Monroe 500kV PCB 4672 & Bellingham 230/115kV Transformer Bank #1 O/S
Winter 2008
South-to-North (SN)
Light Loads
Outage: |  | 583
Temp: |  | 45 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 2399.9973
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3060.65 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 650 | 2900.43 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3052.51 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 650 | 3179.56 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2900.43 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 650 | 3423.89 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 3149.97 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 650 | 1449.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3194.45 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 650 | -964.63 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3179.56 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 380 | 3052.51 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 3366.67 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 380 | 3194.45 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3394.74 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 380 | 3394.74 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3423.89 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 380 | 1540.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1657.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 380 | -869.8 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1540.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 100 | 3060.65 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1449.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 100 | 3149.97 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -572.28 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 100 | 3366.67 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -869.8 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 100 | 1657.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -964.63 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 100 | -572.28 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Tacoma-Raver #1&2 500kV & North-Shoreline 115kV Lines, Monroe 500kV PCB 4672 & Bellingham 230/115kV Transformer Bank #1 O/S
Winter 2008
South-to-North (SN)
Light Loads
Outage: |  | 583
Temp: |  | 60 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 2922.2327
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2807.2 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 650 | 2828.72 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2818.02 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 650 | 2953.69 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2828.72 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 650 | 3179.38 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2924.97 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 650 | 1828.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2950.44 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 650 | -193.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2953.69 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 380 | 2818.02 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3145.77 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 380 | 2950.44 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3163.33 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 380 | 3163.33 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3179.38 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 380 | 1934.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2035.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 380 | -91.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1934.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 100 | 2807.2 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1828.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 100 | 2924.97 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -5.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 100 | 3145.77 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -91.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 100 | 2035.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -193.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 100 | -5.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Tacoma-Raver #1&2 500kV & North-Shoreline 115kV Lines, Monroe 500kV PCB 4672 & Bellingham 230/115kV Transformer Bank #1 O/S
Winter 2008
South-to-North (SN)
Light Loads
Outage: |  | 583
Temp: |  | 70 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 3275.002
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2666.53 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 650 | 2731.07 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2685.08 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 650 | 2832.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2731.07 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 650 | 3021.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2784.28 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 650 | 1919.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2798.52 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 650 | -109.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2832.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 380 | 2685.08 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2991.02 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 380 | 2798.52 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3010.13 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 380 | 3010.13 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3021.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 380 | 2022 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2133.67 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 380 | -23.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2022 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 100 | 2666.53 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1919.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 100 | 2784.28 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 100 | 2991.02 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -23.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 100 | 2133.67 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -109.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 100 | 29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Pink Table
South-to-North (SN) |  |  |  | Light Loads |  |  | 583 | Tacoma-Raver #1&2 500kV & North-Shoreline 115kV Lines, Monroe 500kV PCB 4672 & Bellingham 230/115kV Transformer Bank #1 O/S
PSE Gen |  | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25 Fahrenheit | 3332.3287 | 3090.65 | 3103.66 | 3019.53 | 3218.81 | 3248.42 | 3260.28 | 3399.44 | 3463.04 | 3487.54 | 3238.87 | 2997.76 | 3008.7 | 1301.97 | 1186.82 | 1085.28
35 Fahrenheit | 2643.4727 | 3109.22 | 3052.21 | 2919.78 | 3181.29 | 3221.23 | 3178.33 | 3416.82 | 3426 | 3476.71 | 2544.99 | 2383.1 | 2282.61 | 438.02 | 388.94 | 297.27
45 Fahrenheit | 2399.9973 | 3060.65 | 3052.51 | 2900.43 | 3149.97 | 3194.45 | 3179.56 | 3366.67 | 3394.74 | 3423.89 | 1657.21 | 1540.96 | 1449.36 | -572.28 | -869.8 | -964.63
60 Fahrenheit | 2922.2327 | 2807.2 | 2818.02 | 2828.72 | 2924.97 | 2950.44 | 2953.69 | 3145.77 | 3163.33 | 3179.38 | 2035.35 | 1934.43 | 1828.42 | -5.11 | -91.15 | -193.62
70 Fahrenheit | 3275.002 | 2666.53 | 2685.08 | 2731.07 | 2784.28 | 2798.52 | 2832.71 | 2991.02 | 3010.13 | 3021.42 | 2133.67 | 2022 | 1919.27 | 29 | -23.04 | -109.34

## Results
Description: |  | Tacoma-Raver #1&2 500kV & North-Shoreline 115kV Lines, Monroe 500kV PCB 4672 & Bellingham 230/115kV Transformer Bank #1 O/S
Season/Year: |  | Winter 2008
Direction: |  | South-to-North (SN)
Case Loads: |  | Light Loads
Outage: |  | 583
Power World: |  | 13.0 (*.exe Date: 02/24/08)
File Location: |  | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2008\WINTER_2008
Study Person: |  | FRP9899
Temp: | 25 Fahrenheit |  | Average Puget Sound Net Area Load = 3332 MW
Gen. | Transfer | Worst | Limiting | PASTE RESULTS BELOW
Pattern | Limit | Contingency | Facility | 25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201)
1 | 3090.65 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G0 | 3091.22 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.02 | -2489.86 | -2491.63 | 3396.97 | 3090.65
2 | 3103.66 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G1 | 3102.97 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.02 | -2483.49 | -2481.96 | 3325.96 | 3103.66
3 | 3019.53 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G2 | 3019.55 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: EL-MON-SNK & CHJ-MON | 15.73 | 500.68 | 500.39 | 3331.55 | 3019.53
4 | 3218.81 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G3 | 3218.35 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.02 | -2501.92 | -2501.87 | 3396.99 | 3218.81
5 | 3248.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G4 | 3246.89 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.74 | -2496.81 | -2494.76 | 3328.01 | 3248.42
6 | 3260.28 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G5 | 3259.63 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.02 | -2483.18 | -2482.47 | 3338.56 | 3260.28
7 | 3399.44 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G6 | 3400.19 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2393 | -2391.15 | 3395.58 | 3399.44
8 | 3463.04 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G7 | 3462.96 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.74 | -2497.28 | -2496.05 | 3326.91 | 3463.04
9 | 3487.54 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G8 | 3486.91 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.74 | -2513.15 | -2511.64 | 3339.86 | 3487.54
10 | 3238.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G9 | 3239.58 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -477.09 | -477.02 | 3367.21 | 3238.87
11 | 2997.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G10 | 2997.05 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -465.85 | -465.71 | 3290.6 | 2997.76
12 | 3008.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G11 | 3008.63 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -472.26 | -472.21 | 3302.13 | 3008.7
13 | 1301.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G12 | 1301.57 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -474.29 | -474.46 | 3321.09 | 1301.97
14 | 1186.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G13 | 1185.92 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -473.71 | -473.92 | 3253.97 | 1186.82
15 | 1085.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G14 | 1086.21 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -473.74 | -473.79 | 3269.54 | 1085.28
Temp: | 35 Fahrenheit |  | Average Puget Sound Net Area Load = 2643 MW
Gen. | Transfer | Worst | Limiting
Pattern | Limit | Contingency | Facility | 35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201)
1 | 3109.22 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G0 | 3109.96 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.02 | -2433.69 | -2435.15 | 2708.21 | 3109.22
2 | 3052.21 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G1 | 3052.43 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: EL-MON-SNK & CHJ-MON | 15.73 | 490.54 | 490.17 | 2634.71 | 3052.21
3 | 2919.78 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G2 | 2919.88 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: EL-MON-SNK & CHJ-MON | 15.73 | 497.84 | 497.58 | 2640.81 | 2919.78
4 | 3181.29 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G3 | 3181.68 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2350.83 | -2352.42 | 2707.64 | 3181.29
5 | 3221.23 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G4 | 3220.28 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.74 | -2418.27 | -2419.34 | 2639.86 | 3221.23
6 | 3178.33 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G5 | 3180.13 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: EL-MON-SNK & CHJ-MON | 15.73 | 492.17 | 492.53 | 2647.08 | 3178.33
7 | 3416.82 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G6 | 3415.22 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2361.97 | -2363.31 | 2708.26 | 3416.82
8 | 3426 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G7 | 3424.59 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2381.69 | -2382.92 | 2638.46 | 3426
9 | 3476.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G8 | 3475.27 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.74 | -2460.32 | -2458.46 | 2653.17 | 3476.71
10 | 2544.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G9 | 2544.58 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -465.96 | -466.21 | 2660.2 | 2544.99
11 | 2383.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G10 | 2383.76 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -463.94 | -463.81 | 2588.65 | 2383.1
12 | 2282.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G11 | 2283.32 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -462.91 | -462.78 | 2600.87 | 2282.61
13 | 438.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G12 | 438.23 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -460.1 | -459.98 | 2645.74 | 438.02
14 | 388.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G13 | 391.34 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -462.27 | -462.17 | 2580.24 | 388.94
15 | 297.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G14 | 297.6 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -462.87 | -462.94 | 2598.19 | 297.27
Temp: | 45 Fahrenheit |  | Average Puget Sound Net Area Load = 2400 MW
Gen. | Transfer | Worst | Limiting
Pattern | Limit | Contingency | Facility | 45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201)
1 | 3060.65 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G0 | 3060.53 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.02 | -2377.36 | -2376.31 | 2461.74 | 3060.65
2 | 3052.51 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G1 | 3052.73 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: EL-MON-SNK & CHJ-MON | 15.73 | 477.22 | 477.66 | 2389 | 3052.51
3 | 2900.43 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G2 | 2900.33 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: EL-MON-SNK & CHJ-MON | 15.73 | 482.32 | 482.06 | 2396.59 | 2900.43
4 | 3149.97 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G3 | 3150.62 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2311.98 | -2313.92 | 2460.13 | 3149.97
5 | 3194.45 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G4 | 3194.91 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.74 | -2382.3 | -2383.51 | 2392.84 | 3194.45
6 | 3179.56 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G5 | 3180.72 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: EL-MON-SNK & CHJ-MON | 15.73 | 480.35 | 480.09 | 2402.04 | 3179.56
7 | 3366.67 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G6 | 3365.05 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2316.62 | -2318.1 | 2460.27 | 3366.67
8 | 3394.74 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G7 | 3393.5 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2323.43 | -2325.2 | 2392.05 | 3394.74
9 | 3423.89 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G8 | 3422.42 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.74 | -2396.68 | -2400.03 | 2406.08 | 3423.89
10 | 1657.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G9 | 1656.07 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -430.88 | -430.96 | 2400.93 | 1657.21
11 | 1540.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G10 | 1541.32 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -430.3 | -430.34 | 2332.55 | 1540.96
12 | 1449.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G11 | 1448.23 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -430.93 | -430.99 | 2347.31 | 1449.36
13 | -572.28 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G12 | -571.86 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.99 | -432.96 | -432.85 | 2419.03 | -572.28
14 | -869.8 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G13 | -869.91 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.99 | -426.46 | -426.42 | 2358.12 | -869.8
15 | -964.63 | BFR: Bellingham 230kV Bus | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G14 | -964.11 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -3.99 | -426.75 | -426.72 | 2381.28 | -964.63
Temp: | 60 Fahrenheit |  | Average Puget Sound Net Area Load = 2922 MW
Gen. | Transfer | Worst | Limiting
Pattern | Limit | Contingency | Facility | 60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201)
1 | 2807.2 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G0 | 2807.14 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2207.36 | -2207.31 | 2980.81 | 2807.2
2 | 2818.02 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G1 | 2818.11 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2192.57 | -2193.4 | 2912.17 | 2818.02
3 | 2828.72 | MOD BFR: EL-MON-SNK & CHJ-MON | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | G2 | 2828.72 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | MOD BFR: EL-MON-SNK & CHJ-MON | 15.73 | 462.77 | 462.76 | 2924.58 | 2828.72
4 | 2924.97 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G3 | 2924.89 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2216.18 | -2218.03 | 2980.36 | 2924.97
5 | 2950.44 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G4 | 2950.37 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2221.12 | -2219.81 | 2911.72 | 2950.44
6 | 2953.69 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G5 | 2953.82 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2202.1 | -2202.94 | 2924.82 | 2953.69
7 | 3145.77 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G6 | 3145.92 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2233.28 | -2234.27 | 2980.46 | 3145.77
8 | 3163.33 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G7 | 3163.51 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2229.72 | -2231.62 | 2911.27 | 3163.33
9 | 3179.38 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G8 | 3179.89 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2225.71 | -2227.16 | 2924.5 | 3179.38
10 | 2035.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G9 | 2035.97 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -432.31 | -432.42 | 2936.03 | 2035.35
11 | 1934.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G10 | 1934.68 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -431.06 | -430.87 | 2866.59 | 1934.43
12 | 1828.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G11 | 1828.65 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -430.69 | -430.61 | 2879.01 | 1828.42
13 | -5.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G12 | -4.53 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -430.86 | -430.72 | 2936.87 | -5.11
14 | -91.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G13 | -91.33 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -431.42 | -431.46 | 2872.99 | -91.15
15 | -193.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G14 | -193.43 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -431.04 | -431.07 | 2891.31 | -193.62
Temp: | 70 Fahrenheit |  | Average Puget Sound Net Area Load = 3275 MW
Gen. | Transfer | Worst | Limiting
Pattern | Limit | Contingency | Facility | 70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201)
1 | 2666.53 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G0 | 2666.59 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2123.88 | -2122.5 | 3331.4 | 2666.53
2 | 2685.08 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G1 | 2685.17 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2126.85 | -2126 | 3262.54 | 2685.08
3 | 2731.07 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G2 | 2731.16 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.02 | -2184.34 | -2185.55 | 3276.59 | 2731.07
4 | 2784.28 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G3 | 2784.22 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2141.62 | -2139.77 | 3330.4 | 2784.28
5 | 2798.52 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G4 | 2798.44 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -67.21 | -2124.41 | -2122.96 | 3262.02 | 2798.52
6 | 2832.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G5 | 2832.66 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.74 | -2181.33 | -2180.6 | 3275.87 | 2832.71
7 | 2991.02 | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G6 | 2991.01 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | MOD BFR: 4516 MON-CUS #1 & CHJ-MON | -67.02 | -2195.24 | -2196.68 | 3331.17 | 2991.02
8 | 3010.13 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G7 | 3010.23 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.74 | -2186.72 | -2188.58 | 3262.48 | 3010.13
9 | 3021.42 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | G8 | 3021.54 | Branch CUSTER W (40323) TO MONROE (40749) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.74 | -2181.55 | -2183.14 | 3275.55 | 3021.42
10 | 2133.67 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G9 | 2132.83 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -433.73 | -433.76 | 3294.92 | 2133.67
11 | 2022 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G10 | 2022.57 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -433.04 | -433.12 | 3224.08 | 2022
12 | 1919.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G11 | 1919.57 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -432.18 | -432.34 | 3236.01 | 1919.27
13 | 29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G12 | 29.28 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -427.93 | -428.02 | 3291.59 | 29
14 | -23.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G13 | -22.85 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -430.14 | -430.37 | 3226.32 | -23.04
15 | -109.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | G14 | -109.43 | Branch CUSTER W (40321) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.33 | -431.18 | -431.2 | 3244.09 | -109.34